Valves:
V1-PR	Pressure Relief Valve set at 30PSI
Drains outside thru P1-PR
V2-FILL	House water to the system.
Shown in fill position(open)
Normal Operation it should be closed?
Filling: any excess pressure should drain water out of P1-PR
V3-RECIRC Loop to Heater. Shown in Operating Position (open).
Close when filling?
V4-OUT	Heater to loop shutoff
Shown in Operating Positon (open)
close during servicing?
V5-DRAIN	Attach Diagnostic G3-P Pressure Gauge here, or hose to outside if draining system.
REDUCE-V6	Pressure Reduction Valve, note that these can wear out and this has been suspected stuck closed in 201711 and after fiddling it opened likely allowing higher than 30PSI out because the P1-PR
AV1, AV2	Air release Valves

Controls:
C1-BRK	(small panel) 240V 80amp (2x40)
Turn off when servicing
C2-BRK	Breaker 14 on main panel for pump. Unfortunately also the lights near the tank.
C3-THERM	Thermostat in the suite.
C4-RESET	201711 when system was empty, this breaker popped, you must turn breaker off before resetting or adjusting temperature control
C5	Tank Temperature Control 201711 appears to be set at lowest possible tempurature

Tanks:
T1-HEATER	A water heater
T2-EXPAN	Expansion Tank. 40PSI charge

Pipes:
P1-PR	This pipe is connected to the blow valves for all 3 hot water heaters. They drain outside under the garage. I would expect a larger diameter pipe, and something indicating that water flowing thru is relieving a dangerous error condition.
P2-IN	This is house water in. 201711 had water pressure that may have exceeded 120PSI tested after severe humming in the house water system. The pressure reduction valve into the house was adjusted to lower it to no humming only. Noted that there is not a check valve as of 201711, so water from the radiant heating could affect drinking water.
P3-O	Water from the pump to the radiant loop
This has an air valve on it at the highest point.
P3-RECIRC	Water recirculating from the radiant loop. This also has an air release valve on it at highest point. below the valve and before the pump, house water fill entry T exists. the
Electrical:
E1-PUMP	Wire from panel to pump.
E2-HEATER Wire from panel to Heater (Boiler)
E3-THERM	Thermostat wire
PUMP	201711 This pump made high pitched squealing when the system ran dry. It may make some extra clicks and run warmer than it did last winter.

Procedures:
Fill System / Top System Off:
1. (Check for leaks, loop and other locations)
2. apply pressure gauge to drain valve,
3. open drain valve to check pressure.
  1. If pressure is above 30PSI Error, shut system off, check pressure relief valves.
  2. If pressure is lower than 30PSI
    1. Check under garage drain location (remove anything that can't get wet)
    2. If under 30PSI Open fill valve,
      1. there should be a noise. Check outside drain. Shut off valve if pressure exceeds 30PSI or water drains.
      2. If no noise, you may need to fiddle with the pressure reduction valve.
Shut system down:
Turn down thermostat.
Turn off breakers
Close input valve.
Turn System On:
Fill system:
Turn breakers on. (if fail, turn breakers off then hit reset button, and turn breakers on)
Drain System:
Unknown, may involve using pump to send water out of drain valve hose, and making sure to turn off pump when system is empty.

Error Conditions:
if in doubt, shut it down

Noise -- Gurgling - system likely low on water, This may mean a leak is present which is bad, but if it has been a long time it could just be steam leaving air valves or such.
Top System Off

Noise -- Whailing - Pump failure Turn off both breakers and turn thermostat water down.
Noise -- Pipes Humming - if it's the house system the city pressure may have increased. check pressure (apply pressure gauge to drain valve and open it, also try house water )
Too Cold -- Check thermostat...
is it set to desired temperature?
sweep thermostat thru temperature range. it should make clicking noise when sweeping thru current temperature. adjust it to higher than current temperature and check motor for noise. a slight vibration should be present and no gurgling. or other abnormal noises that may occur if the system is dry
both Yes and no---
Check Gauge Temperatures... If the gauges do not show about 90 in and 100 degrees out, check to see if the system is charged with water. check the pressure relief drain area, removing anything that shouldn't get wet, then open the fill valve, stop when

If the thermometers read the room temperature,
 then it is probably breakers or reset switch under panel. These will only trip if there is an error, such as the system being drained.

Reset Water Heater:
The system may have been damaged when it ran without water. Be alert.
1. Fill System.
2. Turn Heater breaker off.
3. Unscrew panel (Philips #2 bit)
4. listen for a click,
  - Push the reset button. if it clicks, you may have found the problem
  - Turn Heater breaker on