OPTICLIM
Understanding what can be improved on HVAC
and its related benefit
Getting started

---
OPTICLIM
Usual accronyms
- AHU : Air Handling Unit
- HVAC : Heating Ventilation and Air Conditionning
- RH : Relative Humidity
- COP : Coefficient Of Performance

---
Initial config
Do it once only, as you connect to your home page first time.
- Select your weather station from the drop list
- Enter the total number of Air Handling Units on your site

---
Production Calendars config
Room occupancy calendar
Tick the checkboxes when the room is on work during this time slot

---
Production Calendars config
Shutdown production calendar
Tick the checkboxes when no work or maintenance work takes place during the period (each checkboxe covers one day)

---
« Room conditions » Tab
At rest conditions (« out of room occupation ») : these cells relate to the time slot where the room is not used for production, usually at night or during the weekend.
Whenever possible, increase Temperature and RH tolerances
 and simultaneously reduce ventilation (see next tab), it results into double digit savings for very low or almost no investment effort.

---
« Room conditions » Tab
Enter all data (not entering all data will result into a calculation blockage further)
- Tolerances on temperature and RH : these tolerances values are the one that your BMS (or PLC) actually manages for your AHU. Check with your automation engineer the actual value.
- To confirm this information display the following charts from your BMS :
- Temperature versus time
- RH versus time
- Heating and Cooling valves versus time (this will be very useful on next tab)
Regarding these tolerance valudes : the higher, the best, usually for both Temperature and RH
Typical smart values  as for Temperature and RH tolerances:
- Temperature tolerance : ± 3 °C. Temperature setpoint depends on external conditions. If you can move it as external temperature varies you will get significant savings.
- RH tolerance : ± 15 % around 45 % as set point, resulting into 30 60 %

---
« Room conditions » Tab
Does the AHU receive its fresh air from another AHU that prepares the air ?
If it is the case (Yes) , enter the respective values of the incoming air temperature and RH.
The weather data will not be considered for some of the calculations while still being considered as for building energy losses.
This kind of cascade usually generates significant energy losses compared to direct temperature and RH control

---
« Room conditions » Tab
Room dimensions : if the AHU blows into 3 rooms, say room A, room B and room C, the volume to enter = room A volume + room B volum + room C volum
Walls surface : this is the sum of all walls that separate the rooms from outside the building. So do not consider the walls that separate from corridors or from another room.
Same concepts applies to the respective surfaces of windows and roof.
Roof Insulation : if an attic is above the room and it is well insulated, consider that your insulation is at the highest level.

---
« Room conditions » Tab
Heat losses : this parameter depends upon the tightnes of doors and windows
Nominal Heat power (Watts) : the sum of all electrical power equipment inside the room expressed in Watts.
Bulking factor during room occupation (%) : most equipment running inside the room generate heat. This value is the percentage of the Nominal Heat power that eventually turns to heat during working hours
Bulking factor out of room occupation (%) : same concept as above, but during inoccupation periods.
In the example below the equipment burns 10 kW that are entirely dedicated to heat generation during working hours (100%) while only 10 % (= 1 kW) are consummed out of working periods.

---
« Energy & control parameters » Tab
COP : this is the average COP over the year. If you under / over estimate it by x %, the cooling energy difference will report the same percentage versus reallity.
Average efficiency of cooling and heating networks: this relates to the status of the hydraulic balance of the network. If you your installation is old or if you are using 3 ways-valve you should not over estimate it. Efficiency is scarcely above 70 %.
If you have no idea about it, then a network audit may pin-point major issues and offer solutions. Improvement ranging into 20 to 30 % are commons.

---
« Energy & control parameters » Tab
Efficiency of temperature control (heating and cooling)
Due to the to the phenomenon of inertia that is specific to room temperature control, oscillations of heating / cooling valves often occur, therefore limiting the efficiency of the system.
It would be over optimistic to select values above 70 %.
If you want to get rid of this larvery significant source of energy waste, implement the concept of comfort zone, by example using possible existing modules from your BMS such as module tx2 from Siemens (see attached document), or the module FbHxControl from Wago
See on page 198 of the document below
http://global.wago.com/appnoteadmin/libraries23/Libraries_BA/public/Building_HVAC_03_en.pdf
The greater the comfort zone, the greater the savings.
On the 3 next slide we discover why it is paramount to pay attention to this point regarding savings

---
« Energy & control parameters » Tab
Surprise in the technical room…
Current parameters :
Set point :
T° = 21°C  0°C
RH%= 50  0%
Demanding too much (± 0) simply
Results into not getting the expected
Performance : Temperature ranges
within 20 to 23 °C
 and RH from 45 ot 55 %
Temperature :20-23°C
RH% : 45-55%
Dew point : 11°C

---
« Energy & control parameters » Tab
Surprise in the technical room…
Current parameters :
Set point :
T° = 21°C  0°C
RH%= 50  0%
Temperature : 14-18°C
RH% : 45-55%
Dew point : 11°C
Cooling valve : 60-100%
Heating valve : 0-85%
On one day we see how control is
Behaving, with continuous
Oscillations on heating and
Cooling valves!!
2013-08-14
5h00
2013-08-15
12h00

---
Getting started with OPTICLIM
« Energy & control parameters » Tab
Surprise in the technical room…
Current parameters :
Set point :
T° = 21°C  0°C
RH%= 50  0%
New parameters (manual test) :
Set point :
T° = 22°C  4°C (it could be  3°C)
RH%= 55  10%
Temperature : 26°C (it could be 24°C)
RH% : 40% (it could be >45% with 24°C)
Dew point : 12°C
Coming back to just what QA
was actuallyexpecting enabled to
accurately meet the setpoints
and to save about 80 % of
heating / cooling energy !
In such a case, control
efficiency is worth less than 20 %
2013-08-14
5h00
2013-08-15
12h00
2013-08-16
6h00

---
« AHU » Tab
Air change rate:select either volume / hour or m³ / hour according to the most convenient mode. Next enter the related value. These values depends on the category of product and the class of the room.
By exemple for Pharma solids 10 to 12 vol/h is usual during working hours.
Fresh Air change rate:select either volume / hour or m³ / hour according to the most convenient mode. Next enter the related value
This value should meet HSE and legitimated QA requirements.

---
« AHU » Tab
Free cooling mode: in this mode uptaking incoming air instead of recycling is prevails whenever it is more favourable.
Supply air flow rate out of room occupation : the higher the air change rate, the higher the resulting saving. This must be agreed by QA, usually after conducting a risk assesment.
Supply airflow rate during production shutdown: As for Pharma sites, usually during production shutdown a minmum air flow is maintained to avoid re-qualifying the rooms.

---
« AHU » Tab
Fans, mechanical transmission, motors categories :
select appropriate categories from the drop lists or enter directly the values if accurately known.

---
« AHU » Tab
Total pressure heads  :
select appropriate categories from the drop lists or enter directly the values if accurately known.

---
« AHU » Tab
Total pressure heads  :
select appropriate categories from the drop lists or enter directly the values if accurately known.

---
« Energy recovery » Tab
Total pressure heads  :
select appropriate categories from the drop lists or enter directly the values if accurately known.

---
« Energy recovery » Tab
Energy recovery using chilled water exchangers  :
Just select Yes and do not enter any information as for the cells below : calculation will be performed automatically.
Energy recovery using plates exchangers :
This option is not compatible with the previous one (chllied water exchangers). If you select it, enter the expected related air losses.
Uptaking fresh air from the attic :
If the fresh air comes from the attic, then enter max and min temperaure values over the year as actually metered.