Experimental Procedure
A porcelain suspension disk insulator was used for the experiment. The porcelain suspension disk was so chosen because it is the most common type of insulator in the high voltage service conditions that we are interested in. The technical specifications of the chosen insulator are given below
Insulator Parameters
Diameter	255 mm
Axial Height	145 mm
Creepage Distance	330 mm
Pin Diameter	20 mm
Operating Voltage	11 kV

The experiment was performed in the High Tension laboratory according to IEC 60507 standards. The schematic of the testing setup has been shown in the diagram below

The insulator to be tested is hung
# Formation of Pollution Layer
The IS 8704 which is equivalent to IEC 60507 prescribes the procedure to be adopted for performing artificial pollution tests on overhead ceramic insulators to determine their power frequency withstand characteristics. Two methods for artificial contamination are prescribed by the standard
1. Salt Fog Method in which the insulator is subjected to a defined ambient pollution.
2. Solid Layer Method in which a uniform layer of a standard solid pollutant is deposited on the insulator surface.
The solid layer method was chosen for this experiment due to ease of use and availability of equipment.
According to the standards, there are two recommended methods for creating the contamination suspension.
1. Kieselguhr Composition consisting of
  1. 100 gm Kieselguhr (diatomaceous earth)
  2. 10 gm highly dispersed silicon dioxide (particle size 2-20 nm)
  3. 1000 gm tap water (volume conductivity less than 0.05 S/m)
  4. Suitable amount of NACL of commercial purity.
2. Kaolin Composition consisting of
  1. 40 gm Kaolin
  2. 1000 gm tap water (volume conductivity less than 0.05 S/m)
  3. Suitable amount of NACL of commercial purity.
For our experimental purpose the Kaolin Composition method was chosen because of availability of material. Since the volume conductivity of tap water was found to be more than 0.05 S/m, distilled water was used to prepare the suspension.
The insulator is visually inspected for any cracks or defects, and then it is thoroughly cleaned by using warm water and trisodium phosphate. After that it is thoroughly rinsed with tap water and determined as clean if large continuous wet areas are seen on the surface. After cleaning the insulating parts of the insulator are not touched by hand.
Once the insulator has dried, the prepared contamination suspension is applied uniformly around the insulator and it is left to dry for 24 hours so that a uniform layer is formed on the surface.
# Test Procedure
For the purposes of this experiment, it is necessary to record the leakage current at pre determined voltage levels across all levels of contamination.
Fourier Transform
The Fourier Transform is a mathematical transform that decomposes a time domain function into a sum of sinusoidal basis functions. Thus, by applying the Fourier transform on a function in the time domain, we get a complex valued function of frequency whose magnitude represents the amount of frequency present in the signal, and whose argument represents the phase offset of that sinusoidal frequency in the original signal.
By applying the Fourier transform on the captured leakage current data, which is a discrete time series, we can extract the frequency domain information from it, specifically how the magnitudes of the harmonic frequencies in the leakage current change with changing contamination and applied voltage.
# The Discrete Fourier Transform
The Continuous Fourier Transform can be represented as
{ X ( f ) = int to { infinity } from { infinity } { x left ( t right ) e ^ { j2 %pi ft } dt } }
where x( t ) is some continuous time domain signal.
The continuous Fourier Transform can be used to transform a continuous time domain signal into a continuous frequency domain function.
However the continuous time Fourier transform, cannot be used as is with Digital systems like the computer, neither can it be used to process Discrete Time series data, which is how signals acquired via digital data acquisition systems are stored.
Hence, the Discrete Time Fourier transform was developed to deal with discrete data. It can be represented as (in the exponential form)

where is a discrete sequence of time domain sampled values.
To understand how discrete frequency domain information can be extracted from discrete time domain series by using the above equation, we need to express it in the trigonometric form.
We know from Euler’s relation . Thus the above equation can be expressed as

where
X(m) = the mth DFT output components
     m = the index of the DFT output in the frequency domain
  x(n) = the sequence of input samples
      n = the sequence of input samples
     N = the number of samples of the input sequence and the number of frequency points	in the DFT output.
The indices of the input sample (n) and the output sample (m) always go from 0 to N-1. This implies that if there are N number of input time domain samples, then the Discrete Fourier Transform will calculate and return the frequency content of the input at N number of equally spaced frequency points.
The value of N is very important because it determines the resolution of the frequency domain result and algorithmic implementation of Discrete Fourier transform requires N to be in the form of where k is any positive real number.
Results and Discussion
In the previous sections we discussed the theory and the stages leading up to the flashover event of a contaminated insulator. We also discussed the theory of discrete Fourier Transform and how to extract frequency domain information from the time domain leakage current information.
In this section we discuss a method to use the frequency domain information of the measured leakage current and the voltage information at which the measurements were taken to classify the level of contamination on the insulators.
# 3rd to 5th Harmonic Ratio
On analysing the frequency domain information it can be noticed that there is a pronounced spike in magnitudes of odd harmonic components with increasing voltage and with increasing contamination.

Figure 1: Plot of Frequency Components of five different leakage current at same contamination level and increasing voltage level

Figure 2: Plot zoomed in around the third and fifth harmonic
Figure 3: Plot of Frequency Components of five different leakage current at different contamination level and same voltage level

Figure 4: Plot zoomed in around the third and fifth harmonic
On analysing the graph, it can be noticed that the third and fifth harmonic components increase with increasing voltage and contamination levels and thus we can use the ratio of the magnitudes of the third and fifth harmonic components to determine the contamination level.
On plotting the ratio of the third and fifth harmonic components, we get the following plot.

Figure 5: Plot of third to fifth harmonic ratios
As we can observe, while there is a general trend of the ratios increasing with increase in contamination and voltage, the boundaries between successive contamination levels aren’t quite well defined.
To ensure proper classification, we add the voltage information and then obtain the following scatter plot.

As we can see, after adding the voltage information, the different contamination groups align with well defined boundaries with only a few data points having overlapping boundaries.
Thus we can move on to the next step, that is creating a classifier.
# Support Vector Classifier
We discussed the theory of Support Vector Machine and it’s use as a Binary Classifier, that is classification in two class scenarios, in a previous section. However, the concept of Separating Hyperplanes, upon which Support Vector Machines are based, does not extend naturally to multi class classification problems. Various techniques have been proposed to extend SVMs to the multi class classification problems and the most popular of them is the one-versus-one scheme.
In the one-versus-one scheme, { K* left ( { K - 1 } right ) / 2 } binary classifiers are trained for a K-way classification problem. For example, if there are 3 classes ‘Red’, ‘Green’, and ‘Blue’, that is K=3, then 3 binary classifiers would be trained:
1. Red vs Green
2. Red vs Blue
3. Green vs Blue
Each of these binary classifiers receives the samples of the pair of classes from the original training dataset and trains to classify them correctly.
To predict an observation after the training phase, the new sample is passed to all of the trained binary classifiers, and the number of times the sample is classified to a particular class is tallied. The sample is then assigned the class which has the highest score.
The Support Vector Classifier from the sci-kit learn program, uses the one-vs-one technique to facilitate multi class classification.
The classifier can be created by using the following code
from sklearn.svm import SVC
svc_model = SVC()
svc_model.fit(X_train, y_train)
y_predict = svc_model.predict(X_test)
However, on running the Classifier and predicting based on the trained model, we get an accuracy of only around 19%.

# Importance of Standardization.
The reason for such low accuracy can be attributed to the fact that the data isn’t standardized. While the harmonic ratios are in the range of the 0.2 to 2.5, the voltages are in the range of 1 to 20. This causes the voltage to have disproportionate influence on the overall outcome due to it’s larger numerical value, even though the harmonic ratio has more importance in our classification problem.
Standardization is a scaling technique where the values are centered around the mean with a unit standard deviation. This means that the mean of the attribute becomes zero and the resultant distribution has a unit standard deviation.
The standard score of a sample x is calculated as:
{ z ~ = ~ { left ( { x ~ - ~ u } right ) over s } }
where u is the mean of the training samples, and s is the standard deviation of the training samples.
The Support Vector Classifier from the sci-kit learn program, expects the input features to be Standardized.

# Final Result
After standardizing the input, and passing the training data through the program, we get an accuracy of around 95% as shown
The python code used for the classification is reproduced below
# Import Required Modules
import pandas as pd
import numpy as np
from sklearn.model_selection import train_test_split
from sklearn.preprocessing import StandardScaler
from sklearn.svm import SVC
from sklearn.metrics import classification_report

# Import Data and process it for analysis
data = pd.read_csv('Features.csv')
X = data.drop('Class', axis=1)
y = np.ravel(data['Class'])

# Split the data into training and testing sets
# and Standardize the data
X_train, X_test, y_train, y_test = train_test_split(X,y, test_size = 0.2)
scaler = StandardScaler().fit(X_train)
X_train = scaler.transform(X_train)
X_test = scaler.transform(X_test)

# Train the classifier and make predictions
svc_model = SVC()
svc_model.fit(X_train, y_train)
y_predict = svc_model.predict(X_test)

# Print accuracy and other statistics
print(classification_report(y_test, y_predict))