Table of Contents

# Revision History

Rev	Date	Change Description	By	Appr.
New	12/14/2010	Original Issue	LAW	SFK
A	12/16/2010	Additional physical IO not used; add CompactFlash note; separate MRT 2.0 auxiliary input enhancements, add figure numbers and adjust graphics	LAW

# Introduction
The software for MA77950 Manitoba Hydro Kettle Generating Station Unit 4 is based on MRT 2.0 release ?????2010, GE PACSystems RX3i platform with the modifications described in this document, and the enhancements and selected updated manual sections included in the Appendix.
Additional configuration will be programmed in memory so that it is saved to the CompactFlash card in the same manner as other governor configuration.
# Modifications
## Additional Analog Input
One additional analog input is required for JLC/JEC Control and can be configured from any of the standard physical analog inputs. See Appendix MRT20_OM08-2.
## 125VDC Discrete Input Power Supply Monitoring
One discrete input is dedicated to discrete input power supply monitoring. If the power supply to the 125VDC discrete inputs is lost an alarm is generated.
## Additional Discrete Logical Outputs
Additional discrete logical outputs 137-143 are available to be assigned to physical outputs. See Appendix MRT20_OM08-2 for a list of these outputs.
## Aux Inputs and Control Screen
The Aux Inputs screen is renamed to Aux Inputs and Control screen. The values of the auxiliary analog inputs are located here as well as Droop Selection (isochronous, DC collector system, or AC system) Input, Governor Unload to S.N.L. command status, brake OFF/HAND/AUTO soft control switch and status, and JLC/JEC OFF/ON soft control switch and JLC/JEC Enabled/Disabled status information.
Programming Note: Insert Actual Screen Shot When Complete
Figure 1: Aux Inputs and Control Screen

## Brake Control
An Off/Hand/Auto control switch is provided on the DEP that was formerly in hardware. This switch operates with the governor in either Local or Remote control.

The standard brake logic that energizes the Apply Brakes output (logical output 68) that is used to drive the 20-BKX relay is modified to function as follows depending on the position of the Off/Hand/Auto control switch:
- OFF The output is off causing the brakes to be released
- HAND The output is on with the standard brake logic except that the brakes will not be released after a configurable time after the unit has stopped.
- AUTO The output is on with the standard brake logic and the brakes will be released after a configurable time after the unit has stopped. In addition, the Brakes in Auto logical output will be on in this position and off in the other two positions and this position is selected automatically when the power is cycled / PLC is restarted.

## Gain Switching
The governor has the ability to switch between two independent sets of gains for each position control modes (servo or power) without changing the control mode of the governor. The switched parameters are:
Kp – MRT Position Control Mode proportional gain parameter
Ki – MRT Position Control Mode integral gain parameter
Kd – MRT position Control Mode derivative gain parameter
σ – MRT Position Control Mode permanent droop parameter
The switching of these parameters will be controlled by the Droop 2 (DC System) and Droop 3 (AC System) selections which are latched from the discrete inputs or DEP inputs as follows, with DC System gains being selected automatically when the power is cycled / PLC is restarted.
Note: The Droop 1 Select input is configured to select Isolated Control mode, which has its own set of independent gains.
Note: The Droop 2 and 3 Select inputs are configured to select Power Control mode. If there is a problem with the power feedback then the system will automatically switch to Gate Control mode. When switching between Droop 2 &3 modes, however, the controller should stay in the mode currently selected, either Gate or Power.

Figure 2: DC Gains Select

The following block diagram shows how the DC System and AC System gain selection is implemented in the MRT. No changes will be made to the existing transfer function for the gate control or power control modes. The gain parameters are switched external to the existing mode.

Figure 3: DC or AC System Gain Mode Block Diagram

Add text to introduce and explain figures 4 and 5.

Figure 4: Configuring the DC and AC System Gain Values

Figure 5: AC/DC System Gain Mode Indication on Governor Control Screen

Mode Value	Label	Description	Color
1	DC	DC System Gains Selected	Green w/ white text
2	AC	AC System Gains Selected	Green w/ white text

The Set Gains popup accessible from the Trend screen has also been modified to display and modify the active gains when the unit is running.

Figure 6: Set Gains Popup Active Gains
## Auto Unload
When the unit is online and operating in Power or Gate control mode the Auto Unload discrete input generates an Auto Unload command causing the governor to ramp its setpoint down at a configurable rate (initially 4%/sec) to a SNL setting (0 MW or the gate position when the unit last went online plus a configurable value initially 5%). It also commands the JLC/JEC Control OFF. When the unit is not in Power or Gate control this input has no effect and the Auto Unload command is inactive.

## Joint Load Control /Joint Efficiency Control
A JLC/JEC OFF/ON selection on the DEP available when the governor is in Local control mode is used to put the unit on or take it off of the plant joint load control system. (Note: Joint efficiency control at Kettle GS is presently not enabled).
- OFF. JLC/JEC Control is commanded Off. A JOINT-OFF command is sent to the ABB JLC/JEC controller to remove the unit from its control.
- ON. JLC/JEC Control is commanded On. A JOINT-ON command is sent to the ABB JLC/JEC controller to place the unit setpoint under its control. When conditions are satisfied the governor will operate from a governor power setpoint provided by the ABB JLC/JEC control system.
JLC/JEC ON command is sent to the ABB JLC/JEC controller either from the governor DEP, the JLCX relay in the unit start logic connected in parallel with the governor 65JLC-START relay contact, or at the master JLC/JEC console in the control room. After this command is received by the ABB JLC/JEC controller it will respond by sending the “CMD.GOV.EQU.LOAD” signal to governor DI JLC/JEC ENABLED. If the governor is in the correct mode to accept the JLC/JEC ENABLED command (see fig. 7) and it is receiving a healthy external power setpoint signal from the JLC/JEC controller, then the internal JLC/JEC SETPOINT ON command will cause the governor to ramp to the analog JLC/JEC SETPOINT and regulate based on that setpoint. Once matched, the governor energizes the JLC/JEC LOAD EQUALIZED output (65JLC-LEQ relay) and if all conditions are satisfied at the ABB JLC/JEC controller it will accept the unit into its control. This is indicated by a solid indication light for the unit on the master JLC/JEC control panel in the plant control room.
The ABB JLC/JEC controller outputs an analog power setpoint to the governor. The following logic diagram depicts how the governor selects between the external JLC/JEC setpoint and the internal reference setpoint. When using the external JLC/JEC setpoint the internal governor setpoints auto-follow the JLC/JEC setpoint for a bumpless transfer when switching back to the internal reference.

Figure 7: JLC/JEC Setpoint Control Logic

The governor DI JLC/JEC ENABLED going false (i.e. losing the CMD.GOV.EQU.LOAD signal from the main controller) will result in the governor transferring back to the internal governor setpoint and the DEP will indicate that JLC/JEC Control of the unit is OFF.

The discrete outputs associated with the JLC/JEC control are as follows:
JLC/JEC Enable
This output drives the 65JLC-START relay to the ABB JLC/JEC controller. This output picked up from the DEP JLC/JEC ON command; upon a successful transfer to JLC/JEC control (JLC/JEC ENABLED input is received) the output will be reset. If control to JLC/JEC is not transferred within a configurable time (5.00sec) the output will be reset and the “JLC/JEC Control Operation Failure” alarm will be generated causing JLC/JEC Control OFF to be selected.

JLC/JEC Disable
This output is used to drive the 65JLC-STOP relay to the ABB JLC/JEC controller and is on whenever the JLC/JEC Control OFF (from the DEP or internal trip) is operated and remains on until the JLC/JEC ENABLED input is off.

JLC/JEC Load Equalized
This output is used to drive the 65JLC-LEQ relay to the JLC/JEC control. An adjustable window comparator (±2%) is used to compare the actual governor feedback with the JLC/JEC analog setpoint. This output is on when the unit is online, the governor is in Auto control, and the governor output matches the JLC/JEC setpoint.
Note JLC/JEC control does not have to be on for this output to be energized.

The “JLC Analog Setpoint Signal Failed” alarm will be issued if the governor receives a JLC setpoint signal that is out of range or otherwise unhealthy while JLC/JEC Enabled is active and the generator breaker is closed. The unit will drop from JLC/JEC control and will not be able to be placed back on until this alarm is cleared.

The “JLC/JEC Control Mismatch” alarm will be issued if the governor feedback differs from the JLC/JEC setpoint by a configurable amount (initially ±25%) for a configurable time (initially 143.04sec) while JLC/JEC Enabled is active and the generator breaker is closed.

The ABB JLC/JEC controller sends a power setpoint; it doesn't know the health of the governor’s power signal. When the power signal fails, the governor automatically transfers to Gate Control mode. In order for JLC/JEC Control to function correctly, the governor applies the following (user configurable) lookup table (initial values are shown) to derive a gate setpoint for JLC/JEC control when operating on Gate Control mode:

MW	Gate (%)
0	25
89.375	60
99.000	70
104.00	80
109.75	100

The size of the bump on transfer will be dependent on the quality of gate vs. power data provided.

The following JLC/JEC status information is displayed on the DEP:
- JLC/JEC Control OFF/ON status (OFF is green with white text, ON is solid red with white text when governor is regulating to JLC/JEC setpoint and flashing when the JLC/JEC ENABLED input is energized and JLC/JEC LOAD EQUALIZED is not energized)
- LOAD EQUALIZED YES/NO Status (follows JLC/JEC Load Equalized output logic, green with white text)
- JLC/JEC SETPOINT XXX.XX MW

The initial JLC/JEC settings are as follows:
- Power:	0-125MW	0-100%
- JLC/JEC Reference Analog setpoint:	4-20mA	0-125MW
- Power Output to JLC/JEC:	0-125MW	4-20mA
- JLC/JEC Enable timout:	5.00sec
- Load Equalized Δ Window	±2%	±2.5MW
- Load Equalized timeout:	143.04sec
- Feedback vs. JLC/JEC Setpoint Δ Error:	±25%	±31.25MW
- Feedback vs. JLC/JEC Setpoint timeout:	143.04sec

# Appendices
The following MRT 2.0 manual addendum document enhancements to the standard program.
MRT20_Enhancements_Aux_Inputs_Rev New.doc	MRT 2.0 Program Enhancements

The following MRT 2.0 manual sections have been revised to reflect all changes in this project including enhancements to the standard program.
MRT20_OM08-2_MH_Kettle_GS_Rev A.doc	Revised hardwired interface
MRT20_OM08-3_MH_Kettle_GS_Rev A.doc	Revised communication interface
MRT20_OM08-8_MH_Kettle_GS_Rev A.doc	Revised alarms and shutdowns