## DDS XLPE LT
DRAFT DESIGN SHEET
ENQUIRY NO: |  | NRS/30010897/RM-Rev.01
CABLE TYPE: |  | 2XWWY
NO OF CORES X SIZE | No x mm² | 3 x 185 COPPER
VOLTAGE GRADE: | kV | 0.65/1.1
SPECIFICATION |  | IS 7098 PT-1
Dia. Over Inner Sheath | mm | 37.9
ROUND WIRE ARMOUR |  | 0 | 7.85
0 | mm | 2.5 | 43.5835
0 | Nos | 44 | 44
Lay & Direction (L/R) | mm | 404 | L
0 | kg/km | 1780
0 | mm | 42.9
TAPE - MATERIAL |  | PVC | 1.5
No of tapes |  | 1 | H R
Width x Thickness | mm x mm | 60 | 0.25
Over lap (Direction of lapping) |  | 5
0
0 | m/km | 2470
0 | kg/km | 56
0 | mm | 43.4
ROUND WIRE ARMOUR |  | 0 | 7.85
0 | mm | 2.5 | 49.5169
0 | Nos | 29 | 50
Lay & Direction (L/R) | mm | 459 | R
0 | kg/km | 1173
0 | mm | 48.4
CU WIRE ARMOUR |  | TINNED CU (W) | 8.89
Nominal wire diameter | mm | 2.5
No of wires | Nos | 20
0 | kg/km | 916
0 | mm | 48.4
TAPE MATERIAL |  | RCC | 0.5
No of tapes |  | 1
Width x Thickness | mm x mm | 90 | 0.1
Over lap / (Direction of lapping) |  | 5 | L
0 | m/km | 1792
0 | kg/km | 8
Dia over MOPP Tape | mm | 48.6
OUTER SHEATH | Material | FRLS PVC ST-2 | 7.85
Nominal / (minimum) thickness | mm | 3 | 2.2
0 | kg/km | 3224 | 2.5556
0 | mm | 54
- Maximum overall cable diameter | mm | 55.1
W E I G H T S |  |  | MAT CODE
COPPER CONDUCTOR | kg/km | 4871
XLPE INSULATION | kg/km | 268
MOPP TAPE LENGTH | m/km | 2440
MOPP TAPE WEIGHT | kg/km | 11
INNER SHEATH | kg/km | 224
0 | 0 | 1780
0 | 0 | 2470
0 | 0 | 56
0 | 0 | 1173
0 | kg/km | 916
0 | 0 | 1792
0 | 0 | 8
0 | 0 | 3224
CABLE WEIGHT | kg/km | 12531
DRUM DETAIL
DRUM SIZE |  | SU 2614/14
DRUM WEIGHT (Approx) | KG
DRUM LENGTH | MTR. | 1200 ± 5 %
ALUMINIUM | LDPE | MOPP
COPPER | PVC | RCC
FIBRILLATED FILLER
FLAT STRIP ARMOUR | TERENE
ROUND WIRE ARMOUR | CREPE PAPER
PVC ST-2
FRLS PVC ST-2
PRESSURE EXTRUDED PVC ST-2
PRESSURE EXTRUDED FRLS PVC ST-2

## Data Base
COPPER
#REF!
AREA | DIA | Construction | AREA | WEIGHT |  | #REF!
16 | 4.7 | 7/1.74 | 16 | 137
25 | 5.9 | 7/2.2 | 25 | 217
35 | 7 | 7/2.61 | 35 | 301
50 | 8.1 | 19/1.82 | 50 | 411
70 | 9.7 | 19/2.20 | 70 | 594
95 | 11.5 | 19/2.61 | 95 | 824
120 | 13.2 | 36/2.11 | 120 | 1044
150 | 14.5 | 36/2.33 | 150 | 1289
185 | 16.1 | 36/2.61 | 185 | 1612
240 | 18.6 | 60/2.33 | 240 | 2120
300 | 20.8 | 59/2.61 | 300 | 2657
400 | 23.8 | 59/2.97 | 400 | 3400
500 | 27 | 60/3.32 | 500 | 4312
630 | 30.6 | 60/3.80 | 630 | 5677
800 | 34.9 | 36/3.60 + 23/3.50 + 30/3.40 | 800 | 7252
1000 | 39.7 |  | 1000 | 9556
1200 | 42 |  | 1200 | 10668
1400 | 44 |  | 1400 | 12446
1600 | 46 |  | 1600 | 14080
1800 | 51 |  | 1800 | 15840
2000 | 54 |  | 2000 | 17880
2500 | 62 |  | 2500 | 22208
Aluminium
AREA | DIA |  | AREA | WEIGHT
16 | 4.7 | 7/1.70 | 16 | 41 |  | #REF!
25 | 5.9 | 7/2.15 | 25 | 65 |  | #REF!
35 | 7 | 7/2.55 | 35 | 90
50 | 8.1 | 7/2.92 | 50 | 123
70 | 9.7 | 19/2.15 | 70 | 248
95 | 11.5 | 19/2.55 | 95 | 315
120 | 12.9 | 19/2.84 | 120 | 315
150 | 14.5 | 1/2.92 + 35/2.27 | 150 | 387
185 | 16.1 | 36/2.55 | 185 | 485
240 | 18.6 | 60/2.27 | 240 | 637
300 | 20.8 | 59/2.55 | 300 | 796
400 | 23.8 | 59/2.92 | 400 | 1026
500 | 27 | 60/3.25 | 500 | 1308
630 | 30.4 | 37/3.79 + 24/3.51 | 630 | 1688
800 | 34.2 | 87/3.44 | 800 | 2156
1000 | 38.6 | 87/3.88 | 1000 | 2722
1200 | 42 | 88/4.2 | 1200 | 3180
1400 | 44 |  | 1400 | 3784
1600 | 46 |  | 1600 | 4325
1800 | 51 |  | 1800 | 4865
2000 | 54 |  | 2000 | 5406
2500 | 62 |  | 2500 | 6760
| SELECTION OF BLIND CORE |  |  |  |  | WEIGHT OF BLIND CORES
| CORE DIAMETER (mm) |  | BLIND CORE DIA (mm) |  |  | DIA OF BLIND CORE (mm) NOMINAL | APPROX WEIGHT PER CORE (kg/km)
| ABOVE | UPTO | 1 BIG | 2 SMALL |  |  | PVC | LDPE
| 0 | 3.5 | 2 |  |  | 1.5 | 2.7 | 1.6
| 3.5 | 6 | 2.5 |  |  | 2 | 4.7 | 2.9
| 6 | 8.5 | 4 |  |  | 2.5 | 7.4 | 4.5
| 8.5 | 10.5 | 5 |  |  | 3 | 11 | 7
| 10.5 | 13 | 6 |  |  | 3.5 | 14.5 | 8.9
| 13 | 15 | 7 | 3 |  | 4 | 19 | 12
| 15 | 18 | 8 | 4 |  | 5 | 29 | 18
| 18 | 20 | 9 | 5 |  | 6 | 42 | 26
| 20 | 23 | 10 | 5 |  | 7 | 58 | 36
| 23 | 27.5 | 12 | 6 |  | 8 | 75 | 47
| 27.5 | 30.5 | 14 | 7 |  | 9 | 95 | 60
| 30.5 | 35 | 16 | 8 |  | 10 | 118 | 73
| 35 | 40 | 18 | 9 |  | 12 | 170 | 105
| 40 | 44 | 20 | 10 |  | 14 | 231 | 143
| 44 |  | 22 | 10 |  | 16 | 302 | 187
[6 empty] | 18 | 382 | 237
[6 empty] | 20 | 471 | 292
[6 empty] | 22 | 570 | 353
SELECTION OF MOPP TAPE
| DIAMETER BELOW TAPE (mm) |  | SIZE OF MOPP TAPE (mm X mm)
| 0 | 10 | 17 | X | 0.05
| 10.1 | 20 | 30 | X | 0.05
| 20.1 | 35 | 50 | X | 0.1
| 35.1 | 55 | 90 | X | 0.1
| 55.1 |  | 100 | X | 0.1
DENSITY CHART
| G.S. (W) | 7.85
| Aluminium | 2.703
| COPPER | 8.89
| CREPE PAPER | 110
| Extruded SEMICON | 1.17
| EXTRUDED XLPE | 0.93
| FIBRILLATED FILLER | 0.7
| FRLS PVC ST-2 | 1.5
| G.S. (F) | 7.85
| LDPE | 0.9
| MOPP | 0.9
| PRESSURE EXTRUDED FRLS PVC ST-2 | 1.5
| PRESSURE EXTRUDED PVC ST-2 | 1.5
| PVC | 1.5
| PVC ST-2 | 1.5
| RCC | 0.5
| SC WATER SWELLABLE | 128
| TERENE | 110