Renewable Energy Systems and
Firefighter Safety
By Dan Fink
www.otherpower.com
Rist Canyon Volunteer Fire Department
www.rcvfd.org
At left – This popular glossy magazine is dedicated completely to home renewable energy (RE) systems. RE is becoming extremely popular, less expensive, and can be found anywhere, as this cover implies.
Cover reprinted with permission. © 2009 Home Power Inc., www.homepower.com.

---
RE systems, key points:
- RE systems are increasingly common and can be found everywhere—rural, urban, remote and urban interface areas‏.
- RE systems can be used to produce hot air, hot water, electricity, or all of the above. Hazards may involve electricity, hot liquids, broken glass, and chemicals.
- RE systems mounted on roofs, ground racks or poles are NOT designed to hold firefighter, ladder or equipment weight.
- RE electric systems may or may not be connected to the utility power grid. All systems will have a central control point, in the main residence OR in an outbuilding.
- Because RE electric systems also MAKE and can STORE power, some circuits may be live even if the “MAIN” system disconnect has been opened.

---
Solar RE system identification
Image © Solatube
Solar tube lighting:
- Firefighter hazards minimal.
- Installed just like a metal chimney.
- No electricity, heat or fluids involved.
- If breached both inside and out, air flow will occur.
Image © Horizon Energy Systems - www.savenrg.com

---
Solar RE system identification
Solar hot air:
- Firefighter hazards minimal.
- Low-power electricity involved for fans and sensors.
- Liquids such as water, glycol or silicone oil may or may not be involved.
- May limit roof access.
Photo © The Alternative Energy Store
Photo © Clear Dome Solar Thermal LLC

---
Solar RE system identification
Solar hot water:
- Some firefighter hazards.
- Low power electricity used for pumps, sensors, and valves.
- Fluids such as water, glycol or silicone oil are always involved, and may be hot.
- May limit roof access.
- May include exposed, fragile glass on the roof.
- Many more pipes than there are wires.
Photo © Skyflair Ltd UK
Photo © Radiant Floor Company

---
Solar RE system identification
Solar hot water, radiant floor heat:
(interior control system photo, outdoor system remains the same)‏
- Pipes embedded in floors.
- Many more pipes than there are wires.
- Many pipes at manifold.
- Low-power electricity used for pumps and sensors.
- Some firefighter hazards.
- Hot liquids involved.
- Modern systems use only non-flammable liquids. Very old systems (1970s- early 1980s) may use flammable liquids.
Photo © Peak to Prairie Home Inspection Service

---
Solar RE system identification
Solar Electric (aka Photovoltaic, PV):
- Some firefighter hazards.
- Electricity is always involved, and may be at lethal levels.
- Some circuits remain live even if MAIN disconnects are opened!
- May limit roof access (see photo at top left).
- Contain glass, and are both fragile and very expensive.
- Source circuits may or may not be properly labeled.
Photos courtesy DOE/NREL

---
Solar electric system identification
Solar Electric (aka Photovoltaic, PV):
Close-up photos of PV modules
Note individual solar cells wired together in each module.

---
Solar electric system identification
Solar Electric (aka Photovoltaic, PV):
Building-integrated (solar shingles)‏
- Like all other PV panels EXCEPT:
- May not be obvious.
- Usually OK if roof ladders rest on panels.
- Very durable, no glass.
Photo © Decker Homes
Photo courtesy of DOE/NREL
Photo © Global Solar

---
Common hazards of all solar RE systems
Remember!
Roof access for ventilation is very rare in our department, but roof access for possible chimney fires is very common.
Do not cause needless damage to any roof-mounted solar RE system. All are fragile and very expensive, and some could injure or kill you.
- Mounting racks and panel surfaces are NOT strong enough to support firefighters, equipment, or roof ladders.
- Broken glass and irate owner hazards if any of the above are attempted, no matter what system type.
- Roof access may be limited.
- Inhalation hazards from burning plastics, liquids, and PV cell components.
- CalFire and LA Fire do have roof access guidelines for rooftop solar system design:
- http://mpandc.com/resources/LA_Fire.pdf
- http://mpandc.com/resources/Cal_Fire_PV_Guidelines.pdf

---
Specific Hazards, Solar Electric Systems
- Voltage potentials may range from 12 to 600 Volts, AC or DC.
- Different voltages may be present at any time in different parts of the system.
- High voltage presents electrocution and arcing hazards, while low voltage presents overheating, fire, spark and burn hazards.
- Systems may not be properly labeled. During an incident, you may not know with certainty which wires and conduits carry what, even if the homeowner is present (owner may not know or may be confused).
Sample labeling of main disconnect enclosure (CalFire)‏
(could include all 3 types of solar electric system, and could shut off different circuits on each type):
Sample labeling of sub circuit disconnect enclosures (CalFire)‏
(could include all 3 types of solar electric system, and could include electrical sources from solar, wind, hydro, generator):
CAUTION
SOLAR ELECTRIC SYSTEM
CAUTION
SOLAR CIRCUIT

---
Specific Precautions, Solar Electric Systems
- Assume every circuit is live and at lethal voltage, and do not cut any conduit or wiring without using high voltage precautions.
- Be aware that even after opening the “MAIN” disconnect, source (input) circuits will remain live at up to 600 volts DC (electrocution hazard), and other circuits will remain live at battery bank voltage (12-120 volts DC—overheating, fire and burn hazard).
- There will be multiple combiner boxes and disconnects in all solar electric systems, and some will be located outdoors, on a rooftop, or on a pole mount. They may not be labeled at all, and locations may not be obvious or accessible.
- If during daylight hours a photovoltaic module is breached by a tool, clumsy foot, or roof ladder, up to 600 volts DC may be present at any point in the PV array. DO NOT breach PV modules for any reason! Use roof ladders to move around the sides of the PV array and access roof or chimney from a different location.
- MYTH BUSTER: When a PV array is not lit by daylight, it does NOT store electrical energy. To deactivate a PV array immediately during daylight, cover it with a tarp—however the tarp MUST be opaque, and must be secured. But be aware that electrical energy may still be stored in a battery bank located in the main building or in an outbuilding, and could still energize the array wiring at battery voltage (12-120 volts DC).
- Scene lighting is not powerful enough to create dangerous voltage. Lightning may be.

---
Disconnects
- All systems will have a central control point with MAIN and other disconnects.
- There may be multiple important disconnects (one for grid tie connection, one for battery bank, one for solar array, etc.) at the central control point.
- Disconnects may or may not be properly labeled.
- MAIN disconnects will NOT kill solar/wind source circuits outboard (distal of MAIN).
- Remote solar/wind source circuit disconnects may be difficult to identify and locate.
- Any disconnect could cut off power to well pump or cut off household water pressure.
- Disconnects may not look “typical.” :
Photo © Bella Energy - www.bellaenergy.com
Photo © State of Utah

---
More Sample Disconnects
- Most RE electric systems will have an integrated “Control Panel” where all central disconnects are located (shown in photos below), however:
- Some systems will have separate disconnect boxes for each source and branch.
- All of the above will be located close to the battery bank (if included) and be connected to it with very thick wires.
- Disconnects may not be properly labeled.
Photo © Oregonsolarhome.com
Photo © Rochester Solar Technologies

---
3 Types of RE Electric Systems:
1) Grid-tied, non-islanding (direct grid tie):
Drawing courtesy DOE/EERE
- System is interconnected with the utility grid.
- Electrical energy is generated on site, but is not stored—it is only bought or sold to the utility.
- During a grid blackout, the system no longer feeds or is fed by the grid, circuits in the house will be dead, but source (input) circuits will remain live.
- Can be found anywhere there are power lines.
- Do not include battery banks.

---
When main is killed, direct grid tie:
Red: Live at high voltage up to 600 volts, AC or DC.
Red circle: High voltage disconnect. (Large circle is MAIN),
small circle automatically disconnects when main is thrown)‏

---
3 Types of RE Electric Systems:
2) Off Grid:
- All electrical power is generated and stored on site, with no connection to the utility grid.
- Most common in remote and urban interface areas.
- Always include large battery banks.
- Usually obvious due to remote site location, lack of utility power equipment.

---
When main is killed, off grid:
Red: Live at high voltage (up to 600 volts, AC or DC)‏
Green: Live at battery bank voltage (12-48 volts DC typical, could be as high as 120 volts DC.)‏
Circle: Disconnect. Large circle is main, small circles automatically disconnect when main is thrown.

---
3 Types of RE Electric Systems:
3) Grid-tied, islanding:
- System is interconnected with the utility grid.
- Electrical power is generated and stored on site, but is also bought and sold from the utility.
- During a grid blackout, the system no longer feeds the grid (and the grid no longer feeds the system), but circuits in the house will be live.
- Most common in rural and urban interface areas.
- Always include large battery banks.

---
When main is killed, grid tie islanding:
Red: Live at high voltage (up to 600 volts, AC or DC).
Green: Live at battery bank voltage (12-48 volts DC typical, could be as high as 120 volts DC.
Circle: Disconnect. Large red circle is MAIN, Green MAIN must ALSO be thrown to disconnect household loads and feed circuits.

---
All disconnects and combiner boxes, typical:
Red: Live at high voltage (up to 600 volts, AC or DC).
Green: Live at battery bank voltage (12-48 volts DC typical, could be as high as 120 volts DC.
Circle: Disconnect. Firefighters will rarely if ever need to locate and open remote disconnects, but should be aware that they are available.

---
Specific Hazards, Battery Banks
- Voltage potentials may range from 12 to 120 volts DC, 12-48 volts most common.
- Hydrogen gas (explosive) is generated when batteries are charging, and it may or may not be properly vented.
- 99.9% of RE system storage batteries use a sulfuric acid electrolyte.
- In rare cases an alkaline sodium hydroxide electrolyte may be used (NiCad batteries and fuel cells).
- Battery bank interconnection wires may become red hot from bad connections or short circuits.
- Batteries are subject to thermal runaway.
- Batteries can breach and spill electrolyte from freezing temperatures, physical damage, or thermal runaway.
Photo courtesy DOE/NREL
Photo © Northern Arizona Wind and Sun

---
Specific Precautions, Battery Banks
- Use a dry chemical or CO2 extinguisher for a battery bank fire, NOT water.
- Battery bank circuits use very large wires and disconnects. If you must disconnect a battery bank, the disconnect will be both large and near the batteries.
- Be aware that even after opening the battery bank disconnect, source (solar and wind input) circuits elsewhere in the system will remain live at up to 600 volts.
- Be aware that explosive hydrogen gas may be present inside the battery box.
- To neutralize an acid battery electrolyte spill, use baking soda or lots of water.
- To neutralize a (very rare) alkaline battery electrolyte spill, use vinegar or lots of water.
- Using the wrong neutralizer is not hazardous, but has no effect. The correct one will bubble and fizz on contact with the electrolyte.
- To stop a battery in thermal runaway, disconnect or cut the wires between the problem battery and the rest of the battery bank, then remove and cool battery with water outdoors if possible.
- A wrench or other metal tool accidentally dropped across the terminals of even a small RE battery can become red hot in under 3 seconds.

---
Specific Hazards, Wind Turbines
- This document covers ONLY “small” wind turbines that power a single home, with rotor diameters of 3 feet up to 30 feet. It does NOT cover larger, utility-scale turbines.
- Voltage potentials may range from 12 to 600 volts, AC or DC, single or 3 phase.
- Wind turbine towers and tower guy wires are vulnerable to weakening and failure from wildfire encroachment.
- Wind turbines are almost always mounted on very tall towers.
- Wind turbine controls may or may not be properly labeled.
- Wind turbine electrical disconnects are different from wind turbine shut down switches.
- During high winds (above 40 mph), throwing the wrong disconnect (including disconnecting the battery bank) could (in very rare cases) cause turbine failure and flying debris.

---
Specific Precautions, Small Wind Turbines
- As a firefighter your primary task in dealing with a wind turbine is to protect the tower and guy wires from heat and flame!
- While a fast moving grass fire is unlikely to affect guy wires, there may be wood or brush around the guy wire anchor that could cause more serious heat exposure.
- If the tower or guy wires have been compromised by flame, treat it as a “killer tree” and use extreme caution. Flag the tower as such, and consider flagging the perimeter of the fall zone. Think of the tower as a flyswatter, and you as the fly.
- Upon evacuation notice, the homeowner should shut down the turbine before leaving the area. This will kill the source circuit from the tower to the system control point, but battery bank voltage may still be present from battery bank to controller.
- A spinning wind turbine will produce source voltages of 12 to 600 volts, AC or DC, that could remain present in parts of the system even if the “MAIN” disconnect is opened (just like with PV panels).
- Look for a switch at the RE system control point labeled “Wind Turbine Shutdown” or “Wind Turbine Stop” if you need to stop the turbine from spinning and therefore kill the source circuit.
- If the firefighter is in doubt and switches are not labeled, DO NOT throw any wind turbine switches. Let it be, spinning or not. Non-electrical hazards to firefighters are minimal.
- SMALL HYDRO TURBINES are similar to wind turbines electrically—you may not know how to shut it down so that it no longer spins. Let it spin, non-electrical hazards are minimal.

---
Backup Generator Hazards and Precautions
- Voltage potentials may range from 12 to 480 Volts, AC or DC, single or 3 phase, and may be present in some circuits even when the “MAIN” disconnect is opened.
- Fuels may include gasoline, diesel, propane, or natural gas.
- Generators may be located inside outbuildings, with exhaust directed outdoors.
- Generators may be so quiet that you are not aware they are on.
- Overheated disconnect and junction boxes and improperly sized wires are common causes of fires from generators.
- Be aware that the generator may be the only way to power the well pump at the residence.
- Most generator installations have disconnects both at the machine, and at where the source wires connect to the system (just like solar, wind and hydro).
- Watch for generator fuel lines, and fuel stored both inside and outside all outbuildings!

---
Summary for Firefighters:
- Don't hang anything from any type of RE system roof or pole mounts. Especially you.
- Identify the type of system you are dealing with and be aware of specific hazards for that system—electrocution, overheated wires and boxes, hot liquids, broken glass, chemicals, and fuels.
- Assume all electrical wires are live and lethal, no matter what disconnects have been opened.
- If you can't identify the system:
- Don't break anything that's covered with or made of glass or plastic, and assume the guts of it are electric, live and lethal.
- Don't hang roof ladders from or in contact with anything covered with or made of glass.
- Don't cut wires, conduit or pipes.

---
Summary for administrators who have to write SOPs and SOGs
RE SYSTEMS:
- Are no more dangerous to firefighters than homes connected only to the utility electrical grid, IF firefighters identify what they are dealing with and are aware of a few specific hazards and precautions.
- Are increasingly common in urban, rural, and urban interface communities—in other words, everywhere.
- May or may not be connected to utility grid power lines.
- Could include solar electric panels, solar water or air heating panels, wind turbines, small hydro turbines, and gasoline, diesel, and propane backup generators.
- May use voltages ranging from 12 to 600 volts, AC or DC.
- Will have a central control point that may located in the house or in an outbuilding.
- Include indoor and outdoor electrical feed circuits that can remain live even if the main disconnect is opened. Multiple disconnects at different locations are very common and may not be obvious or easily accessible.
- May limit roof access, and may not be mounted with proper roof setbacks and access pathways.
- Will power household water pressure, but may or may not be able to power on-site water well pumping.
- Can pose chemical hazards from large battery banks.
- Can cause falling object hazards from wind turbine and PV towers.
- May or may not be properly permitted, labeled and installed.

---
Document information:
- This Revision 2 dated 1/26/2009, Copyright 2009. Distribution within the fire service and professional RE community is allowed and encouraged. Please contact the author regarding further distribution, as copyright use permission for the included photos has been obtained only for these uses.
- This document by Dan Fink.
- Author information: Dan Fink has been a firefighter for the Rist Canyon Volunteer Fire Department for 10 years, and has lived off-grid in a remote corner of their response area for 18 years, 11 miles from the nearest utility electric or phone line. He is a Firefighter 1 and First Responder, with a BA in Technical Journalism from Colorado State University. He spent 10 years as a renewable energy system consultant, designer and installer, and has been employed as a renewable energy technical author and educator since the year 2000. He is co-author of the book “Homebrew Wind Power,” and his articles and photographs frequently appear in such magazines as Home Power, Back Home, the Energy Self Sufficiency Newsletter, and Lighting Today. He is an on-call “Ask the Experts” columnist for Home Power Magazine.
- Contact: Dan Fink, PO Box 292, Masonville CO 80541. danbob@otherpower.com
- The contents of this document are for general firefighter safety information ONLY. Renewable energy technology, installation techniques, and industry best practices change rapidly and without warning. Nothing in this document is intended to represent compliance with NEC, UBC or local building and electrical codes.
- The author is available in the Northern Colorado area to give this presentation in person for fire training with other departments, and be available for questions and answers. Please contact if interested.