DIRECTORY OF MODIFICATIONS

| INDEX | DATE | DESCRIPTION |
| --- | --- | --- |
| Rev A | 2009/11/16 | First issue: After ID Rev A checking |
| Rev B | 2009/12/21 | After ID Rev B checking |
| Rev C | 2010/01/15 | After IO list TC2Alpha_E0872_10_12_2009, ID 136B5756 Rev C and drawing completion checking |

Project references

This test report is referred to the Turbine Control Compartment for Iraq Mega Deal-Project B, under the scope of supply described within the purchase order number: 104-482465, 104-482473, 104-482477 104-482481.

.

- Equipments

| PEECC Fabrication Number | PEECC-IT-2010/01 to 04 |
| --- | --- |
| Components | Designation |
| Auxiliary Control Panel | TRE CAB 500 |
| Turbine Control Panel | TRE CAB 503 |
| Operator Interface Panel | TRE CAB 504 |
| Generator Control Panel | TEX CAB 502 |
| Battery Chargers | LBA BYC 001 LBA BYC 002 LNA INVT 001 |
| Fire Fighting panel | TPT CAB 001 |
| Motor Control Center | LKA BKR 001 LKA BKR 002 LKA ECBD 001 LKA ECBD 002 LKA ECBD 003 LKA ECBD 004 LKA ECBD 005 LKB ECBD 001 LKB ECBD 002 LKB ECBD 003 LBA ECBD 001 LBA ECBD 002 LKB XFMR 001 LKB XFMR 002 |

- Equipment drawings and setting specifications

| Turbine Control Compartment (PEECC): | Reference | Rev. | GEEPE SNC. Ref. |
| --- | --- | --- | --- |
| Lighting and air conditioner Schematic Diagram | IT0031-22-111 | B |  |
| General/Equipment Arrangement | IT0031-53-101 IT0031-64-101 | A A |  |
| Part List | IT0031-25-111 | A |  |
| Interconnection Diagram |  | C | 136B5756 |
| Setting Specification | ESP-32-IT0031-111 | A |  |
| Test Procedure |  |  |  |
| Motor Control Center (MCC) |  |  |  |
| General Arrangement drawing | IT0031-42-110 | B |  |
| Single Line Diagram | IT0031-21-101 | C |  |
| Schematic Diagram | IT0031-22-101 | B |  |
| Part List | IT0031-25-101 | A |  |
| Setting Specification | ESP-32/IT0031-110 | A |  |
| Internal Arrangement | IT0031-42-111 | A |  |
| Auxiliary Panel (TRE CAB500) |  |  |  |
| Electrical Diagram | N.A. | A | 09I11-AUX-038 |
| Part List | IT0031-25-112 | A |  |
| General Arrangement | IT0031-42-113 | A |  |
| Turbine Control Compartment (TCC): | Reference | Revision | GEEPE SNC. Ref. |
| Battery 125Vdc | - | - |  |
| Battery Charger + Inverter LBA BYC001-2 LNA INVT 001 | 63763 | 01 |  |
| Operator Interface Panel (TRE CAB504) | IT0031-42-1103 IT0031-42-1104 | A |  |
| Generator Control Panel (TEX CAB502) |  | A | 226B7495ED |
| Turbine Control Panel (TRE CAB503) |  |  |  |
| Fire Fighting panel (TPT CAB001) |  | A | SA-013185-004 |

* Means that a forthcoming revision is going to be issued

- Date and Validation

| Tests Validated By Responsible Test Technician Inabensa | Technical Project Leader Inabensa |
| --- | --- |
| Name: | Date: 2010/1/15 | Name: | Date: 2010/1/15 |
| Alex Liu Haitao |  | Carlos García-Valdecasas Merino |  |

- After Preliminary Inspection Phase of the Interconnection Diagram

| Topic | Date | GE Response | Date response |
| --- | --- | --- | --- |
| The following signals are not defined or completed in Interconnection Diagram. Please update the interconnection diagram to provide this information. On red are the cells with missing information The following signals are still not defined or completed in Interconnection Diagram Rev B. Already solved in ID Rev C. | 2009/11/16 2009/12/21 2010/1/15 |  |  |
| The following air condition signals are not defined in Interconnection Diagram. Please update the interconnection diagram. This point is still not corrected in interconnection diagram Rev B. Already solved in ID Rev C. | 2009/11/16 2009/12/21 2010/1/15 |  |  |
| According the MCC schematic diagram Rev B, X18-2 should connect to BYC001 X1-7, X18-1 should connect to BYC001 X1-8, X18-5 should connect to BYC002 X1-7, X18-4 should connect to BYC002 X1-8. Please update the interconnection diagram. Already solved in ID Rev C. | 2009/12/21 2010/1/15 |  |  |
| The fault contacts of the battery charger included on the signals 27BL-1, 27BL-2, according to the interconnection diagram Rev B, these contacts are NC. In MCC schematic diagram Rev B both battery chargers have been changed to NO. Please, reflect this modification in the interconnection diagram, changing the wiring from 9-11 to 9-10. Already Solved in ID Rev C. | 2009/12/21 2010/1/15 |  |  |
| The AC power supply of gas detection system (A500) comment is “Gas detection rack 230VAC ups power supply” in ID Rev C line 2965. According to the ID Rev C and MCC load list, this power supply is located in 230Vac bar. Therefore, it is not connected in the UPS 230Vac bar, so that the comment in the ID should be wrong. For this reason the ID comments should be corrected by removing the “ups” word. | 2010/1/15 |  |  |
| According to the PEECC schematic diagram, the air conditioning control cable connection is wrong in ID line 3127. The right connection is shown in the attached document. Please update the ID accordingly. | 2010/1/15 |  |  |
| According to the IO list and ID Rev C, the signal 45FTX belongs to logic output relay type, located in 1G5A card relay 11. IT thinks this signal should be a logic input contact signal. Please check it. | 2010/1/15 |  |  |
| In the ID Rev C, they are defined two cables connected to one terminal block in the speedtronic. Please find here attached document and IT comments. | 2010/1/15 |  |  |
| Following signals are indicated in the IO as wired, but they are not in the ID, Please find here attached document and IT comments. | 2010/1/15 |  |  |
| Following logic output signals jumpers are not right, the right jumper configuration is shown in the attached document. Please check it. | 2010/1/15 |  |  |
| According the ID rev C, all analogy input signals located in 1B2A and 1B3A cards that are connected to "20mA" and "return" terminals, according to the ID, need to change the jumper from "2-3 P_COM" to "1-2 Open". But according to I/O list, we need modify the connection to "P24+ and "20ma" terminal. Please find here attached the list of signals with such problem (coloured on yellow) and advise if they should modify the jumper or the wiring. | 2010/1/15 |  |  |

- MCC

No issues after preliminary drawing completion phase

- Fire Fighting Panel

No issues after preliminary drawing completion phase

- Speedtronic:

No issues after preliminary drawing completion phase

- HVAC :

No issues after preliminary drawing completion phase

- Auxiliary panel :

No issues after preliminary drawing completion phase

- Generator Control Panel:

No issues after preliminary drawing completion phase

- Battery Charger :

No issues after preliminary drawing completion phase

- PEECC :

No issues after preliminary drawing completion phase

- After Tests

N/A

- Tests not performed

N/A