Temperature Distribution
Linear Thermal Transmittance / W/m.K
Ψ =	0.05

General Construction Specification: / (see detail below for full construction)		Main/Load-bearing:	140mm Stud Wall
		Insulation:	100mm PU/PIR, λ=0.023
		Cavity:	50mm Low-e, Glidevale Protect2000Thermo (or equal)
		Cladding:	102mm Brick, λ=0.77
Description:	140mm stud wall, External Corner
Reference:	External corner detail

Issued to:
Jamie Roe
Roe Timber
Roe Limited
Enterprise Road
Westwood Industrial Estate
Kent
CT9 4JA
T: 01843 232888

Junction Detail

Certificate No:	C4TM – 000273	Issued:	10/03/10

Temperature Factor3 for Humidity and Mould
f =	0.89

Calculation Prepared By:	Matthew Wright MA Physics (Oxon) PGCE

Notes: -
1. Ψ and f are only valid for the detail drawn and described above.
2. U-values for the flanking walls are within the range of U = 0.23 W/m2.K or less.
3. In dwellings, a temperature factor f that is >0.75 would avoid the risk of mould growth.
4. Calculations have been performed in accordance with:
  1. EN ISO 10211_2007 (British Standards)
  2. IP 1/06 & BR497 (BRE Press)
and with reference to the following publications:
- EN ISO 6946 (British Standards)
- BR443 (BRE Press)