## Problems:

The OPTIONAL property as defined in the standard does not explicitly restrict proprietary properties.

Additionally, the text for the special property ALL uses the words "defined properties" or just "properties" which could indicate all the properties that are defined for a particular object in the standard, even if those properties are not implemented or supported. The testing standard 135.1 typically uses the word "supported" in reference to implemented functionality.

## Change History:

1 - 20-Jan-2006: Created document.

2 - 06-Feb-2007: added "present and readable" to 15.6.1.1.2 based on feedback from OS-WG Atlanta 2006 meeting minutes.

## References:

ANSI/ASHRAE Standard 135-2004, “BACnet®, A Data Communication Protocol for Building Automation and Control Networks”

## Document Conventions

Italics are used to indicate changes or additions to the standard.  Strike-through is used to indicate deletion from the standard.

## Changes To Standard 135

[Change 15.6.1.1.2 List of Property References page 322]

15.6.1.1.2 List of Property References

This optional parameter, if present, shall be a list of one or more BACnetPropertyReferences, each of which corresponds directly to a specific property of any object selected on the basis of the 'Object Selection Criteria'. Specifying the property ALL indicates that all supported present and readable properties of any selected object shall be returned, including any proprietary properties. Specifying the property REQUIRED means that only those non-proprietary properties having a conformance code of "R" or "W" shall be returned. Specifying the property identifier OPTIONAL means that only those non-proprietary properties that have a conformance code of "O" shall be returned. See the specification for the particular object type in Clause 12. If this parameter is absent, no properties shall be returned in the 'List of Read Access Results' portion of the 'Result(+)' primitive; however, the object identifier shall be returned in the 'Object Identifier' parameter.

[Change 15.7.3.1.2 List of Property References page 329]

15.7.3.1.2 List of Property References

This parameter shall be a list of one or more BACnetPropertyReferences, each of which corresponds directly to a specific property of the object identified above. The property identifier ALL means that all supported defined properties of the object are to be accessed, including any proprietary properties. The property identifier REQUIRED means that only those non-proprietary properties having a conformance code of "R" or "W" shall be returned. The property identifier OPTIONAL means that only those non-proprietary properties that have a conformance code "O" shall be returned. See the specification for the particular object type in Clause 12.