Calculation of Contingency Shift Factors
Method for calculation of contingency shift factors from base case shift factor matrix in the PLEXOS software
# Calculation of Network Sensitivity Factors
First we show how to derive the generation-shift sensitivity factors. To start:

bold %theta =[X]bold P	(11A.1)

This is the standard matrix calculation for the DC load flow. Since the DC power-flow model is a linear model, we may calculate perturbations about any given set of system conditions by use of the same model. Thus, if we are interested in the changes in bus phase angles, bold %DELTA bold %theta , for a given set of changes in the bus power injections, bold %DELTA bold P , we can use the following calculation.

bold %DELTA bold %theta = [X] bold %DELTA bold P	(11A.2)

In Eq. 11A.1, it is assumed that the power on the swing bus is equal to the sum of the injections of all the other buses. Similarly, the net perturbation of the swing bus in Eq. 11A.2 is the sum of the perturbations on all the other buses.

Suppose that we are interested in calculating the generation shift sensitivity factors for the generator on bus i. To do this, we will set the perturbation on bus i to +1 and the perturbation on all other buses to zero. We can then solve for the change in bus phase angles using the matrix calculation in Eq 11A.3.

bold %DELTA bold %theta = [X]left [ stack {+1# -1} right ] stack {alignl nitalic - row i#alignl nitalic -ref nitalic row}	(11A.3)

The vector of bus power injection perturbations in Eq. 11A.3 represents the situation when a 1 pu power increase is made at bus i and is compensated by a 1 pu decrease in power at the reference bus. The %DELTA %theta values in Eq. 11A.3 are thus equal to the derivative of the bus angles with respect to a change in power injection at bus i. Then, the required sensitivity factors are:

a_{li} = {df_l over dP_i} = {bold d over dP_i}[bold 1 over x_l (%theta_n - %theta_m)] newline alignl {} = 1 over x_l left ( d %theta_n over d P_j - d %theta_m over d P_i right ) = 1 over x_l ( X_{n i} - X_{m i} )	(11A.4)

where:

X_{n i} = {d %theta_n} over {d P_i} = n^{"th"} nitalic "element from the" bold %DELTA bold %theta "vector in Eq. 11A.3"
X_{m i} = {d %theta_m} over {d P_i} = m^{"th"} nitalic "element from the" bold %DELTA bold %theta "vector in Eq. 11A.3"
x_l = "line reactance for line" l

A line outage may be modeled by adding two power injections to a system, one at each end of the line to be dropped. The line is actually left in the system and the effects of it being dropped are modeled by injections. Suppose line k from bus n to bus m were opened by circuit breakers as shown in Figure 11.16. Note that when the circuit breakers are opened, no current flows through them and the line is completely isolated for the remainder of the network. In the bottom part of Fiture 11.16, the breakers are still closed but injections %DELTA P_n and %DELTA P_m have been added to bus n and bus m, respectively. If %DELTA P_n = tilde {P}_{nm} , where tilde {P}_{nm} is equal to the power flowing over the line, and %DELTA P_m = - tilde {P}_{nm} we will still have no current flowing through the circuit breakers even though they are closed. As far as the remainder of the network is concerned, the line is disconnected.

Using Eq. 11A.2 relating to bold %DELTA bold%theta and bold %DELTA bold P , we have:

bold %DELTA bold %theta = [ X ] bold %DELTA bold P

where:

bold %DELTA bold P = left [ stack {dotsvert # %DELTA P_n # dotsvert # %DELTA P_m } right ]

so that:

%DELTA %theta_n = X_{n m}%DELTA P_n + X_{n m}%DELTA P_m newline %DELTA %theta_m = X_{m n}%DELTA P_n + X_{m n}%DELTA P_m	(11A.5)

define:

%theta_n,%theta_m,P_{n m} to exist before the outage, where P_{n m} is the flow on line k from bus n to bus m
%DELTA%theta_n,%DELTA%theta_m,%DELTA P_{n m} to be the incremental changes resulting from the outage
tilde %theta_n,tilde %theta_m,tilde P_{n m} to exist after the outage

The outage modeling criteria requires that the incremental injections %DELTA P_n and %DELTA P_m equal the power flowing over the outaged line after the injections are imposed. Then if we let the line reactance be x_k :

tilde P_{n m}=%DELTA P_n=-%DELTA P_m	(11A.6)

where:

tilde P_{n m}=1 over x_k left ( tilde %theta_n - tilde %theta_m right )

then:

%DELTA%theta_n = left ( X_{n n} - X_{n m} right ) %DELTA P_n newline %DELTA%theta_m = left ( X_{m m} - X_{m n} right ) %DELTA P_m	(11A.7)

and:

tilde %theta_n = %theta_n + %DELTA%theta_n newline tilde %theta_m = %theta_m + %DELTA%theta_m	(11A.8)

giving:

tilde P_{n m} = 1 over x_k left ( tilde %theta_n - tilde %theta_m right ) = 1 over x_k left (%theta_n - %theta_m right ) + 1 over x_k left ( %DELTA %theta_n - %DELTA %theta_m right )	(11A.9)

or:

tilde P_{n m} = P_{nm} + 1 over x_k left ( X_{n m} + X_{m m } - 2X_{n m} right ) %DELTA P_n

Then (using the fact that tilde P_{n m} is set to %DELTA P_n ):

%DELTA P_n = left [ 1 over {1-1 over x_k left ( X_{n n} + X_{m m} - 2X_{n m} right )} right ] P_{n m}	(11A.10)

Define a sensitivity factor %delta as the ratio of the change in phase angle %theta , anywhere in the system, to the original power P_{n m} flowing over the line nm before it was dropped. This is:

%delta_{i, n m} = {%DELTA%theta_i} over {P_{n m}}	(11A.11)

If neither n nor m is the system reference bus, two injections, %DELTA P_n and %DELTA P_m , are imposed at buses n and m respectively. This gives a change in phase angle at bus i equal to:

%DELTA%theta_i = X_{i n}P_n + X_{i m}%DELTA P_m	(11A.12)

Then using the relationship between %DELTA P_n and %DELTA P_m , the resulting %delta factor is:

%delta_{i, n m}={left ( X_{i n} - X_{i m} right ) x_k} over {x_k - left ( X_{n n} + X_{m m} - 2X_{n m} right )}	(11A.13)

If either n or m is the reference bus, only one injection is made. The resulting factors are:

%delta_{i, n m} = {X_{i n} x_k} over {left ( x_k - X_{n n} right )} " for " m " = ref" newline %delta_{i, n m} = {X_{i m} x_k} over {left ( x_k - X_{m m} right )} " for " n " = ref"	(11A.14)

If bus i itself is the reference bus, then %delta_{i, n m} = 0 since the reference bus angle is constant.

The expression for d_{%scriptl, k} is:

d_{%scriptl,k} = {%DELTA f_l} over {f^0_k} = {{1 over x sub %scriptl} left( %DELTA%theta_i - %DELTA%theta_j right )} over {f^0_k} newline {}= 1 over x sub %scriptl left [ {%DELTA%theta_i} over {P_{n m}} - {%DELTA%theta_j} over {P_{n m}} right ] newline {}= 1 over x sub %scriptl left ( %delta_{i,n m} - %delta_{j,n m} right )	(11A.15)

If neither i nor j is the reference bus:

d sub {%scriptl,k}=1 over x sub %scriptl left [ {left ( X sub {i n} - X sub {i m} right ) x sub k - left ( X sub {j n} - X sub {j m} right ) x sub {k}} over { x sub k - left ( X sub {n n} + X sub {m m} - 2 X sub {n m} right ) } right ] newline {}= {{x sub k over x sub %scriptl} left ( X sub {i n} - X sub {j n} - X sub {i m} + X sub {j m} right )} over {x sub k - left ( X sub {n n} + X sub {m m} - 2 X sub {n m} right ) }	(11A.16)

The fact that the a and d factors are linear models of the power system allows us to use superposition to extend them. One very useful extension is to use the a and d factors to model the power system in its post-outage state; that is, to generate factors that model the system's sensitivity after a branch has been lost.

Suppose one desired to have the sensitivity factor between line l and generator bus i when line k was opened. This is calculated by first assuming that the change in generation on bus i,??, has a direct effect on line l and an indirect effect through their influence on the power flowing on line k, which in turn, influences line l when line k is out. Then:

???

However, we know that:

???

therefore,

We can refer to ??? as the “compensated generation shift sensitivity”.

The compensated sensitivity factors are useful in finding corrections to the generation dispatch that will make the post-contingency state of the system secure from overloads. This leads to a security constrained optimal power flow.