Abstract: We have chosen to keep the offered location and data about Darsilami in Gambia. However, as we had had a lot of informations about the SMA products but not much about other manufacturers, we chose to realize the project without using any of their products. This could lead to a less optimal result, technically and economically, but the purpose of this choice is for us to gain a wider view of available hardware on the market.
Gambia Project Report
Manfred Amoureux, Julien Herbreteau, Alan Cuddihy
Kassel Universität

Keywords: hybrid system, solar home systems, mini-grid, rural electrification, developing countries, Gambia, photovoltaic, inverters.
Resources and conditions assessment
A resources assessment table is available in Annexe 1.
  1. Hydro
There is a river in medium distance (1,4 km from the centre of the village).
- No data available about seasonality of the river and technical conditions of the flow
- Very low variation of altitude, many meanders so flat field thus very low head: weak potential for hydro power
  1. Wind
We used NASA databases.
- Same values for 2 cities (Gunjur & Brikama) located close to Darsilami (10km) in 2002
- Averaged values for a 10 years period (1983-1993) located in 13°N, -16°W
- Low average wind speed (< 5 m/s, too low)
  1. Sun
- Horizontal irradiation : average of 4 data sources (PVGIS, NASA, SoDa: NCEP & HelioClim)
- Optimal angle for a stand alone system: 22° S
- We use the “k” factor from PVGIS to calculate the irradiation at the chosen angle.
  1. Biomass - Fuels
Gambia is second largest producer of peanut per capita in the world. Peanut can be easily transformed into vegetable oil, and is usable as fuel for the diesel gensets with little modification.
We estimated the average price of peanut oil to 0,50 € / L.
Assumptions:
- peanut oil is available in the area.
- its selling price is lower than the diesel oil.
- Some of the gensets installed in the village are diesel engines (and not gasoline).
  1. Temperature
We averaged values from 3 sources (NASA, MeteoTest & NCEP). Temperature is relatively constant : 25°C.
  1. Humidity
One source is used: SoDa (averaged values of 65% of humidity for a 15 years period (1990-2004)).
  1. Already available equipment
Assumptions:
- all 3kW gensets are single-phase air cooled gasoline engines with short lifetime
- all 5kW gensets are single-phase air cooled diesel engines with short lifetime
- it was said that some of the houses type 4 have very small gensets, we considered that 2 out of 4 houses have 1 kW one-phase gasoline gensets.
- Diesel gensets in use for the minigrid (7kW and more) are industrial grade gensets with 2 pairs of poles, 3 phases and liquid cooled (most efficient way of warming up the vegetable oil).
1. Demand assessment
  1. Load profile
Seasonal variations are almost non-existent. Each load profile is shown in Annexe 2.
### Case 1 (SHS)
Building type	Nb	Daily consumption / building (Wh)	Peak Load / building (W)
Lodge	2	1600	400
Churches	3	400	110
Schools	2	1200	400
Disco	1	4800	1200
Cinema	1	1400	500
Offices	5	12000	1000
Nurseries	2	660	110
HCE	1	200	200
Juice factory	1	45000	3750
House type 1	32	274	33
House type 2	12	294	43
House type 3	10	670	125
House type 4	4	3590	700

### Case 2 (Minigrid)
The load profile for the mini grid is shown in Annexe 2.
- Average demand: 145 kWh / day
- Peak demand: 13 kW
  1. Appliances
We included in the budget the purchase of the following appliances (characteristics in Annexe 2):
- all lightings
- all fridges
- radios and TVs
- fans
Indeed, letting the inhabitants purchase themselves the appliances would probably result in having them purchasing inadequate products.
  1. Stand-by power
None of the appliances listed has a standby mode, except maybe for the equipments of the disco and cinema, which can anyway be assumed to be switched off properly since they are not in use on a daily basis.
1. Pre-design
  1. Case 1: SHS (Standalone Home Systems)
### DC or AC ?
Due to the short distances, DC bus will be used in most cases, as DC appliances can be found most uses and small affordable DC/AC converters can be found for the few uses requiring them.
It is expected that the additional cost of buying those appliances over the whole lifetime of the system will be smaller than buying island inverters.
The bigger consumers, especially those who have gensets have been put in single-phase AC.
### Pure solar , genset only or hybrid ?
Some houses already have available gensets. They are bigger consumers to which AC current will be provided. It seemed sound to consider keeping the genset and going for a small hybrid system.
We just ran some simulations using HOMER for each one of the 3 types of buildings which are candidates to using an hybrid system, for both cases:
- pure solar system (no genset) with only a DC bus.
- hybrid system (PV + existing genset) with an inverter and load supplied in AC.
We also compared the results with calculations made with the spreadsheets. Results were:
- Juice Factory: hybrid system is best, with a solar fraction of around 0,7.
- Offices: the resulting costs for the kWh of electricity are similar (1% difference), as well as the initial investment (8% difference). In the case of the hybrid solution, the solar fraction is above 0,9.
- Houses type 4: same results (costs and investments are similar, solar fraction is above 0,9).
The hybrid system has the advantage to be more flexible, would the demand increase, or the would the design be undersized, so we favoured it.
### Buildings left apart
Some buildings are only used a few hours a week. Installing a system with PV panels and batteries is expensive compared to the few kWh that are used every year. After economic calculations, it was found that keeping the genset is a better option.
The HCE and the PV pump already having autonomous systems. It was chosen not to change them.
### Summary
Building type	Consumption (kWh / week)	Solution
Houses type 1, 2, 3	< 5	DC
Houses type 4 with no genset	25	DC
Houses type 4 with very small genset	25	AC (hybrid )
Lodges, Churches, Schools	< 6	DC
Disco + Cinema	5,2	AC (genset only)
Offices	72	AC (hybrid)
Juice Factory	270	AC (hybrid)

Connection schemes are shown in Annexe 3.
  1. Case 2: Full minigrid
An AC bus will be chosen with 3 phases. A higher voltage is necessary due to the long distances of transmission.
### Scope of study
As in the previous case, the HCE was left apart from the study, except we considered connecting it to the grid. The island inverter would then be set into 'grid following' mode.
The PV pump was integrated to the grid via a bidirectional inverter. Any excess energy produced by the PV panel can then be integrated in the grid while the pump will still be operational in case of grid or PV failure. The usual command system that stops the pump when the tank is full is left in place and a circuit breaker is added for safety.
### Method
Quick calculations based on the previously established load profile are done on spreadsheets to get a first approximation of the total size of PV panels and batteries.
Those values were used for a starting value of sizing in HOMER.
### Sub-case 1: diesel oil
In the first case (“classical”), the diesel gensets are powered “normally” with diesel oil.
### Sub-case 2: vegetable oil
An alternative case in which the diesel gensets are powered with peanut oil has been studied.
Costs for adapting the gensets have been established using the following configuration:
- additional feeding pump before the filters and the injection pump
- heat exchanger to warm-up oil using the cooling liquid (can be made in the country at a local workshop with welding tools quite easily).
- additional electric heater at the injection nozzle (especially useful for cold starting).
Prices were found in specialized web sites and through personal contacts (Aeden.fr , Mecaoil , Seeflex).
The total cost is estimated below 300€ / genset, including manpower. Costs of O&M are typically increased (+20%) due to a higher supervision, and the requirement to filter oil, either before filling the fuel tank or in the injection line.
### Disposition of facilities
Power production, storage and transformation will be concentrated in the same facilities, in order to facilitate maintenance and reduce nuisances.
It is also a requirement that the PV panels be connected directly to the island inverter.
  1. Case 3: Mixed solution (minigrid + SHS)
### Discussion
Obviously, the SHS solution has two main drawbacks:
- equipments must be oversized to supply demand even during days of low irradiation.
- multiplying the number of small sizes equipments is costly.
In the other hand, the pure mini-grid system shows one limitation:
some small-time consumers are pretty much isolated for the rest of the village. Laying out power lines over hundreds of meters to supply less than 1 kWh / day is expensive both in money and losses in the transmission system.
Therefore, a mixed solution, with a minigrid for most of the village, with a few SHSs for the small isolated consumers is studied.
In the case of a small group of isolated buildings (such as houses 29 to 33), we considered setting up small micro-grids for those sets of buildings.
### Definitions
To avoid confusions, the following terms will be used now on:
- standalone system: a building which has its own power supply completely independent from others (such as pure solar systems working a DC bus).
- mini-grid: the grid laid for the whole village, except for the areas which are too isolated.
- micro-grid: a very small grid laid between 2 or 3 neighbouring buildings isolated from the rest of the village.
### Analysis of constraints
- the comparison for each isolated building (or set of neighbouring buildings) between the cost of extending the grid and setting an isolated system (micro-grid or standalone).
- the possibility of further extending the local grid to absorb those houses, would the village extend.
The last constraint, plus the expectation that micro-grids would be the cheapest solution, has led us to favour this solution.
1. Design
  1. SHS
The voltage of the DC buses were chosen accordingly to the demand of each building type. Equipments are detailed in Annexe 5.
### Overcharge and Deep discharge
All the systems have a charge controller (Xantrex C35 or C40) connected to the PV panels, which will take care of disconnecting the PV panels from the batteries in case of excess of energy. They also do DC-DC converter and have a MPPT system.
The same systems are used (on a different mode) to connect the battery to the load, working as DDP.
  1. Minigrid
### Characteristics of the AC bus:
- 3 phases. Buildings are connected in single-phase, except for the biggest consumers (juice factory), connected in 3 phases.
- Voltage and frequency will comply with Gambia's national standard: 230 V, 50 Hz
### Energy excess management
The PV panels are connected directly to the island inverter (CONERGY ISA) which, in addition to have MPP tracking, will take care of disconnecting the PV panels from the batteries in case of excess of energy. Equipments are shown in Annexe 5.
### Reactive power
The only consumer from which we expect significant reactive load is the juice factory. In case it is required, we would add some capacitors directly on the factory site.
### Power lines layout
The possible layout of the power lines was studied using the map. A simple arborescent layout pattern was chosen. The total length of the power line was found at 10 km.
To size the lines, the main arteries were identified and their lengths summed (cf. Annexe 4)
The current going through the power lines is rated as following:
- Main arteries (4 km in 4 main branches). 5 kW max. It is considered that no branch will be longer than 1 km. Cost: 10k€/km
- Smaller arteries (6 km in several dozen branches). 1 kW max. No branch is longer than 500 m. Cost: 3,5k€/km
  1. Mixed solution (Minigrid + SHS)
### Buildings not connected to the grid
In addition to the buildings which were already not connected, will not be connected:
- Houses 02, 44, 45, 46, 64 and 74, which will be supplied with a SHS each.
- Houses 29 and 30 which will share a SHS together (equivalent to type 3).
- Houses 31, 32, 33 which will share a SHS together (equivalent to type 3).
Altogether, this add 4 SHS type 1 and 4 SHS type 3 (for an additional cost of 19k€), and save 2,8 km of cable (20k€).
The decrease of demand on the minigrid is not sensible (about 1,5 % for power and energy) and therefore its design is left unchanged.
The saving will mainly be on the fuel not consumed.
  1. Hardware choice
### Inverters and converters
The following manufacturers' products were reviewed: KACO , Conergy , Xantrex , Mastervolt , Outback , Victron , Dorfmueller, Leonics, Fronius, Satcon, Suntechnics, Studer, PowerMaster, Sunways
We chose the island inverters first, as the choice of is scarcer, and the rest of the electronics afterwards.
We also decided to avoid having products from too many different manufacturers.
### PV panels
Dmsolar manufactures the complete line of "Brightwatts" solar modules ranging from 5w to 220w with UL, TUV and FSEC approval.
Chosen PV model : BrightWatts, guaranteed 25 years of working life time.
  1. Gensets starters and synchronizers
For SHS with gensets, the start/stop will be done manually by the users, who already know the management of gensets and live on site. They will have to be trained to know when to start and stop the genset.
The Xantrex SW inverters include 2 modes of functioning with gensets, one for controlled gensets and the other one for uncontrolled genset.
For the big genset of the minigrid, the start/stop is done automatically through relays by the island inverter.
1. Protections
  1. Peak loads
### Case 1 (SHS)
#### Motor starters of the Juice Factory
The motor of the factory is rated at 3,75 kW. Since it is started only once or twice a day, it was chosen equip the motor with a resistive or capacitive starter, and to train the staff (which may be considered professionals) at using it.
#### Gensets
As all the gensets are small portable equipments, they have their own power source for starting up.
### Case 2 (Minigrid)
The island inverter is capable of providing enough power for the starting of both the motor of the factory and the genset.
  1. Fuses
The island inverter is powerful to activate the circuit breakers.
For SHS system we use a DC circuit breaker after the inverter with a current depending on the load. Before each building with a AC system, a Residual Current breaker with Over Current protection is used with a sensitivity of 500mA and a rating current depending of the maximum of current in the line.
For the grid we use 11 circuits breakers in order to protect people during maintenance or if a fault occurs.
Economical calculations
Project lifetime: 20 years. Used currency: €.
Rate of interests: 8%
Refer to annex ??
  1. Discussion
The resulting costs are high. It must be remembered that the costs estimation were quite conservative, including hight transportation fees, unlisted accessories, and high interest rate.
1. Social issues
  1. Social and Economical Impact Study in Darisalami
Following activities will be conducted using a participatory approach:
- Investigation of social structures
- Analysis of productive activities and potentials of evolution
- Anticipation of social impact
  1. Payment and initial investment
### Payment
For payments, different solution are possible in the case 1 and 3:
- People pay according the type of installation they have
- Everybody pays the same price
We recommend the 2nd solution, because:
- it will simplify the accounting
- the installation of the system is a community act
- it will avoid fuelling social dissensions in the village
For SHSs, a fixed renting price will be calculated for each building based on the energy that the system was designed to provide.
For grid-connected buildings, single-phase credit meter were found available at a price of 30€.
  1. Case 3: social stigma
The inhabitants of the isolated buildings may find themselves 'stigmatised' by not belonging to the main local grid
- if their access to electricity offers a lesser level of quality (real or not).
- if the inhabitants connected to the grid may blame them for the extra-expense of SHS (real or not).
1. Conclusion
  1. Room for improvement
### Location of PV panels (minigrid / mixed case)
The requirement of locating all the PV panels close to the CONERGY island inverter is a definitive constraint. This implies the system is very centralized.
### MPP Tracking (minigrid / mixed case)
The same island inverter offers a MPP tracking system. However, given the number of PV panels, having several MPPT systems could be of interest.
### Over-sizing of inverters (standalone systems)
Most of the island inverters for the hybrid SHS must be sized for the gensets rated power, as they have the highest power flow the inverter may have to handle.
The average loads at which the island inverters work are very low (~25% of their nominal power) which implies a low efficiency. This is due to the fact that the inverter must be capable of handling:
- the high PV peak power. This was avoided by connecting the PV panels onto the DC bus
- the genset. This can be avoided by sizing the genset reasonably, compared to the load. In our case, it could not be avoided, as 1kW is already a very very small genset.
### Simpler hybrid system
For the small hybrid SHS, an alternative simpler design was to use an island inverter, to which, the PV panels, batteries bank, genset and AC load are all directly connected to the inverter - similarly to the 20K used for the minigrid. Possible inverters are:
- the CONERGY ISA 4K (rated power 4kW and 5,2kWp PV).
- the KACO KI1000 and KI2000 (rated powers 0,8 and 1,6kW)
The problem is that the maximum admitted PV peak power is usually not sufficient.
### Micro-grids (SHS case)
An interesting alternative not explored in this study is to form not a single minigrid or a constellation of micro-grids, but several micro-grids, each one corresponding to a small set of neighbouring houses, as it was done in the mixed case for houses 29 to 33.
The advantages of this approach, is to have save money by increasing the size of each system (compared to the reference SHS case), while keeping the costly power lines to very short distances. This is especially interesting for buildings with small hybrid systems (as stated in the paragraph discussing the problem of the over-sizing of inverters).
The main disadvantage would be the payment issues as neighbouring houses would be interdependent.
  1. The less you buy, the more it costs
The found costs are high. This is due to the low consumption of most buildings. With such small consumptions, equipments for energy production, management and transformation are costlier (kW-wise). Centralized equipments, such as in the case of the minigrid, are cheaper, but laying power lines is expensive.
  1. The virtue of decentralization
The constraint we added to ourselves of not choosing any SMA equipment resulted in that we were not able to use a grid with decentralized systems. Indeed, we have not found any other system capable of intelligent management without a communication bus, which is hardly a solution when distances spread over the kilometre range.