ASTRO PAK CORPORATION

PROCESS PROCEDURE DOCUMENT #:

AP01-300-P041 (JT3)

DOCUMENT TITLE:

FIELD PROCESS FOR PRECISION PAO FLUID

FLUSHING OF PIPING AND EQUIPMENT

OWNER / CLIENT: AIR FORCE FLIGHT TEST CENTER / JT3

LOCATION: EDWARDS AIR FORCE BASE, CA

PROJECT: BUILDING 1030, BAF PAO FLUID EXCHANGE

SYSTEM: GROUND SUPPORT PAO SYSTEM

TRACKING NUMBER: ____________________

| 11-14-06 | 11-14-06 | 11-14-06 | 11-14-06 | 11-14-06 | 09-11-09 |
| --- | --- | --- | --- | --- | --- |
| H. Razvi | T. Tate | T. Sowell | B. Ekstrand | D. Roll | DATE IN SERVICE |
| PREPARED BY | CHECKED BY | REVIEWED BY | QA REVIEW BY | APPROVED BY |  |

| Astro Pak Document No. | AP01 | 300 | P | 041 | JT3 |
| --- | --- | --- | --- | --- | --- |
|  | Application Code | Function Code | Document Type | Sequence No | Rev No |

THIS DOCUMENT CONTAINS PROPREITARY INFORMATION OF ASTRO PAK CORPORATION AND SHALL NOT BE DISCLOSED OUTSIDE OF THE COMPANIES IT IS SUBMITTED TO EXCEPT IN ACCORDANCE WITH THE TERMS OF AN EXISTING AGREEMENT OR CONTRACT. IT SHALL NOT BE DUPLICATED, IN WHOLE OR IN PART OR OTHERWISE USED, FOR ANY PURPOSE OTHER THAN TO EVALUATE THIS DOCUMENT.

REVISILON HISTORY

This page is a record of all revisions to the Process Procedure Document referenced above.

Record field changes or revisions made to this document to meet changed or added requirements of the contract. Approvals shall be obtained from the Astro Pak Project Leader (PL) and Owner / Client representative, both of whom shall sign all changes.

All changes shall be referenced on this page and changed in the document.

| Rev | Date | Revised By | Approved By | Revision Reason |
| --- | --- | --- | --- | --- |
| 0 | 11-14-06 | Hyder Razvi | Daryl Roll | New |
| 1 | 11-20-06 | Hyder Razvi | Daryl Roll | Changed oil flushing temperature and word format. |
| 2 & 3 | 04-06-08 | Daryl Roll | Daryl Roll | Revisions to include Client specifications |
| 4 | 02-20-09 | Daryl Roll | Daryl Roll | Revision to include updates |
| 5 | 06-01-09 | Daryl Roll | Daryl Roll | Revision to include updates |
| JT3 | 09-11-09 | Hyder Razvi | Daryl Roll | To meet project specific requirements |

SIGNATURE LOG

| Company | Name | Signature | Initials | Date |
| --- | --- | --- | --- | --- |

### CONTENTS

### Procedure Review and Approval of Scope of Work

### Non-Disclosure Agreement

### Applicability

### Scope of Procedure

- General

- References

- Process Materials and Equipment Set

- Owner / Representative’s Responsibilities

- Pre-Process Preparation

- Process Set-up

- Variance List

- PAO Flushing Process

- Inspection

- Process Completion

- System Acceptance and Certification

- Documentation

- Attachment List

### PROCEDURE REVIEW AND APPROVAL OF SCOPE OF WORK

  - The undersigned have reviewed and hereby approve the following process procedure:

| Company / Department | Representative Name | Signature / Date |
| --- | --- | --- |
| Flushing / Cleaning Contractor: ASTRO PAK CORPORATION |  |  |
| Owner: |  |  |
| Other Representative: |  |  |

Note: These approvals to be obtained prior to commencing these procedures.

- NON-DISCLOSURE AGREEMENT

  - This document is comprised of information that shall not be disclosed outside of the companies to which it is submitted, and shall not be duplicated, incorporated as a part of another document, or otherwise utilized, in whole or in part, for any purpose other than evaluation by the intended parties.

- APPLICABILITY

  - This procedure is applicable to fluid (PAO) handling systems constructed of stainless steel, carbon steel and or corrosion resistant materials.

- SCOPE OF PROCEDURE

  - This document describes the procedures that Astro Pak shall utilize for precision PAO fluid flushing of piping and equipment in order to ensure that the internal surface is suitable for its designated use. It is also intended to demonstrate Astro Pak’s understanding of the scope of work and to provide sequential guidance to Astro Pak and Owner’s project personnel.

  - The list of Piping & Instrumentation Diagrams - P&ID(s) that defines the physical boundary of the systems and the equipment that will be processed and / or affected by this procedure (or which needs to be isolated) are shown in Attachment “A” Line List and P&ID’s with highlighted Process Flow Path.

- GENERAL

  - This procedure uses a multi-stage process to perform leak testing, fluid replacement and precision PAO fluid flushing to remove debris and undesirable particles and to ensure internal surfaces are suitable for use in high quality PAO fluid coolant systems.

  - Astro Pak proposes to provide the personnel, equipment, materials, technical expertise, process documentation and certification necessary to accomplish the work in accordance with the procedures and conditions given within this document.

  - The following activities will be executed per this procedure:

- Pre-process preparation

- Process set-up

- Leak test and fluid replacement

- PAO fluid flushing process

- Equipment rig-down and documentation

- REFERENCES

  - The content in this procedure is in accordance with accepted standard industrial practices used in a wide range of industries.

- PROCESS MATERIALS AND EQUIPMENT SET

  - Process Materials

    - Attachment “D” Materials and Instrument Certifications, provides details of the materials used for precision PAO fluid flushing.

  - Equipment Set

    - Astro Pak shall provide as needed, pumps, tanks, hoses, tubing, control valves, manifolds, fittings and flanges, safety gear, filters and small tools.

    - The equipment set shall also include calibrated analysis instruments. A listing of instruments to be utilized by Astro Pak is provided in Attachment “D”.

- OWNER / REPRESENTATIVE’S RESPONSIBILITIES

  - The Owner / Representative shall be responsible to supply the following, unless otherwise noted.

    - Utilities such as plant air (150 scfm @ 100 psig), electrical power 480V/3Ø/30A and 110V/1Ø/20A and a qualified electrician to connect Astro Pak equipment to an appropriate electrical supply.

    - Site access and support elements such as special connection flanges that exceed 2.5” in size, valves, jumper spools, scaffolding, etc; as well as Owner / representative’s operations and support personnel required by Astro Pak for conduct of work.

    - A means for approved waste disposal and or storage of PAO fluid in quantities required to facilitate timely accomplishment of the processes and procedures described by this document.

- PRE-PROCESS PREPARATION

  - Astro Pak PL shall meet with the System Owner / representative to discuss, implement the issues listed in section 9.1.1 through 9.1.9.

    - Provide Owner’s representative with a list of Astro Pak personnel on project, obtain badges for access to plant area and arrange for required site orientation.

    - Inform Owner’s representative about Astro Pak’s working hours and shift operations required for conduct of the work.

    - Confirm / prepare a schedule to determine the sequence, priority of all the systems to be flushed by Astro Pak in order to minimize disruption of plant operations and complete maintenance / project activities on time.

    - Hold a safety meeting to discuss work plan, site safety and PPE issues with all participating personnel.

    - Astro Pak PL / Owner’s representative shall inspect equipment, hoses, piping, fittings, and instrumentation provided by Astro Pak for acceptable cleanliness level prior to setting up for flushing.

    - Review the system P&ID(s) (if available) and perform a walk-down of the system with Owner’s representative to identify flow paths, resolve any interferences, restrictions and other issues that will impact the work plan.

    - Highlight P&ID’s (if available) to show flow paths of system being processed in Attachment “A”.

    - Resolve any issues such as flow rate and volume of effluent to be transferred to process/sewer drains or waste storage.

    - Obtain approval for field setup and location of Astro Pak process and effluent handling equipment and temporary piping.

| Description | Sign / Date |
| --- | --- |
| Confirm completion of Sections 9.1.1 through 9.1.9. |  |

  - Astro Pak PL shall continue the pre-process preparation and documentation:

    - List line number and equipment ID number of items included in this system in Attachment “A” Line List (if line and equipment ID is not known give brief description).

    - List control valves such as PCV, FCV, LCV and TCV’s (pressure / flow / level / temperature control valves) and instruments to be removed or relocated in Attachment “B” and ensure these are carried out by Astro Pak or Owner’s representative.

    - Confirm that the subject system has been isolated from other process equipment as per isolation points required, shown on P&ID(s).

    - Check calibration records for all instruments / devices to be utilized in execution of this procedure and verify that they are current. (List Instrument calibration records in Attachment “D”).

    - Obtain approval from Owner’s representative to proceed with field installation activities and set-up flow path for procedure execution as approved during the walk-down of the system and shown on P&ID's (if available).

| Description | Sign / Date |
| --- | --- |
| Confirm completion of Sections 9.2.1 to 9.2.5. |  |

- PROCESS SET-UP

  - Astro Pak PL shall carry-out the following process set-up activities:

    - Situate equipment in a location that is free of congestion and unauthorized traffic.

    - Install inlet and outlet connections, rig up all tees, valves and use points with proper bleeds to ensure proper performance of the PAO flushing process.

    - Ensure that all use points further than 5 pipe diameters from the drop have been set-up to flow as identified on the flow paths / P&ID.

    - Identify hazards in work area; meet with all personnel participating in execution of procedure to discuss safety and PPE issues.

    - Barricade and label work areas, uninsulated pipe, temporary piping and hoses that are under pressure and or contain hot fluids to protect personnel and plant facilities.

    - Establish and maintain control of work site, equipment location to ensure the safety of all personnel transiting or working in the area.

| Description | Sign / Date |
| --- | --- |
| Confirm completion of Sections 10.1.1 to 10.1.6. |  |

  - Astro Pak PL will review the system flow paths to confirm:

    - All valves are in the open or closed position as required to set-up the flow paths and as listed in Attachment “C” Valve Position and Location List.

    - That isolation valves are closed and tagged to confirm the integrity of the flow paths.

    - Install PAO fluid cleaning filters (50 microns or less) on the discharge and return side of the Astro Pak flushing skid with by-pass lines for transferring the existing coolant fluid out of the system.

| Description | FILTER SIZE | Sign / Date |
| --- | --- | --- |
| Confirm completion of Sections 10.2.1 to 10.2.3 and field setup of procedure flow paths is complete. | Microns |  |

  - Following completion of the process set-up activities listed above:

    - Pneumatic test the temporary hoses installed to the system boundary (by closing valves at the system boundaries) with clean, dry air or nitrogen using minimum pressure required to detect leaks up to a maximum pressure limit of 60 psi.

    - Displace and transfer the existing coolant fluid (approximately 250 gallons of Castrol Micronic 889) from the subject system and support equipment including mobile aircraft test carts using filtered nitrogen (5 micron) to original coolant fluid containers or DOT approved waste drums; label all used coolant fluid drums with client name, location, system, name, type of coolant fluid and transfer date.

| Description | Pressure | Sign / Date |
| --- | --- | --- |
| Confirm successful completion of pneumatic leak check. | psi |  |
| Confirm successful completion of Sections 10.3.1 to 10.3.2. |  |

    - Fill the temporary hoses and system with new coolant fluid (AeroShell 602).

    - Astro Pak will start circulating the coolant fluid through the system at ambient temperature and purge air from the system at all high point vents.

    - Astro Pak will constantly monitor the system for any leaks in the system equipment, piping and in Astro Pak installed temporary connections and hoses. Any leaks observed shall be repaired by the appropriate party.

    - Astro Pak shall perform a hydraulic leak test by pressurizing the system to 10% above the expected system working pressure. The test pressure should not drop for a minimum period of 10 minutes.

    - Walk the system to locate any leaks in the system equipment and piping or in Astro Pak installed temporary connections and hoses.

    - Astro Pak shall repair leaks that are located in its hoses, connections and fittings.

    - Inform Owner’s representative to arrange for repairing of leaks that are on system equipment and piping.

| Description | Pressure | Sign / Date |
| --- | --- | --- |
| Confirm successful completion of Sections 10.3.3 to 10.3.9 and hydraulic leak test. | psi |  |

- VARIANCE LIST

  - List any system changes, modifications, or discrepancies observed while executing the requirements of this procedure and notify Owner’s representative of any deviations.

  - The Owner’s representative shall contact any necessary support personnel in order to obtain resolution as needed.

Reported By (Name): Date:

Variance / Change:

Resolution:

Resolution Acceptance (Owner’s Representative Name / Signature / Date):

  - Should additional attachments be required, include these supplementary attachments after the Attachments section.

- PAO FLUID FLUSHING PROCESS

The objective of the PAO fluid flushing process is to filter and flush the new PAO fluid in the system and remove loose debris, undesirable particles in the system piping in order to meet the cleanliness specification.

  - On completion of PAO fluid transfer, filling and hydraulic leak test of the system, commence the PAO fluid flushing stage.

  - Flush the PAO fluid through the system in four (4) stages using different filter media in each stage. Install 50 microns filter media for the first stage of PAO fluid flushing followed by 25 microns for the second stage, 10 microns for the third stage and 5 microns absolute for the fourth stage.

  - Circulate the PAO fluid through each circuit in the system at 100 to 140ºF to flush the system at a flow rate sufficient to create a minimum velocity of 5 feet per second (turbulent flow) for a period of two (2) hours or until an inspection of the filter sock shows no significant debris.

  - Monitor differential pressure across inlet and return filter units; change filter media as necessary to maintain low differential pressures. Change filter sizes at the end of each flushing stage as required.

| PAO FLUID FLUSHING 1st FILL - STAGE 1 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

| PAO FLUID FLUSHING 1st FILL - STAGE 2 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

| PAO FLUID FLUSHING 1st FILL - STAGE 3 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

| PAO FLUID FLUSHING 1st FILL - STAGE 4 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

  - Collect two samples (500 mL) of coolant fluid on completion of first (1st) fill stage 4 for particle count tests.

  - Test first (1st) fill coolant fluid samples to determine particle count and document these results as the baseline in Attachment ‘H’ Particle Count Analysis Log.

  - Displace the first (1st) fill coolant fluid (AeroShell 602) from the subject system using filtered nitrogen (5 micron) and transfer to original PAO containers; label all used PAO drums with client name, location, system, name, type of PAO and transfer date.

  - Fill the temporary hoses and system with new coolant fluid (AeroShell 602).

  - Astro Pak will start circulating the coolant fluid through the system at ambient temperature and purge air from the system at all high point vents.

  - Circulate the PAO fluid through each circuit in the system at 100 to 140ºF in accordance with the listed specification or a flow rate sufficient to create a minimum velocity of 5 feet per second (turbulent flow) for a period of two (2) hours or until an inspection of the filter sock shows no significant debris.

  - Monitor differential pressure across inlet and return filter units; change filter media as necessary to maintain low differential pressures. Change filter sizes at the end of each flushing stage as required.

| PAO FLUSHING Final FILL - STAGE 1 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

| PAO FLUSHING Final FILL - STAGE 2 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

| PAO FLUSHING Final FILL - STAGE 3 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

| PAO FLUSHING Final FILL - STAGE 4 | Filter Size | Sign / Date |
| --- | --- | --- |
| Start Time: | End Time: | microns |  |

  - Collect two samples (500 mL) of coolant fluid on completion of final fill stage 4, one each for client and for particle count test.

  - Test the final fill coolant fluid samples to determine particle count and document these results as the final fill results in Attachment ‘H’ Particle Count Analysis Log.

  - Continue circulating and flushing of the coolant fluid through system at 100 to 140ºF at a flow rate sufficient to create a minimum velocity of 5 feet per second (turbulent flow) for an additional period of two (2) hours

  - Collect two samples (500 mL) of coolant fluid on completion of section 12.14, one each for client and for particle count test.

  - Test the final fill coolant fluid samples to determine particle count and document these results as the final fill results in Attachment ‘H’ Particle Count Analysis Log.

  - Repeat Sections 12.14 through 12.16 until particle count specifications are met.

| Description | Sign / Date |
| --- | --- |
| Confirm completion of Section 12.1 to 12.17 of PAO fluid flushing process. |  |

- INSPECTION

  - Review particle count test results with Owner’s representative and confirm acceptance.

| Description | Sign / Date |
| --- | --- |
| Particle count results accepted by Owner’s representative. |  |

- PROCESS COMPLETION

  - Review this procedure to ensure completeness.

  - Remove Astro Pak’s temporary valve or piping tags, Astro Pak’s furnished equipment from subject system, and insure all product and waste containers have been removed to designated storage and or disposal area.

  - Reinstall fittings and instruments to return subject system to operational configuration as identified in Attachment “B”, Equipment and Instrument Isolation / Removal / Restoration.

  - Return Customer’s system to pre-service status and Customer’s environment/ site to pre-Astro Pak state or better.

  - Walk site with Customer showing all work complete and condition of process area.

| Description | Sign / Date |
| --- | --- |
| Confirm completion of work listed in Section 14.1 to 14.5. |  |

- SYSTEM ACCEPTANCE AND CERTIFICATION

  - The undersigned have reviewed and accept the completion of the process procedures for the subject system as documented above. This confirms the Certification of PAO Fluid Flushing for the above listed system.

| Company / Department | Representative Name | Signature / Date |
| --- | --- | --- |
| Oil Flushing / Cleaning Contractor: ASTRO PAK CORPORATION |  |  |
| Owner: |  |  |
| Other Representative: |  |  |

Note: To be signed on completion of all procedures listed in this document.

- DOCUMENTATION

  - Astro Pak representative shall review documentation and field records with Owner’s representative.

  - Astro Pak representative shall submit copy of completed and signed PPD (Process Procedure Document) to Owner’s representative on completion of work and document review by Astro Pak’s Quality Assurance Department.

- ATTACHMENT LIST

#### Line List and P&ID’s with Highlighted Process Flow Path

#### Equipment and Instrument Isolation / Removal / Restoration

#### Valve Position and Location List

#### Materials and Instrumentation Certifications

#### System Batch Volume and Waste Disposal Plan

#### Pipe Sizes and Flow Values

#### Flow Calculations

#### Particle Count Analysis Log

| ATTACHMENT A |
| --- |
| LINE LIST AND P&ID’s WITH HIGHLIGHLTED PROCESS FLOW PATH |
| TOTAL NUMBER OF LINES: | Page ___ of ___ |
| LINE / EQUIPMENT ID | DESCRIPTION | DRAWING NUMBER |
| 2” Supply / Return lines | Aircraft Support Equipment (ASE) Room 012 to Anechoic Chamber |  |
|  | Room 032 |  |
| 1.5” Flex hoses | To / from Aircraft Service Carts |  |

| NOTES: |
| --- |
| ASTRO PAK REPRESENTATIVE SIGNATURE: | DATE: |

| ATTACHMENT B |
| --- |
| EQUIPMENT & INSTRUMENT ISOLATION / REMOVAL / RESTORATION |
| Page ___ of ___ |
| COMPONENt Tag NUMBER | Description | IsolatED / RemoveD or RELOCATED | Removed By Company / Sign / Date | Equipment / Instrument re-installed (Circle One) | Company / Sign / Date |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |
|  |  |  |  | Y / N |  |

| NOTES: |
| --- |
| ASTRO PAK REPRESENTATIVE SIGNATURE: | DATE: |

| ATTACHMENT C |
| --- |
| VALVE POSITION & LOCATION LIST |
| Page ___ of ___ |
| VALVE ID NUMBER OR LOCATION | INITIAL VALVE POSITION | VALVE POSITION / ACTUATIONS DURING PAO FLUSHING | COMMENTS |

| NOTES: Show location of valves on P&ID’s with flow paths. O = Open C = Closed CCO = Closed Cycle Open |
| --- |
| ASTRO PAK REPRESENTATIVE SIGNATURE: | DATE: |

| ATTACHMENT D |
| --- |
| MATERIALS AND INSTRUMENT CERTIFICATIONS |
| PROCESS MATERIALS | MANUFACTURER | LOT NUMBER | CERTIFICATE DATE |
| Coolant Fluid, AeroShell 602 | Shell Oil Company |  |  |
| INSTRUMENT DESCRIPTION | MODEL NUMBER | SERIAL NUMBER | CALIBRATION DATE |

| NOTES: |
| --- |
| ASTRO PAK REPRESENTATIVE SIGNATURE: | DATE: |

| ATTACHMENT E |
| --- |
| SYSTEM BATCH VOLUME AND WASTE DISPOSAL PLAN |
| SYSTEM BATCH VOLUME |
| DESCRIPTION | GALLONS / LITERS * | FLUID SOURCE | COMMENTS AND CALCULATIONS |
| Owner provided fluid volume used |  |  |  |
| Astro Pak provided fluid volume used |  |  |  |
| Total System Batch Volume |  |  |  |
| WASTE DISPOSAL PLAN |
| DESCRIPTION | GALLONS / LITERS * | DISPOSAL / STORAGE? | COMMENTS |
| PAO Fluid 1st stage flushing waste volume |  |  |  |
| PAO Fluid 2nd stage flushing waste volume |  |  |  |
| Total Waste Volume Generated |  |  |  |

| NOTES: * Circle units used. |
| --- |
| ASTRO PAK REPRESENTATIVE SIGNATURE: | DATE: |

INSTRUCTIONS FOR USING THE FLOW CALCULATION WORKSHEET (ATTACHMENT F)

- Place cursor inside the rectangular chart block and double click the cursor.

- Attachment I will change from a Word document page to an Excel worksheet page.

- Fill in the actual Tubing OD and Wall Thickness in the blank cells in columns 1 and 2.

- This will immediately calculate and show the Tubing ID in millimeters and meters in columns 3 and 4.

- Fill in the Flow Rate in gallons per minute in the blank cell in column 5.

- This will immediately calculate and show the flow rate in Liters per minute and Flow Velocity in m/sec and ft/sec in columns 6, 7 and 8.

- Fill in Kinematic Viscosity (in CentiStokes) of the Flushing Oil in column 9.

- This will immediately calculate and show the Reynolds Number and Friction Factor in columns 10 and 11.

- Fill in the Length of the Tubing/Pipe (in Feet) in column 12.

- This will immediately calculate and show the Length of the Tubing/Pipe (in meters) in column 13.

- Fill in the Specific Gravity of the Flushing Oil in column 14.

- This will immediately calculate and show the Density of the Flushing Oil and the Pressure Drop per 100 ft in columns 15 and 16.

- Note the results obtained in Attachment H, Flow Values.

- Change the tubing size and length combination to get the flow values for each tubing section to be flushed; note results as in step 13.

- When all the lines have been covered; double click outside the excel worksheet block or go to the next page.

- This will switch the Excel worksheet back to a word document page.

- Check Attachments H and I for errors and correct as necessary.

- Discard these instructions from the Attachment package before submitting to Customer.

| ATTACHMENT F |
| --- |
| PIPE SIZES AND FLOW VALUES |
| Page ___ of ___ |
| TUBING / LINE | OD | WT | D | FLOWRATE | VELOCITY | REYLNOLDS | FRICTION | ΔP100 |
| # | Inches | Inches | Inches | Q – Gals / min | V - ft / sec | NUMBER - Re | FACTOR - f | Psig / 100 ft |

D = OD – (2 x WT);                 V = Q x 21.22            Re = 1000 x V x D               f = 0.3164 x Re - 0.25           ΔP100 = v2 x f x L x p

D2 x 3.281                                   v                                                                                        2D

Where

D = Inside Diameter of tube in millimeters (mm);    OD = Outside Diameter of tube in millimeters (mm);    WT = Wall Thickness of tube in millimeters (mm)

Q = Flow rate in Liter per minute (Lit/min);  V = Velocity in meters per second (m/sec);    v  = Kinematic Viscosity of oil at 40 ºC in centistokes (cS) or mm2/sec

Re* = Reynolds Number;   f *  = Friction Factor;       L  = Length of pipe in meters (m);    p  = Density of oil in Kilogram per cubic meter (Kg/m3)

1 inch = 25.4 millimeters; 1 meter per second (m/sec) = 3.281 feet per second; 1 liter per minute (Lit/min) = 0.2642 gallons per minute;

1 gallon per minute (gals/min) = 3.785 liters per minute; 1 millimeter (mm) = 0.0394 inches

*Re and f   are non-dimensional numbers (no units)

| ASTRO PAK REPRESENTATIVE SIGNATURE: | DATE: |
| --- | --- |
| ATTACHMENT G FLOW CALCULATIONS |

ATTACHMENT H

PARTICLE COUNT ANALYSIS LOG

Page ___ of ___

| Cleaning Specification: MIL-PRF-87252C | Flushing Oil Used: AeroShell 602 | Manufacturer: Shell Oil Company |
| --- | --- | --- |
| Particle Count Instrument Type: | Instrument Model #: | Manufacturer: |

| SAMPLE DATE | TIME | SAMPLE ID # | PARTICLE SIZE | PARTICLE COUNT RESULTS | PARTICLE COUNT LIMIT | SIGN / DATE |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 5 to 15 um |  | 2664 |  |
|  |  |  | 16 to 25 um |  | 345 |  |
|  |  |  | 26 to 50 um |  | 86 |  |
|  |  |  | 51 to 100 um |  | 10 |  |
|  |  |  | >100 |  | 0 |  |

| SAMPLE DATE | TIME | SAMPLE ID # | PARTICLE SIZE | PARTICLE COUNT RESULTS | PARTICLE COUNT LIMIT | SIGN / DATE |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 5 to 15 um |  | 2664 |  |
|  |  |  | 16 to 25 um |  | 345 |  |
|  |  |  | 26 to 50 um |  | 86 |  |
|  |  |  | 51 to 100 um |  | 10 |  |
|  |  |  | >100 |  | 0 |  |

| NOTES: |
| --- |
| ASTRO PAK REPRESENTATIVE SIGNATURE / DATE: | OWNER REPRESENTATIVE SIGNATURE /DATE: |