graphical setup - note repaired scale factor for motor speed

breaker says input currents are 4.1, 3.1, 4.1A

11:35 - dump valve opened
12:26 - dump valve closed

start 10.png ; good start, leaks

start 11, good start

run 11 - going for 2 hour run at this rate. started at 13:15
13:18 main breaker 15.5, 13.1, 15.9A 15.2A on drive
13:30 transformer frame 45, 43, 42, cells A3, B3, C3 heatsink 56 56 56
13:48 transformer 38, 36, 33, cells 38, 36, 38
14:10 transformer 26, 37, 34, cells 37, 27,27
14:35 transformer 29, 29, 29, cells 36, 37, 36
15:00 transfoirmer 31, 27, 34 cells 36, 37, 36

ramp 11.png, speed increased 

ramp 11 down.png, back to operating speed

15:18 transformer 37, 44, 44, cells 56,56,51

stop 11.png