## Cryo Power
High Field VLHC Cryogenic Power Estimates
Arc magnets
Tom Peterson
2001-01-10
updated 20 Apr 01 | [5 empty] | For comparison:
Overall shield
|  | Shield supply |  |  | Shield return pipe | system total |  |  |  | Corrector leads only |  | Main leads
|  | pipe | Thermal shield | Beam screen | and thermal shield | (Magnet and | Magnet cold mass | Arc power leads |  | 80 K conduction | 4.5 K conduction | 80 K gas | 4.5 K vapor
|  | (in transfer line) | (magnet) | (two beams) | (transfer line) | transfer line) |  |  |  | cooling | cooling | cooling | cooling
Temp in | (K) | 77 | 77.5476 | 85.5276 | 77.5476 | 77 | 4.5 | Temp in | (K) | 77.5476 | 4.5 | 80 | 4.5
Press in | (bar) | 20 | 19.1063 | 19.0273 | 17.2509 | 20 | 4 | Press in | (bar) | 19.1063 | 4 | 2 | 4
Enthalpy in | (J/g) | 416.809 | 419.6657 | 461.2974 | 419.6657 | 416.809 | 12.09 | Enthalpy in | (J/g) | 419.6657 | 12.1 | 432.46 | 12.1
Entropy in | (J/gK) | 18.3584 | 18.4807 | 19.004 | 18.6732 | 18.3584 | 3.522 | Entropy in | (J/gK) | 18.4807 | 3.5 | 23.29 | 3.5
Temp out | (K) | 77.5476 | 85.5276 | 104.5276 | 106.6278 | 106.6278 | 5.5 | Temp out | (K) | 85.5276 | 5.5 | 300 | 300
Press out | (bar) | 19.1063 | 19.0273 | 17.2509 | 16.5985 | 16.5985 | 1.8 | Press out | (bar) | 19.0273 | 1.8 | 1.6 | 1.6
Enthalpy out | (J/g) | 419.6657 | 461.2974 | 560.4204 | 571.3775 | 571.3775 | 35.9 | Enthalpy out | (J/g) | 461.2974 | 35.9 | 1580.2 | 1580.2
Entropy out | (J/gK) | 18.4807 | 19.004 | 20.2427 | 20.4199 | 20.4199 | 8.706 | Entropy out | (J/gK) | 19.004 | 8.7 | 30.6403 | 30.6403
[8 empty] | Number of leads per sector |  |  |  | 6
[8 empty] | Current | (kA) |  |  | 25
Predicted heat load | (W/m) | 0.1 | 4.2 | 10 | 2.2 | 16.5195 | 0.83 | Flow per lead | (g/s) |  |  | 0.9875 | 0.15
Heat uncertainty factor |  | 1.25 | 1.25 | 1.25 | 1.25 |  | 1.25 | Corrector leads per sector |  | 1000 |  | 0
Design heat load | (W/m) | 0.125 | 5.25 | 12.5 | 2.75 | 20.9031 | 1.0375 | Average current | (kA) | 0.1 |  | 0.1
Distance | (m) | 9700 | 9700 | 7824 | 9700 | 9700 | 9700 | Flow per lead (for gas cooled) | (g/s) |  |  | 0.00395 | 0.0006
Design total heat | (kW) | 1.2125 | 50.925 | 97.8 | 26.675 | 202.7603 | 10.0637 | Heat per lead (for cond cooled) | (W) | 4.45 | 0.04
Avg design mass flow | (g/s) | 424.4405 | 1223.2277 | 986.6529 | 175.8268 | 1311.7831 | 422.669 | Total heat per sector | (W) | 4450 | 40
Design mass flow | (g/s) | 1349.8948 | 17.0243 | 8.5122 | 1349.8948 |  | 422.669
Segment distance | (m) |  | 135 | 135 |  |  |  | Total current | (kA) | 100 |  | 150
Segment heat | (W) |  | 708.75 | 1687.5 |  |  |  | Total flow | (g/s) |  |  | 5.925 | 0.9
Segment mass flow | (g/s) |  | 17.0243 | 17.0243 |  |  |  | Flow or heat uncertainty factor |  | 1.25 | 1.25 | 1.25 | 1.25
Segments per sector |  |  | 71.8519 | 57.9556 |  |  |  | Design heat | (W) | 5562.5 | 50
[8 empty] | Design flow | (g/s) | 133.6123 | 2.1008 | 7.4063 | 1.125
Design ideal power | (kW) | 14.3713 | 141.1095 | 268.8255 | 65.4594 | 608.5146 | 647.2712 | Design ideal power | (kW) | 15.4133 | 3.2273 | 7.831 | 7.3957
4.5 K equiv design power | (kW) | 0.21887 | 2.1491 | 4.0942 | 0.99695 | 9.2677 | 9.8579 | 4.5 K equiv design pwr | (kW) | 0.23474 | 0.049152 | 0.11927 | 0.11264
Efficiency (fraction Carnot) |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Efficiency (fraction Carnot) |  | 0.3 | 0.3 | 0.25 | 0.25
Efficiency in Watts/Watt | (W/W) | 39.5086 | 9.2364 | 9.1624 | 8.1799 | 10.0038 | 214.3903
Nominal operating power | (kW) | 47.9042 | 470.365 | 896.0851 | 218.1981 | 2028.3819 | 2157.5705 | Nominal operating power | (kW) | 51.3776 | 10.7577 | 31.3242 | 29.583
Overcapacity factor |  | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | Overcapacity factor |  | 1.3 | 1.3 | 1.3 | 1.3
Installed operating power | (kW) | 62.2754 | 611.4745 | 1164.9106 | 283.6575 | 2636.8965 | 2804.8417 | Installed operating power | (kW) | 66.7909 | 13.985 | 40.7214 | 38.4578
Installed 4.5 K equiv | (kW) | 0.28454 | 2.7938 | 5.3225 | 1.296 | 12.048 | 12.8153 | Installed 4.5 K equiv | (kW) | 0.30517 | 0.063897 | 0.18606 | 0.17571
Percent of power |  | 1.224% | 12.02% | 22.9% | 5.576% | 51.83% | 55.14%
10.002
Total installed operating power for one 10 km string (MW) | [6 empty] | 5.0871
Total installed 4.5 K equivalent power for one 10 km string (kW) | [6 empty] | 22.8739
Number of standard large cryoplants per 10 km string | [6 empty] | 0.91496
Number of standard large cryoplants per location (cooling two 10 km strings) | [6 empty] | 1.8299
Number of above "strings" in accelerator | [6 empty] | 24
Operating wall plug power for cryogenics for entire accelerator (MW) | [6 empty] | 92.4247
Installed wall plug power for cryogenics for entire accelerator (MW) | [6 empty] | 122.0908
Installed 4.5 K equivalent power for entire accelerator (kW) | [6 empty] | 548.9741
Installed number of standard large cryoplants | [6 empty] | 21.959
Installed number of LHC system equivalents | [6 empty] | 3.8123

## Supply helium
|  | Helium temperature for the supply end of the pipe in K. |  |  |  |  | 77 | K
|  | Helium pressure for the supply end of the pipe in bar. |  |  |  |  | 20 | bar
|  | This pressure and temperature will be used to find an initial helium density. | [8 empty] | Calculation of pressure drop for helium gas | [10 empty] | T. Peterson
[11 empty] | through a pipe with pressure drop and heat added | [10 empty] | 2000-01-02
|  |  |  | Enter a maximum delta-T |  |  | 2 | K | [17 empty] | Helium |  |  |  | Helium
Note: Bin size and number of bins |  |  |  | Linear heat flux (W/m) |  | Heat = | 0.1 | W/m pipe heat load |  |  |  |  | Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar | [12 empty] | temperatures | Supply | Supply |  | temperatures
are manually entered to match total length |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 21.35 | cm | [13 empty] | f incl factor |  |  |  | copied for | pipe inlet | pipe exit | Delta-T | inverted for
|  |  |  | Total pipe length (m) |  | Length = | 9700 | m |  |  |  |  | Helium |  |  | Helium | Helium |  | Number | Overall avg |  | 4 for D |  |  |  | supply pipe | temperature | temperature | from far end | return pipe
|  | Bin | [7 empty] | Total heat |  | Specific heat | temperature | mt | mShield | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
|  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | (J/gK) | (K) | (g/s) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar) | (K) | (K) | (K) | (K) | (K)
|  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin)
Supply end |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  | 5.19 | 77 | 1082.4755 | 6.1932 | 0.012468 | 8.0942e-06 | 21.35 | 1 | 242.5226 | 797545.0625 | 0.010588 | 0 | 0 | 20 | 77 | 77 | 76.6045 | -0.39555 | 76.6045
|  | 270 | 270 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0049 | 1057.7025 | 6.1932 | 0.012467 | 8.0945e-06 | 21.35 | 1 | 236.9875 | 779264.7441 | 0.010649 | 27000 | 471.4709 | 19.9953 | 77.0049 | 77 | 76.6045 | -0.40046 | 76.5995
|  | 270 | 540 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.01 | 1032.9296 | 6.1932 | 0.012463 | 8.0948e-06 | 21.35 | 1 | 231.5067 | 760985.0873 | 0.010713 | 27000 | 452.457 | 19.9908 | 77.01 | 77 | 76.6045 | -0.4055 | 76.5945
|  | 270 | 810 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0151 | 1008.1567 | 6.1932 | 0.012459 | 8.0951e-06 | 21.35 | 1 | 226.0207 | 742706.1079 | 0.010778 | 27000 | 433.7696 | 19.9864 | 77.0151 | 77 | 76.6045 | -0.41066 | 76.5893
|  | 270 | 1080 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0204 | 983.3838 | 6.1932 | 0.012456 | 8.0954e-06 | 21.35 | 1 | 220.5298 | 724427.8224 | 0.010845 | 27000 | 415.4116 | 19.9823 | 77.0204 | 77 | 76.6045 | -0.41595 | 76.584
|  | 270 | 1350 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0258 | 958.6109 | 6.1932 | 0.012452 | 8.0958e-06 | 21.35 | 1 | 215.0342 | 706150.2483 | 0.010915 | 27000 | 397.386 | 19.9783 | 77.0258 | 77 | 76.6045 | -0.42138 | 76.5786
|  | 270 | 1620 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0314 | 933.838 | 6.1932 | 0.012449 | 8.0961e-06 | 21.35 | 1 | 209.534 | 687873.4039 | 0.010986 | 27000 | 379.6959 | 19.9745 | 77.0314 | 77 | 76.6045 | -0.42695 | 76.5731
|  | 270 | 1890 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0371 | 909.0651 | 6.1932 | 0.012446 | 8.0964e-06 | 21.35 | 1 | 204.0294 | 669597.3085 | 0.011061 | 27000 | 362.3442 | 19.9709 | 77.0371 | 77 | 76.6045 | -0.43267 | 76.5673
|  | 270 | 2160 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.043 | 884.2921 | 6.1932 | 0.012442 | 8.0968e-06 | 21.35 | 1 | 198.5205 | 651321.9825 | 0.011137 | 27000 | 345.334 | 19.9674 | 77.043 | 77 | 76.6045 | -0.43855 | 76.5614
|  | 270 | 2430 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0491 | 859.5192 | 6.1932 | 0.012439 | 8.0971e-06 | 21.35 | 1 | 193.0076 | 633047.4474 | 0.011217 | 27000 | 328.6685 | 19.9641 | 77.0491 | 77 | 76.6045 | -0.44461 | 76.5554
|  | 270 | 2700 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0553 | 834.7463 | 6.1932 | 0.012436 | 8.0975e-06 | 21.35 | 1 | 187.4908 | 614773.7258 | 0.011299 | 27000 | 312.3509 | 19.961 | 77.0553 | 77 | 76.6045 | -0.45084 | 76.5492
|  | 270 | 2970 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0617 | 809.9734 | 6.1932 | 0.012433 | 8.0979e-06 | 21.35 | 1 | 181.9702 | 596500.8419 | 0.011385 | 27000 | 296.3845 | 19.958 | 77.0617 | 77 | 76.6045 | -0.45726 | 76.5427
|  | 270 | 3240 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0683 | 785.2005 | 6.1932 | 0.01243 | 8.0983e-06 | 21.35 | 1 | 176.4461 | 578228.8211 | 0.011474 | 27000 | 280.7726 | 19.9552 | 77.0683 | 77 | 76.6045 | -0.46389 | 76.5361
|  | 270 | 3510 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0752 | 760.4276 | 6.1932 | 0.012427 | 8.0987e-06 | 21.35 | 1 | 170.9185 | 559957.6907 | 0.011566 | 27000 | 265.5187 | 19.9526 | 77.0752 | 77 | 76.6045 | -0.47073 | 76.5293
|  | 270 | 3780 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0823 | 735.6546 | 6.1932 | 0.012425 | 8.0991e-06 | 21.35 | 1 | 165.3875 | 541687.4795 | 0.011663 | 27000 | 250.6263 | 19.9501 | 77.0823 | 77 | 76.6045 | -0.4778 | 76.5222
|  | 270 | 4050 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0896 | 710.8817 | 6.1932 | 0.012422 | 8.0996e-06 | 21.35 | 1 | 159.8534 | 523418.2185 | 0.011763 | 27000 | 236.099 | 19.9477 | 77.0896 | 77 | 76.6045 | -0.48512 | 76.5149
|  | 270 | 4320 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0972 | 686.1088 | 6.1932 | 0.012419 | 8.1e-06 | 21.35 | 1 | 154.3162 | 505149.9405 | 0.011868 | 27000 | 221.9406 | 19.9455 | 77.0972 | 77 | 76.6045 | -0.4927 | 76.5073
|  | 270 | 4590 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.105 | 661.3359 | 6.1932 | 0.012417 | 8.1005e-06 | 21.35 | 1 | 148.7762 | 486882.6811 | 0.011978 | 27000 | 208.1548 | 19.9434 | 77.105 | 77 | 76.6045 | -0.50057 | 76.4994
|  | 270 | 4860 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1132 | 636.563 | 6.1932 | 0.012414 | 8.101e-06 | 21.35 | 1 | 143.2333 | 468616.4782 | 0.012093 | 27000 | 194.7458 | 19.9415 | 77.1132 | 77 | 76.6045 | -0.50874 | 76.4913
|  | 270 | 5130 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1217 | 611.7901 | 6.1932 | 0.012411 | 8.1015e-06 | 21.35 | 1 | 137.6878 | 450351.3729 | 0.012214 | 27000 | 181.7176 | 19.9397 | 77.1217 | 77 | 76.6045 | -0.51724 | 76.4828
|  | 270 | 5400 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1306 | 587.0172 | 6.1932 | 0.012409 | 8.102e-06 | 21.35 | 1 | 132.1397 | 432087.4093 | 0.012341 | 27000 | 169.0745 | 19.938 | 77.1306 | 77 | 76.6045 | -0.52611 | 76.4739
|  | 270 | 5670 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1398 | 562.2442 | 6.1932 | 0.012406 | 8.1025e-06 | 21.35 | 1 | 126.5891 | 413824.6357 | 0.012475 | 27000 | 156.8211 | 19.9364 | 77.1398 | 77 | 76.6045 | -0.53536 | 76.4646
|  | 270 | 5940 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1495 | 537.4713 | 6.1932 | 0.012404 | 8.1031e-06 | 21.35 | 1 | 121.0362 | 395563.1041 | 0.012616 | 27000 | 144.9619 | 19.9349 | 77.1495 | 77 | 76.6045 | -0.54504 | 76.455
|  | 270 | 6210 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1596 | 512.6984 | 6.1932 | 0.012401 | 8.1037e-06 | 21.35 | 1 | 115.481 | 377302.8718 | 0.012766 | 27000 | 133.5018 | 19.9336 | 77.1596 | 77 | 76.6045 | -0.55518 | 76.4448
|  | 270 | 6480 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1703 | 487.9255 | 6.1932 | 0.012399 | 8.1044e-06 | 21.35 | 1 | 109.9237 | 359044.0013 | 0.012926 | 27000 | 122.4461 | 19.9324 | 77.1703 | 77 | 76.6045 | -0.56585 | 76.4342
|  | 270 | 6750 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1815 | 463.1526 | 6.1932 | 0.012396 | 8.105e-06 | 21.35 | 1 | 104.3642 | 340786.5615 | 0.013095 | 27000 | 111.8001 | 19.9313 | 77.1815 | 77 | 76.6045 | -0.57708 | 76.4229
|  | 270 | 7020 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1934 | 438.3797 | 6.1932 | 0.012394 | 8.1057e-06 | 21.35 | 1 | 98.8028 | 322530.6287 | 0.013277 | 27000 | 101.5696 | 19.9302 | 77.1934 | 77 | 76.6045 | -0.58895 | 76.4111
|  | 270 | 7290 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.206 | 413.6068 | 6.1932 | 0.012391 | 8.1065e-06 | 21.35 | 1 | 93.2394 | 304276.2879 | 0.013472 | 27000 | 91.7608 | 19.9293 | 77.206 | 77 | 76.6045 | -0.60152 | 76.3985
|  | 270 | 7560 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.2194 | 388.8338 | 6.1932 | 0.012388 | 8.1073e-06 | 21.35 | 1 | 87.674 | 286023.634 | 0.013682 | 27000 | 82.38 | 19.9285 | 77.2194 | 77 | 76.6045 | -0.6149 | 76.3851
|  | 270 | 7830 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.2336 | 364.0609 | 6.1932 | 0.012385 | 8.1081e-06 | 21.35 | 1 | 82.1068 | 267772.7742 | 0.013909 | 27000 | 73.4343 | 19.9278 | 77.2336 | 77 | 76.6045 | -0.62919 | 76.3708
|  | 270 | 8100 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.249 | 339.288 | 6.1932 | 0.012382 | 8.109e-06 | 21.35 | 1 | 76.5378 | 249523.8302 | 0.014157 | 27000 | 64.9312 | 19.9271 | 77.249 | 77 | 76.6045 | -0.64453 | 76.3555
|  | 270 | 8370 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.2655 | 314.5151 | 6.1932 | 0.012379 | 8.11e-06 | 21.35 | 1 | 70.9669 | 231276.9415 | 0.014428 | 27000 | 56.879 | 19.9266 | 77.2655 | 77 | 76.6045 | -0.66107 | 76.3389
|  | 270 | 8640 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.2835 | 289.7422 | 6.1932 | 0.012376 | 8.1111e-06 | 21.35 | 1 | 65.3943 | 213032.2695 | 0.014727 | 27000 | 49.2864 | 19.9261 | 77.2835 | 77 | 76.6045 | -0.67902 | 76.321
|  | 270 | 8910 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.3031 | 264.9693 | 6.1932 | 0.012373 | 8.1123e-06 | 21.35 | 1 | 59.8197 | 194790.0031 | 0.015061 | 27000 | 42.1634 | 19.9256 | 77.3031 | 77 | 76.6045 | -0.69866 | 76.3013
|  | 270 | 9180 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.3248 | 240.1963 | 6.1932 | 0.012369 | 8.1135e-06 | 21.35 | 1 | 54.2433 | 176550.3665 | 0.015435 | 27000 | 35.5208 | 19.9253 | 77.3248 | 77 | 76.6045 | -0.72031 | 76.2797
|  | 270 | 9450 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.3489 | 215.4234 | 6.1932 | 0.012365 | 8.115e-06 | 21.35 | 1 | 48.6649 | 158313.6302 | 0.015862 | 27000 | 29.3709 | 19.925 | 77.3489 | 77 | 76.6045 | -0.74446 | 76.2555
|  | 270 | 9720 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.3762 | 190.6505 | 6.1932 | 0.01236 | 8.1166e-06 | 21.35 | 1 | 43.0845 | 140080.1266 | 0.016355 | 27000 | 23.7275 | 19.9248 | 77.3762 | 77 | 76.6045 | -0.77175 | 76.2282
|  | 270 | 9990 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.4076 | 165.8776 | 6.1932 | 0.012355 | 8.1185e-06 | 21.35 | 1 | 37.5018 | 121850.2745 | 0.016935 | 27000 | 18.6067 | 19.9246 | 77.4076 | 77 | 76.6045 | -0.80311 | 76.1969
|  | 270 | 10260 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.4444 | 141.1047 | 6.1932 | 0.012349 | 8.1207e-06 | 21.35 | 1 | 31.9166 | 103624.6176 | 0.017635 | 27000 | 14.0275 | 19.9244 | 77.4444 | 77 | 76.6045 | -0.83998 | 76.16
|  | 270 | 10530 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.4892 | 116.3318 | 6.1932 | 0.012342 | 8.1233e-06 | 21.35 | 1 | 26.3285 | 85403.8903 | 0.018508 | 27000 | 10.0125 | 19.9243 | 77.4892 | 77 | 76.6045 | -0.8847 | 76.1153
|  | 270 | 10800 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.546 | 91.5589 | 6.1932 | 0.012333 | 8.1267e-06 | 21.35 | 1 | 20.7372 | 67189.1393 | 0.019652 | 27000 | 6.5904 | 19.9243 | 77.546 | 77 | 76.6045 | -0.94152 | 76.0585
|  | 270 | 11070 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.6239 | 66.7859 | 6.1932 | 0.01232 | 8.1313e-06 | 21.35 | 1 | 15.1416 | 48981.9771 | 0.021268 | 27000 | 3.7987 | 19.9242 | 77.6239 | 77 | 76.6045 | -1.0194 | 75.9806
|  | 270 | 11340 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.7477 | 42.013 | 6.1932 | 0.012301 | 8.1387e-06 | 21.35 | 1 | 9.5403 | 30785.2117 | 0.023886 | 27000 | 1.691 | 19.9242 | 77.7477 | 77 | 76.6045 | -1.1432 | 75.8568
|  | 270 | 11610 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 78.0495 | 17.2401 | 6.1932 | 0.012253 | 8.1566e-06 | 21.35 | 1 | 3.9301 | 12604.9704 | 0.029861 | 27000 | 0.35735 | 19.9242 | 78.0495 | 77 | 76.6045 | -1.445 | 75.555
|  | 270 | 11880 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.3588 | -7.5328 | 6.1932 | 0.012363 | 8.1156e-06 | 21.35 | 1 | -1.702 | -5535.4167 | #NUM! | 27000 | #NUM! | #NUM! | 77.3588 | 77 | 76.6045 | -0.75438 | 76.2456
|  | 270 | 12150 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1978 | -32.3057 | 6.1932 | #NUM! | 8.106e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 77.1978 | 77 | 76.6045 | -0.59334 | 76.4067
|  | 270 | 12420 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.1067 | -57.0786 | 6.1932 | #NUM! | 8.1006e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 77.1067 | 77 | 76.6045 | -0.5022 | 76.4978
|  | 270 | 12690 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 77.0431 | -81.8515 | 6.1932 | #NUM! | 8.0968e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 77.0431 | 77 | 76.6045 | -0.43864 | 76.5614
|  | 270 | 12960 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.9943 | -106.6245 | 6.1932 | #NUM! | 8.0939e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.9943 | 77 | 76.6045 | -0.38985 | 76.6101
|  | 270 | 13230 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.9547 | -131.3974 | 6.1932 | #NUM! | 8.0915e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.9547 | 77 | 76.6045 | -0.35026 | 76.6497
|  | 270 | 13500 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.9214 | -156.1703 | 6.1932 | #NUM! | 8.0896e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.9214 | 77 | 76.6045 | -0.31695 | 76.6831
|  | 270 | 13770 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.8927 | -180.9432 | 6.1932 | #NUM! | 8.0878e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.8927 | 77 | 76.6045 | -0.2882 | 76.7118
|  | 270 | 14040 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.8674 | -205.7161 | 6.1932 | #NUM! | 8.0863e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.8674 | 77 | 76.6045 | -0.26291 | 76.7371
|  | 270 | 14310 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.8448 | -230.489 | 6.1932 | #NUM! | 8.085e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.8448 | 77 | 76.6045 | -0.24034 | 76.7597
|  | 270 | 14580 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.8244 | -255.262 | 6.1932 | #NUM! | 8.0838e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.8244 | 77 | 76.6045 | -0.21996 | 76.78
|  | 270 | 14850 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.8058 | -280.0349 | 6.1932 | #NUM! | 8.0827e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.8058 | 77 | 76.6045 | -0.20138 | 76.7986
|  | 270 | 15120 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.7888 | -304.8078 | 6.1932 | #NUM! | 8.0817e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.7888 | 77 | 76.6045 | -0.18431 | 76.8157
|  | 270 | 15390 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.773 | -329.5807 | 6.1932 | #NUM! | 8.0807e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.773 | 77 | 76.6045 | -0.16853 | 76.8315
|  | 270 | 15660 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.7583 | -354.3536 | 6.1932 | #NUM! | 8.0799e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.7583 | 77 | 76.6045 | -0.15385 | 76.8462
|  | 270 | 15930 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.7446 | -379.1265 | 6.1932 | #NUM! | 8.079e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.7446 | 77 | 76.6045 | -0.14012 | 76.8599
|  | 270 | 16200 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.7317 | -403.8994 | 6.1932 | #NUM! | 8.0783e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.7317 | 77 | 76.6045 | -0.12724 | 76.8728
|  | 270 | 16470 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.7196 | -428.6724 | 6.1932 | #NUM! | 8.0776e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.7196 | 77 | 76.6045 | -0.11511 | 76.8849
|  | 270 | 16740 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.7081 | -453.4453 | 6.1932 | #NUM! | 8.0769e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.7081 | 77 | 76.6045 | -0.10363 | 76.8964
|  | 270 | 17010 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6972 | -478.2182 | 6.1932 | #NUM! | 8.0762e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6972 | 77 | 76.6045 | -0.092756 | 76.9072
|  | 270 | 17280 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6869 | -502.9911 | 6.1932 | #NUM! | 8.0756e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6869 | 77 | 76.6045 | -0.082414 | 76.9176
|  | 270 | 17550 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.677 | -527.764 | 6.1932 | #NUM! | 8.075e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.677 | 77 | 76.6045 | -0.072556 | 76.9274
|  | 270 | 17820 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6676 | -552.5369 | 6.1932 | #NUM! | 8.0745e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6676 | 77 | 76.6045 | -0.063141 | 76.9369
|  | 270 | 18090 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6586 | -577.3098 | 6.1932 | #NUM! | 8.0739e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6586 | 77 | 76.6045 | -0.05413 | 76.9459
|  | 270 | 18360 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6499 | -602.0828 | 6.1932 | #NUM! | 8.0734e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6499 | 77 | 76.6045 | -0.045489 | 76.9545
|  | 270 | 18630 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6416 | -626.8557 | 6.1932 | #NUM! | 8.0729e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6416 | 77 | 76.6045 | -0.03719 | 76.9628
|  | 270 | 18900 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6337 | -651.6286 | 6.1932 | #NUM! | 8.0724e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6337 | 77 | 76.6045 | -0.029207 | 76.9708
|  | 270 | 19170 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.626 | -676.4015 | 6.1932 | #NUM! | 8.072e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.626 | 77 | 76.6045 | -0.021515 | 76.9785
|  | 270 | 19440 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6186 | -701.1744 | 6.1932 | #NUM! | 8.0715e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6186 | 77 | 76.6045 | -0.014096 | 76.9859
|  | 270 | 19710 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6114 | -725.9473 | 6.1932 | #NUM! | 8.0711e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6114 | 77 | 76.6045 | -0.0069298 | 76.9931
|  | 270 | 19980 | 0.1 | 27 |  | 0 | 0 | 0.1 | 27 |  | 5.19 | 76.6045 | -750.7202 | 6.1932 | #NUM! | 8.0707e-06 | 21.35 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM! | 76.6045 | 77 | 76.6045 | 0 | 77
Far end
[18 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | #NUM! | #NUM!
[8 empty] | Total system heat = | 1998 | W
[23 empty] | Pressure drop in pipe (Pa) = | #NUM!
[23 empty] | Pressure drop in pipe (bar) = | #NUM!
The above spreadsheet is duplicated here for calculation of the flows and pressure drops after the applied heat load uncertainty factor.
|  | Helium temperature for the supply end of the pipe in K. |  |  |  |  | 77 | K
|  | Helium pressure for the supply end of the pipe in bar. |  |  |  |  | 20 | bar
|  | This pressure and temperature will be used to find an initial helium density. | [8 empty] | Calculation of pressure drop for helium gas | [10 empty] | T. Peterson
[11 empty] | through a pipe with pressure drop and heat added | [10 empty] | 2000-01-02
|  |  |  | Enter a maximum delta-T |  |  | 2 | K | [17 empty] | Helium |  |  |  | Helium
Note: Bin size and number of bins |  |  |  | Linear heat flux (W/m) |  | Heat = | 0.125 | W/m pipe heat load |  |  |  |  | Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar | [12 empty] | temperatures | Supply | Supply |  | temperatures
are manually entered to match total length |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 13.58 | cm | [13 empty] | f incl factor |  |  |  | copied for | pipe inlet | pipe exit | Delta-T | inverted for
|  |  |  | Total pipe length (m) |  | Length = | 9700 | m |  |  |  |  | Helium |  |  | Helium | Helium |  | Number | Overall avg |  | 4 for D |  |  |  | supply pipe | temperature | temperature | from far end | return pipe
|  | Bin | [7 empty] | Total heat |  | Specific heat | temperature | mt | mShield | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
|  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | (J/gK) | (K) | (g/s) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar) | (K) | (K) | (K) | (K) | (K)
|  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin)
Supply end |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  | 5.19 | 77 | 1349.8948 | 8.5564 | 0.012468 | 8.0942e-06 | 13.58 | 1 | 747.533 | 1563634.3496 | 0.0089475 | 0 | 0 | 20 | 77 | 77 | 77.5476 | 0.54758 | 77.5476
|  | 135 | 135 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0024 | 1332.7819 | 8.5564 | 0.012467 | 8.0944e-06 | 13.58 | 1 | 738.0797 | 1543784.196 | 0.0089761 | 13500 | 3030.1711 | 19.9697 | 77.0024 | 77 | 77.5476 | 0.54514 | 77.5451
|  | 135 | 270 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0049 | 1315.669 | 8.5564 | 0.012448 | 8.0945e-06 | 13.58 | 1 | 729.7318 | 1523934.3986 | 0.0090052 | 13500 | 2967.0154 | 19.94 | 77.0049 | 77 | 77.5476 | 0.54266 | 77.5427
|  | 135 | 405 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0074 | 1298.5562 | 8.5564 | 0.012429 | 8.0947e-06 | 13.58 | 1 | 721.3354 | 1504084.9622 | 0.0090348 | 13500 | 2904.232 | 19.911 | 77.0074 | 77 | 77.5476 | 0.54016 | 77.5402
|  | 135 | 540 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.01 | 1281.4433 | 8.5564 | 0.01241 | 8.0948e-06 | 13.58 | 1 | 712.8911 | 1484235.8913 | 0.0090649 | 13500 | 2841.8313 | 19.8826 | 77.01 | 77 | 77.5476 | 0.53762 | 77.5376
|  | 135 | 675 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0125 | 1264.3304 | 8.5564 | 0.012392 | 8.095e-06 | 13.58 | 1 | 704.3998 | 1464387.1909 | 0.0090954 | 13500 | 2779.8236 | 19.8548 | 77.0125 | 77 | 77.5476 | 0.53505 | 77.5351
|  | 135 | 810 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0151 | 1247.2176 | 8.5564 | 0.012375 | 8.0951e-06 | 13.58 | 1 | 695.862 | 1444538.866 | 0.0091265 | 13500 | 2718.2192 | 19.8276 | 77.0151 | 77 | 77.5476 | 0.53244 | 77.5324
|  | 135 | 945 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0178 | 1230.1047 | 8.5564 | 0.012357 | 8.0953e-06 | 13.58 | 1 | 687.2787 | 1424690.9218 | 0.0091581 | 13500 | 2657.0286 | 19.801 | 77.0178 | 77 | 77.5476 | 0.5298 | 77.5298
|  | 135 | 1080 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0205 | 1212.9918 | 8.5564 | 0.01234 | 8.0954e-06 | 13.58 | 1 | 678.6505 | 1404843.3635 | 0.0091903 | 13500 | 2596.2619 | 19.7751 | 77.0205 | 77 | 77.5476 | 0.52712 | 77.5271
|  | 135 | 1215 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0232 | 1195.879 | 8.5564 | 0.012324 | 8.0956e-06 | 13.58 | 1 | 669.9782 | 1384996.1965 | 0.009223 | 13500 | 2535.9295 | 19.7497 | 77.0232 | 77 | 77.5476 | 0.5244 | 77.5244
|  | 135 | 1350 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0259 | 1178.7661 | 8.5564 | 0.012307 | 8.0958e-06 | 13.58 | 1 | 661.2625 | 1365149.4264 | 0.0092564 | 13500 | 2476.0415 | 19.7249 | 77.0259 | 77 | 77.5476 | 0.52164 | 77.5216
|  | 135 | 1485 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0287 | 1161.6532 | 8.5564 | 0.012291 | 8.0959e-06 | 13.58 | 1 | 652.5043 | 1345303.059 | 0.0092903 | 13500 | 2416.6084 | 19.7008 | 77.0287 | 77 | 77.5476 | 0.51884 | 77.5188
|  | 135 | 1620 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0316 | 1144.5404 | 8.5564 | 0.012276 | 8.0961e-06 | 13.58 | 1 | 643.7043 | 1325457.1001 | 0.0093249 | 13500 | 2357.6402 | 19.6772 | 77.0316 | 77 | 77.5476 | 0.516 | 77.516
|  | 135 | 1755 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0345 | 1127.4275 | 8.5564 | 0.012261 | 8.0963e-06 | 13.58 | 1 | 634.8633 | 1305611.556 | 0.0093602 | 13500 | 2299.1472 | 19.6542 | 77.0345 | 77 | 77.5476 | 0.51312 | 77.5131
|  | 135 | 1890 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0374 | 1110.3146 | 8.5564 | 0.012246 | 8.0965e-06 | 13.58 | 1 | 625.9821 | 1285766.4328 | 0.0093961 | 13500 | 2241.1394 | 19.6318 | 77.0374 | 77 | 77.5476 | 0.51019 | 77.5102
|  | 135 | 2025 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0404 | 1093.2018 | 8.5564 | 0.012232 | 8.0966e-06 | 13.58 | 1 | 617.0615 | 1265921.737 | 0.0094327 | 13500 | 2183.6271 | 19.61 | 77.0404 | 77 | 77.5476 | 0.50722 | 77.5072
|  | 135 | 2160 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0434 | 1076.0889 | 8.5564 | 0.012218 | 8.0968e-06 | 13.58 | 1 | 608.1023 | 1246077.4753 | 0.00947 | 13500 | 2126.6202 | 19.5887 | 77.0434 | 77 | 77.5476 | 0.5042 | 77.5042
|  | 135 | 2295 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0465 | 1058.976 | 8.5564 | 0.012204 | 8.097e-06 | 13.58 | 1 | 599.1053 | 1226233.6546 | 0.0095081 | 13500 | 2070.1289 | 19.568 | 77.0465 | 77 | 77.5476 | 0.50113 | 77.5011
|  | 135 | 2430 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0496 | 1041.8631 | 8.5564 | 0.01219 | 8.0972e-06 | 13.58 | 1 | 590.0713 | 1206390.282 | 0.0095469 | 13500 | 2014.1631 | 19.5478 | 77.0496 | 77 | 77.5476 | 0.498 | 77.498
|  | 135 | 2565 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0527 | 1024.7503 | 8.5564 | 0.012177 | 8.0974e-06 | 13.58 | 1 | 581.0012 | 1186547.3648 | 0.0095866 | 13500 | 1958.7328 | 19.5283 | 77.0527 | 77 | 77.5476 | 0.49483 | 77.4948
|  | 135 | 2700 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.056 | 1007.6374 | 8.5564 | 0.012165 | 8.0976e-06 | 13.58 | 1 | 571.8957 | 1166704.9107 | 0.0096271 | 13500 | 1903.848 | 19.5092 | 77.056 | 77 | 77.5476 | 0.49161 | 77.4916
|  | 135 | 2835 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0593 | 990.5245 | 8.5564 | 0.012152 | 8.0978e-06 | 13.58 | 1 | 562.7557 | 1146862.9273 | 0.0096685 | 13500 | 1849.5185 | 19.4907 | 77.0593 | 77 | 77.5476 | 0.48832 | 77.4883
|  | 135 | 2970 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0626 | 973.4117 | 8.5564 | 0.01214 | 8.098e-06 | 13.58 | 1 | 553.582 | 1127021.423 | 0.0097108 | 13500 | 1795.7541 | 19.4728 | 77.0626 | 77 | 77.5476 | 0.48498 | 77.485
|  | 135 | 3105 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.066 | 956.2988 | 8.5564 | 0.012128 | 8.0982e-06 | 13.58 | 1 | 544.3754 | 1107180.406 | 0.009754 | 13500 | 1742.5647 | 19.4553 | 77.066 | 77 | 77.5476 | 0.48158 | 77.4816
|  | 135 | 3240 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0695 | 939.1859 | 8.5564 | 0.012117 | 8.0984e-06 | 13.58 | 1 | 535.1367 | 1087339.885 | 0.0097982 | 13500 | 1689.96 | 19.4384 | 77.0695 | 77 | 77.5476 | 0.47812 | 77.4781
|  | 135 | 3375 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.073 | 922.0731 | 8.5564 | 0.012106 | 8.0986e-06 | 13.58 | 1 | 525.8669 | 1067499.8691 | 0.0098434 | 13500 | 1637.9498 | 19.4221 | 77.073 | 77 | 77.5476 | 0.47459 | 77.4746
|  | 135 | 3510 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0766 | 904.9602 | 8.5564 | 0.012095 | 8.0988e-06 | 13.58 | 1 | 516.5666 | 1047660.3676 | 0.0098897 | 13500 | 1586.5438 | 19.4062 | 77.0766 | 77 | 77.5476 | 0.471 | 77.471
|  | 135 | 3645 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0802 | 887.8473 | 8.5564 | 0.012085 | 8.099e-06 | 13.58 | 1 | 507.2367 | 1027821.3903 | 0.009937 | 13500 | 1535.7515 | 19.3908 | 77.0802 | 77 | 77.5476 | 0.46734 | 77.4673
|  | 135 | 3780 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.084 | 870.7345 | 8.5564 | 0.012075 | 8.0992e-06 | 13.58 | 1 | 497.878 | 1007982.9471 | 0.0099856 | 13500 | 1485.5826 | 19.376 | 77.084 | 77 | 77.5476 | 0.4636 | 77.4636
|  | 135 | 3915 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0878 | 853.6216 | 8.5564 | 0.012065 | 8.0994e-06 | 13.58 | 1 | 488.4914 | 988145.0486 | 0.010035 | 13500 | 1436.0467 | 19.3616 | 77.0878 | 77 | 77.5476 | 0.4598 | 77.4598
|  | 135 | 4050 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0917 | 836.5087 | 8.5564 | 0.012055 | 8.0997e-06 | 13.58 | 1 | 479.0776 | 968307.7057 | 0.010086 | 13500 | 1387.1533 | 19.3477 | 77.0917 | 77 | 77.5476 | 0.45591 | 77.4559
|  | 135 | 4185 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0956 | 819.3959 | 8.5564 | 0.012046 | 8.0999e-06 | 13.58 | 1 | 469.6375 | 948470.9296 | 0.010139 | 13500 | 1338.9118 | 19.3344 | 77.0956 | 77 | 77.5476 | 0.45194 | 77.4519
|  | 135 | 4320 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.0997 | 802.283 | 8.5564 | 0.012037 | 8.1002e-06 | 13.58 | 1 | 460.1719 | 928634.7322 | 0.010192 | 13500 | 1291.3319 | 19.3214 | 77.0997 | 77 | 77.5476 | 0.44789 | 77.4479
|  | 135 | 4455 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1038 | 785.1701 | 8.5564 | 0.012028 | 8.1004e-06 | 13.58 | 1 | 450.6815 | 908799.1259 | 0.010248 | 13500 | 1244.4228 | 19.309 | 77.1038 | 77 | 77.5476 | 0.44375 | 77.4437
|  | 135 | 4590 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1081 | 768.0572 | 8.5564 | 0.01202 | 8.1007e-06 | 13.58 | 1 | 441.1672 | 888964.1233 | 0.010304 | 13500 | 1198.1941 | 19.297 | 77.1081 | 77 | 77.5476 | 0.43951 | 77.4395
|  | 135 | 4725 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1124 | 750.9444 | 8.5564 | 0.012012 | 8.1009e-06 | 13.58 | 1 | 431.6298 | 869129.738 | 0.010363 | 13500 | 1152.6552 | 19.2855 | 77.1124 | 77 | 77.5476 | 0.43518 | 77.4352
|  | 135 | 4860 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1168 | 733.8315 | 8.5564 | 0.012004 | 8.1012e-06 | 13.58 | 1 | 422.0699 | 849295.984 | 0.010422 | 13500 | 1107.8155 | 19.2744 | 77.1168 | 77 | 77.5476 | 0.43075 | 77.4308
|  | 135 | 4995 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1214 | 716.7186 | 8.5564 | 0.011996 | 8.1014e-06 | 13.58 | 1 | 412.4885 | 829462.876 | 0.010484 | 13500 | 1063.6843 | 19.2638 | 77.1214 | 77 | 77.5476 | 0.42622 | 77.4262
|  | 135 | 5130 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.126 | 699.6058 | 8.5564 | 0.011989 | 8.1017e-06 | 13.58 | 1 | 402.8862 | 809630.4293 | 0.010548 | 13500 | 1020.271 | 19.2536 | 77.126 | 77 | 77.5476 | 0.42157 | 77.4216
|  | 135 | 5265 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1308 | 682.4929 | 8.5564 | 0.011982 | 8.102e-06 | 13.58 | 1 | 393.2639 | 789798.6601 | 0.010613 | 13500 | 977.5851 | 19.2438 | 77.1308 | 77 | 77.5476 | 0.4168 | 77.4168
|  | 135 | 5400 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1357 | 665.38 | 8.5564 | 0.011975 | 8.1023e-06 | 13.58 | 1 | 383.6223 | 769967.5854 | 0.010681 | 13500 | 935.6359 | 19.2344 | 77.1357 | 77 | 77.5476 | 0.41192 | 77.4119
|  | 135 | 5535 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1407 | 648.2672 | 8.5564 | 0.011968 | 8.1026e-06 | 13.58 | 1 | 373.962 | 750137.2228 | 0.010751 | 13500 | 894.4329 | 19.2255 | 77.1407 | 77 | 77.5476 | 0.4069 | 77.4069
|  | 135 | 5670 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1458 | 631.1543 | 8.5564 | 0.011962 | 8.1029e-06 | 13.58 | 1 | 364.2839 | 730307.5912 | 0.010823 | 13500 | 853.9856 | 19.217 | 77.1458 | 77 | 77.5476 | 0.40175 | 77.4018
|  | 135 | 5805 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1511 | 614.0414 | 8.5564 | 0.011956 | 8.1032e-06 | 13.58 | 1 | 354.5887 | 710478.7104 | 0.010898 | 13500 | 814.3034 | 19.2088 | 77.1511 | 77 | 77.5476 | 0.39646 | 77.3965
|  | 135 | 5940 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1566 | 596.9286 | 8.5564 | 0.01195 | 8.1035e-06 | 13.58 | 1 | 344.8771 | 690650.6011 | 0.010975 | 13500 | 775.3959 | 19.2011 | 77.1566 | 77 | 77.5476 | 0.39101 | 77.391
|  | 135 | 6075 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1622 | 579.8157 | 8.5564 | 0.011944 | 8.1039e-06 | 13.58 | 1 | 335.1497 | 670823.2856 | 0.011056 | 13500 | 737.2728 | 19.1937 | 77.1622 | 77 | 77.5476 | 0.3854 | 77.3854
|  | 135 | 6210 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.168 | 562.7028 | 8.5564 | 0.011939 | 8.1042e-06 | 13.58 | 1 | 325.4073 | 650996.787 | 0.011139 | 13500 | 699.9437 | 19.1867 | 77.168 | 77 | 77.5476 | 0.37962 | 77.3796
|  | 135 | 6345 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1739 | 545.59 | 8.5564 | 0.011934 | 8.1046e-06 | 13.58 | 1 | 315.6505 | 631171.1303 | 0.011225 | 13500 | 663.4184 | 19.1801 | 77.1739 | 77 | 77.5476 | 0.37366 | 77.3737
|  | 135 | 6480 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1801 | 528.4771 | 8.5564 | 0.011929 | 8.1049e-06 | 13.58 | 1 | 305.88 | 611346.3417 | 0.011315 | 13500 | 627.7068 | 19.1738 | 77.1801 | 77 | 77.5476 | 0.36751 | 77.3675
|  | 135 | 6615 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1864 | 511.3642 | 8.5564 | 0.011924 | 8.1053e-06 | 13.58 | 1 | 296.0965 | 591522.4492 | 0.011409 | 13500 | 592.8191 | 19.1679 | 77.1864 | 77 | 77.5476 | 0.36115 | 77.3612
|  | 135 | 6750 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.193 | 494.2513 | 8.5564 | 0.011919 | 8.1057e-06 | 13.58 | 1 | 286.3005 | 571699.4829 | 0.011507 | 13500 | 558.7652 | 19.1623 | 77.193 | 77 | 77.5476 | 0.35457 | 77.3546
|  | 135 | 6885 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.1998 | 477.1385 | 8.5564 | 0.011914 | 8.1061e-06 | 13.58 | 1 | 276.4926 | 551877.4745 | 0.011608 | 13500 | 525.5557 | 19.157 | 77.1998 | 77 | 77.5476 | 0.34776 | 77.3478
|  | 135 | 7020 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2069 | 460.0256 | 8.5564 | 0.01191 | 8.1065e-06 | 13.58 | 1 | 266.6736 | 532056.4585 | 0.011715 | 13500 | 493.2011 | 19.1521 | 77.2069 | 77 | 77.5476 | 0.34069 | 77.3407
|  | 135 | 7155 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2142 | 442.9127 | 8.5564 | 0.011906 | 8.107e-06 | 13.58 | 1 | 256.8439 | 512236.4716 | 0.011827 | 13500 | 461.7121 | 19.1475 | 77.2142 | 77 | 77.5476 | 0.33335 | 77.3334
|  | 135 | 7290 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2219 | 425.7999 | 8.5564 | 0.011902 | 8.1074e-06 | 13.58 | 1 | 247.0042 | 492417.5535 | 0.011944 | 13500 | 431.0999 | 19.1431 | 77.2219 | 77 | 77.5476 | 0.32571 | 77.3257
|  | 135 | 7425 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2298 | 408.687 | 8.5564 | 0.011898 | 8.1079e-06 | 13.58 | 1 | 237.1549 | 472599.747 | 0.012067 | 13500 | 401.3757 | 19.1391 | 77.2298 | 77 | 77.5476 | 0.31776 | 77.3178
|  | 135 | 7560 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2381 | 391.5741 | 8.5564 | 0.011894 | 8.1084e-06 | 13.58 | 1 | 227.2967 | 452783.0985 | 0.012197 | 13500 | 372.5512 | 19.1354 | 77.2381 | 77 | 77.5476 | 0.30946 | 77.3095
|  | 135 | 7695 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2468 | 374.4613 | 8.5564 | 0.01189 | 8.1089e-06 | 13.58 | 1 | 217.43 | 432967.6585 | 0.012335 | 13500 | 344.6385 | 19.132 | 77.2468 | 77 | 77.5476 | 0.30077 | 77.3008
|  | 135 | 7830 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2559 | 357.3484 | 8.5564 | 0.011887 | 8.1094e-06 | 13.58 | 1 | 207.5552 | 413153.482 | 0.01248 | 13500 | 317.6502 | 19.1288 | 77.2559 | 77 | 77.5476 | 0.29167 | 77.2917
|  | 135 | 7965 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2655 | 340.2355 | 8.5564 | 0.011883 | 8.11e-06 | 13.58 | 1 | 197.673 | 393340.6295 | 0.012634 | 13500 | 291.5991 | 19.1259 | 77.2655 | 77 | 77.5476 | 0.28212 | 77.2821
|  | 135 | 8100 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2755 | 323.1227 | 8.5564 | 0.01188 | 8.1106e-06 | 13.58 | 1 | 187.7837 | 373529.1673 | 0.012798 | 13500 | 266.499 | 19.1232 | 77.2755 | 77 | 77.5476 | 0.27205 | 77.2721
|  | 135 | 8235 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2861 | 306.0098 | 8.5564 | 0.011877 | 8.1112e-06 | 13.58 | 1 | 177.8877 | 353719.1688 | 0.012974 | 13500 | 242.364 | 19.1208 | 77.2861 | 77 | 77.5476 | 0.26143 | 77.2614
|  | 135 | 8370 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.2974 | 288.8969 | 8.5564 | 0.011874 | 8.1119e-06 | 13.58 | 1 | 167.9855 | 333910.7157 | 0.013162 | 13500 | 219.2091 | 19.1186 | 77.2974 | 77 | 77.5476 | 0.25017 | 77.2502
|  | 135 | 8505 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.3094 | 271.784 | 8.5564 | 0.01187 | 8.1126e-06 | 13.58 | 1 | 158.0775 | 314103.8992 | 0.013365 | 13500 | 197.0502 | 19.1166 | 77.3094 | 77 | 77.5476 | 0.23821 | 77.2382
|  | 135 | 8640 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.3221 | 254.6712 | 8.5564 | 0.011867 | 8.1134e-06 | 13.58 | 1 | 148.1638 | 294298.8222 | 0.013584 | 13500 | 175.9042 | 19.1149 | 77.3221 | 77 | 77.5476 | 0.22544 | 77.2254
|  | 135 | 8775 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.3358 | 237.5583 | 8.5564 | 0.011864 | 8.1142e-06 | 13.58 | 1 | 138.245 | 274495.6011 | 0.013823 | 13500 | 155.7892 | 19.1133 | 77.3358 | 77 | 77.5476 | 0.21176 | 77.2118
|  | 135 | 8910 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.3506 | 220.4454 | 8.5564 | 0.011861 | 8.1151e-06 | 13.58 | 1 | 128.3213 | 254694.3694 | 0.014084 | 13500 | 136.7245 | 19.1119 | 77.3506 | 77 | 77.5476 | 0.19701 | 77.197
|  | 135 | 9045 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.3666 | 203.3326 | 8.5564 | 0.011857 | 8.116e-06 | 13.58 | 1 | 118.3928 | 234895.2809 | 0.014372 | 13500 | 118.7313 | 19.1107 | 77.3666 | 77 | 77.5476 | 0.18102 | 77.181
|  | 135 | 9180 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.384 | 186.2197 | 8.5564 | 0.011854 | 8.1171e-06 | 13.58 | 1 | 108.4598 | 215098.5156 | 0.014692 | 13500 | 101.8326 | 19.1097 | 77.384 | 77 | 77.5476 | 0.16356 | 77.1636
|  | 135 | 9315 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.4032 | 169.1068 | 8.5564 | 0.01185 | 8.1182e-06 | 13.58 | 1 | 98.5225 | 195304.2864 | 0.015051 | 13500 | 86.0538 | 19.1089 | 77.4032 | 77 | 77.5476 | 0.14433 | 77.1443
|  | 135 | 9450 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.4246 | 151.994 | 8.5564 | 0.011847 | 8.1195e-06 | 13.58 | 1 | 88.5809 | 175512.8492 | 0.015458 | 13500 | 71.4234 | 19.1082 | 77.4246 | 77 | 77.5476 | 0.12294 | 77.1229
|  | 135 | 9585 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.4487 | 134.8811 | 8.5564 | 0.011843 | 8.1209e-06 | 13.58 | 1 | 78.6351 | 155724.5176 | 0.015927 | 13500 | 57.9735 | 19.1076 | 77.4487 | 77 | 77.5476 | 0.098831 | 77.0988
|  | 135 | 9720 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.4764 | 117.7682 | 8.5564 | 0.011838 | 8.1226e-06 | 13.58 | 1 | 68.6849 | 135939.6844 | 0.016478 | 13500 | 45.7409 | 19.1071 | 77.4764 | 77 | 77.5476 | 0.071222 | 77.0712
|  | 135 | 9855 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.5087 | 100.6554 | 8.5564 | 0.011833 | 8.1245e-06 | 13.58 | 1 | 58.7302 | 116158.8565 | 0.017139 | 13500 | 34.7686 | 19.1068 | 77.5087 | 77 | 77.5476 | 0.03892 | 77.0389
|  | 135 | 9990 | 0.125 | 16.875 |  | 0 | 0 | 0.125 | 16.875 |  | 5.19 | 77.5476 | 83.5425 | 8.5564 | 0.011827 | 8.1268e-06 | 13.58 | 1 | 48.7706 | 96382.7133 | 0.017957 | 13500 | 25.1083 | 19.1065 | 77.5476 | 77 | 77.5476 | 0 | 77
Far end
[18 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | 20.9462 | 19.1063
[8 empty] | Total system heat = | 1248.75 | W
[23 empty] | Pressure drop in pipe (Pa) = | 89369.0881
[23 empty] | Pressure drop in pipe (bar) = | 0.89369

## Thermal shield
|  |  | Helium temperature for the supply end of the pipe in K. |  |  |  |  | 76.6045 | K
|  |  | Helium pressure for the supply end of the pipe in bar. |  |  |  |  | #NUM! | bar
|  |  | This pressure and temperature will be used to find an initial helium density. | [10 empty] | Calculation of pressure drop for helium gas | [9 empty] | T. Peterson
[14 empty] | through a pipe with pressure drop and heat added | [9 empty] | 2000-01-02
[5 empty] | Enter a linear heat flux (W/m) |  | Heat = | 4.2 | W/m | [6 empty] | Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar
| Heat per |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 2.29 | cm | [14 empty] | f incl factor
| section in |  |  |  | Enter a total pipe length (m) |  | Length = | 135 | m |  |  |  | Total heat |  |  | Helium |  | Helium | Helium |  | Number | Overall avg |  | 4 for D
| Watts: |  | Bin | [7 empty] | Total heat |  | in each |  | Specific heat | temperature | mt | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| Qsect (W) |  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | section |  | (J/gK) | (K) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
|  |  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin) |  | Qsect (W)
Supply end |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 5.19 | 76.6045 | 12.3865 | #NUM! | 8.0707e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 0 | #NUM! | #NUM!
Section 1 | 141.75 |  | 2.25 | 2.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  | 141.75 |  | 5.19 | 76.7515 | 12.3865 | #NUM! | 8.0794e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 4.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 76.8985 | 12.3865 | #NUM! | 8.0882e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 6.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 77.0455 | 12.3865 | #NUM! | 8.0969e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 9 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 77.1925 | 12.3865 | #NUM! | 8.1057e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 11.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 77.3395 | 12.3865 | #NUM! | 8.1144e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 13.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 77.4865 | 12.3865 | #NUM! | 8.1232e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 15.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 77.6335 | 12.3865 | #NUM! | 8.1319e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 18 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 77.7805 | 12.3865 | #NUM! | 8.1406e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 20.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 77.9275 | 12.3865 | #NUM! | 8.1494e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 22.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 78.0745 | 12.3865 | #NUM! | 8.1581e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 24.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 78.2215 | 12.3865 | #NUM! | 8.1669e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 27 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 78.3685 | 12.3865 | #NUM! | 8.1756e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 29.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 78.5155 | 12.3865 | #NUM! | 8.1843e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 31.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 78.6625 | 12.3865 | #NUM! | 8.1931e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 33.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 78.8095 | 12.3865 | #NUM! | 8.2018e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Section 2 | 141.75 |  | 2.25 | 36 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  | 141.75 |  | 5.19 | 78.9565 | 12.3865 | #NUM! | 8.2106e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 38.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 79.1035 | 12.3865 | #NUM! | 8.2193e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 40.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 79.2505 | 12.3865 | #NUM! | 8.228e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 42.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 79.3975 | 12.3865 | #NUM! | 8.2368e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 45 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 79.5445 | 12.3865 | #NUM! | 8.2455e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 47.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 79.6915 | 12.3865 | #NUM! | 8.2543e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 49.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 79.8385 | 12.3865 | #NUM! | 8.263e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 51.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 79.9855 | 12.3865 | #NUM! | 8.2718e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 54 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 80.1325 | 12.3865 | #NUM! | 8.2805e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 56.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 80.2795 | 12.3865 | #NUM! | 8.2892e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 58.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 80.4265 | 12.3865 | #NUM! | 8.298e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 60.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 80.5735 | 12.3865 | #NUM! | 8.3067e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 63 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 80.7205 | 12.3865 | #NUM! | 8.3155e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 65.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 80.8675 | 12.3865 | #NUM! | 8.3242e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 67.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 81.0145 | 12.3865 | #NUM! | 8.3329e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Section 3 | 141.75 |  | 2.25 | 69.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  | 141.75 |  | 5.19 | 81.1615 | 12.3865 | #NUM! | 8.3417e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 72 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 81.3085 | 12.3865 | #NUM! | 8.3504e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 74.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 81.4555 | 12.3865 | #NUM! | 8.3592e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 76.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 81.6025 | 12.3865 | #NUM! | 8.3679e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 78.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 81.7495 | 12.3865 | #NUM! | 8.3766e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 81 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 81.8965 | 12.3865 | #NUM! | 8.3854e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 83.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 82.0435 | 12.3865 | #NUM! | 8.3941e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 85.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 82.1905 | 12.3865 | #NUM! | 8.4029e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 87.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 82.3375 | 12.3865 | #NUM! | 8.4116e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 90 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 82.4845 | 12.3865 | #NUM! | 8.4204e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 92.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 82.6315 | 12.3865 | #NUM! | 8.4291e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 94.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 82.7785 | 12.3865 | #NUM! | 8.4378e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 96.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 82.9255 | 12.3865 | #NUM! | 8.4466e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 99 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 83.0725 | 12.3865 | #NUM! | 8.4553e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 101.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 83.2195 | 12.3865 | #NUM! | 8.4641e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Section 4 | 141.75 |  | 2.25 | 103.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  | 141.75 |  | 5.19 | 83.3665 | 12.3865 | #NUM! | 8.4728e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 105.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 83.5135 | 12.3865 | #NUM! | 8.4815e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 108 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 83.6605 | 12.3865 | #NUM! | 8.4903e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 110.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 83.8075 | 12.3865 | #NUM! | 8.499e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 112.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 83.9545 | 12.3865 | #NUM! | 8.5078e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 114.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 84.1015 | 12.3865 | #NUM! | 8.5165e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 117 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 84.2485 | 12.3865 | #NUM! | 8.5253e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 119.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 84.3955 | 12.3865 | #NUM! | 8.534e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 121.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 84.5425 | 12.3865 | #NUM! | 8.5427e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 123.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 84.6895 | 12.3865 | #NUM! | 8.5515e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 126 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 84.8365 | 12.3865 | #NUM! | 8.5602e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 128.25 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 84.9835 | 12.3865 | #NUM! | 8.569e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 130.5 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 85.1305 | 12.3865 | #NUM! | 8.5777e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 132.75 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 85.2775 | 12.3865 | #NUM! | 8.5864e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 135 | 4.2 | 9.45 |  | 0 | 0 | 4.2 | 9.45 |  |  |  | 5.19 | 85.4245 | 12.3865 | #NUM! | 8.5952e-06 | 2.29 | 1 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Far end | [19 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | #NUM! | #NUM!
Total dynamic heat = | 567 | W | [9 empty] | Total system heat = | 567 | W | [10 empty] | Pressure drop in pipe (Pa) = | #NUM!
[25 empty] | Pressure drop in pipe (bar) = | #NUM!
The above spreadsheet is duplicated here for calculation of the flows and pressure drops after the applied heat load uncertainty factor.
|  |  | Helium temperature for the supply end of the pipe in K. |  |  |  |  | 77.5476 | K
|  |  | Helium pressure for the supply end of the pipe in bar. |  |  |  |  | 19.1063 | bar
|  |  | This pressure and temperature will be used to find an initial helium density. | [10 empty] | Calculation of pressure drop for helium gas | [9 empty] | T. Peterson
[14 empty] | through a pipe with pressure drop and heat added | [9 empty] | 2000-01-02
[5 empty] | Enter a linear heat flux (W/m) |  | Heat = | 5.25 | W/m | [6 empty] | Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar
| Heat per |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 2.29 | cm | [14 empty] | f incl factor
| section in |  |  |  | Enter a total pipe length (m) |  | Length = | 135 | m |  |  |  | Total heat |  |  | Helium |  | Helium | Helium |  | Number | Overall avg |  | 4 for D
| Watts: |  | Bin | [7 empty] | Total heat |  | in each |  | Specific heat | temperature | mt | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| Qsect (W) |  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | section |  | (J/gK) | (K) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
|  |  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin) |  | Qsect (W)
Supply end |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 5.19 | 77.5476 | 17.1129 | 0.011826 | 8.1268e-06 | 2.29 | 1 | 351.3278 | 117078.9556 | 0.017105 | 0 | 0 | 19.1063
Section 1 | 177.1875 |  | 2.25 | 2.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  | 177.1875 |  | 5.19 | 77.6806 | 17.1129 | 0.011806 | 8.1347e-06 | 2.29 | 1 | 351.9304 | 116965.1292 | 0.017109 | 225 | 122.9019 | 19.1051
|  |  | 2.25 | 4.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 77.8136 | 17.1129 | 0.011785 | 8.1426e-06 | 2.29 | 1 | 352.5556 | 116851.5238 | 0.017113 | 225 | 123.1501 | 19.1038
|  |  | 2.25 | 6.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 77.9466 | 17.1129 | 0.011764 | 8.1505e-06 | 2.29 | 1 | 353.181 | 116738.139 | 0.017117 | 225 | 123.3985 | 19.1026
|  |  | 2.25 | 9 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 78.0796 | 17.1129 | 0.011743 | 8.1584e-06 | 2.29 | 1 | 353.8064 | 116624.974 | 0.017121 | 225 | 123.647 | 19.1014
|  |  | 2.25 | 11.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 78.2126 | 17.1129 | 0.011723 | 8.1663e-06 | 2.29 | 1 | 354.4321 | 116512.0281 | 0.017126 | 225 | 123.8957 | 19.1001
|  |  | 2.25 | 13.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 78.3456 | 17.1129 | 0.011702 | 8.1742e-06 | 2.29 | 1 | 355.0578 | 116399.3008 | 0.01713 | 225 | 124.1445 | 19.0989
|  |  | 2.25 | 15.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 78.4786 | 17.1129 | 0.011681 | 8.1822e-06 | 2.29 | 1 | 355.6837 | 116286.7914 | 0.017134 | 225 | 124.3934 | 19.0977
|  |  | 2.25 | 18 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 78.6116 | 17.1129 | 0.011661 | 8.1901e-06 | 2.29 | 1 | 356.3097 | 116174.4994 | 0.017138 | 225 | 124.6424 | 19.0964
|  |  | 2.25 | 20.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 78.7446 | 17.1129 | 0.011641 | 8.198e-06 | 2.29 | 1 | 356.9358 | 116062.4239 | 0.017142 | 225 | 124.8915 | 19.0952
|  |  | 2.25 | 22.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 78.8776 | 17.1129 | 0.01162 | 8.2059e-06 | 2.29 | 1 | 357.562 | 115950.5646 | 0.017146 | 225 | 125.1408 | 19.0939
|  |  | 2.25 | 24.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 79.0106 | 17.1129 | 0.0116 | 8.2138e-06 | 2.29 | 1 | 358.1884 | 115838.9206 | 0.01715 | 225 | 125.3902 | 19.0927
|  |  | 2.25 | 27 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 79.1436 | 17.1129 | 0.01158 | 8.2217e-06 | 2.29 | 1 | 358.8149 | 115727.4914 | 0.017154 | 225 | 125.6398 | 19.0914
|  |  | 2.25 | 29.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 79.2766 | 17.1129 | 0.011559 | 8.2296e-06 | 2.29 | 1 | 359.4416 | 115616.2764 | 0.017159 | 225 | 125.8895 | 19.0901
|  |  | 2.25 | 31.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 79.4096 | 17.1129 | 0.011539 | 8.2375e-06 | 2.29 | 1 | 360.0683 | 115505.2749 | 0.017163 | 225 | 126.1393 | 19.0889
|  |  | 2.25 | 33.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 79.5426 | 17.1129 | 0.011519 | 8.2454e-06 | 2.29 | 1 | 360.6952 | 115394.4864 | 0.017167 | 225 | 126.3892 | 19.0876
Section 2 | 177.1875 |  | 2.25 | 36 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  | 177.1875 |  | 5.19 | 79.6756 | 17.1129 | 0.011499 | 8.2533e-06 | 2.29 | 1 | 361.3222 | 115283.9102 | 0.017171 | 225 | 126.6393 | 19.0863
|  |  | 2.25 | 38.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 79.8086 | 17.1129 | 0.011479 | 8.2612e-06 | 2.29 | 1 | 361.9494 | 115173.5457 | 0.017175 | 225 | 126.8895 | 19.0851
|  |  | 2.25 | 40.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 79.9416 | 17.1129 | 0.011459 | 8.2691e-06 | 2.29 | 1 | 362.5767 | 115063.3923 | 0.017179 | 225 | 127.1398 | 19.0838
|  |  | 2.25 | 42.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 80.0746 | 17.1129 | 0.01144 | 8.2771e-06 | 2.29 | 1 | 363.2041 | 114953.4494 | 0.017183 | 225 | 127.3902 | 19.0825
|  |  | 2.25 | 45 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 80.2076 | 17.1129 | 0.01142 | 8.285e-06 | 2.29 | 1 | 363.8317 | 114843.7164 | 0.017187 | 225 | 127.6408 | 19.0813
|  |  | 2.25 | 47.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 80.3406 | 17.1129 | 0.0114 | 8.2929e-06 | 2.29 | 1 | 364.4594 | 114734.1927 | 0.017191 | 225 | 127.8915 | 19.08
|  |  | 2.25 | 49.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 80.4736 | 17.1129 | 0.011381 | 8.3008e-06 | 2.29 | 1 | 365.0872 | 114624.8777 | 0.017196 | 225 | 128.1424 | 19.0787
|  |  | 2.25 | 51.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 80.6066 | 17.1129 | 0.011361 | 8.3087e-06 | 2.29 | 1 | 365.7151 | 114515.7709 | 0.0172 | 225 | 128.3933 | 19.0774
|  |  | 2.25 | 54 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 80.7396 | 17.1129 | 0.011342 | 8.3166e-06 | 2.29 | 1 | 366.3432 | 114406.8715 | 0.017204 | 225 | 128.6444 | 19.0761
|  |  | 2.25 | 56.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 80.8726 | 17.1129 | 0.011322 | 8.3245e-06 | 2.29 | 1 | 366.9714 | 114298.1791 | 0.017208 | 225 | 128.8956 | 19.0748
|  |  | 2.25 | 58.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 81.0056 | 17.1129 | 0.011303 | 8.3324e-06 | 2.29 | 1 | 367.5998 | 114189.6929 | 0.017212 | 225 | 129.147 | 19.0735
|  |  | 2.25 | 60.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 81.1386 | 17.1129 | 0.011284 | 8.3403e-06 | 2.29 | 1 | 368.2282 | 114081.4126 | 0.017216 | 225 | 129.3985 | 19.0723
|  |  | 2.25 | 63 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 81.2716 | 17.1129 | 0.011264 | 8.3482e-06 | 2.29 | 1 | 368.8568 | 113973.3374 | 0.01722 | 225 | 129.6501 | 19.071
|  |  | 2.25 | 65.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 81.4046 | 17.1129 | 0.011245 | 8.3561e-06 | 2.29 | 1 | 369.4856 | 113865.4667 | 0.017224 | 225 | 129.9019 | 19.0697
|  |  | 2.25 | 67.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 81.5376 | 17.1129 | 0.011226 | 8.3641e-06 | 2.29 | 1 | 370.1145 | 113757.8001 | 0.017228 | 225 | 130.1537 | 19.0684
Section 3 | 177.1875 |  | 2.25 | 69.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  | 177.1875 |  | 5.19 | 81.6706 | 17.1129 | 0.011207 | 8.372e-06 | 2.29 | 1 | 370.7435 | 113650.3369 | 0.017232 | 225 | 130.4057 | 19.067
|  |  | 2.25 | 72 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 81.8036 | 17.1129 | 0.011188 | 8.3799e-06 | 2.29 | 1 | 371.3726 | 113543.0765 | 0.017236 | 225 | 130.6579 | 19.0657
|  |  | 2.25 | 74.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 81.9366 | 17.1129 | 0.011169 | 8.3878e-06 | 2.29 | 1 | 372.0019 | 113436.0184 | 0.01724 | 225 | 130.9101 | 19.0644
|  |  | 2.25 | 76.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 82.0696 | 17.1129 | 0.01115 | 8.3957e-06 | 2.29 | 1 | 372.6313 | 113329.162 | 0.017245 | 225 | 131.1625 | 19.0631
|  |  | 2.25 | 78.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 82.2026 | 17.1129 | 0.011131 | 8.4036e-06 | 2.29 | 1 | 373.2609 | 113222.5067 | 0.017249 | 225 | 131.4151 | 19.0618
|  |  | 2.25 | 81 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 82.3356 | 17.1129 | 0.011113 | 8.4115e-06 | 2.29 | 1 | 373.8906 | 113116.052 | 0.017253 | 225 | 131.6677 | 19.0605
|  |  | 2.25 | 83.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 82.4686 | 17.1129 | 0.011094 | 8.4194e-06 | 2.29 | 1 | 374.5204 | 113009.7972 | 0.017257 | 225 | 131.9205 | 19.0592
|  |  | 2.25 | 85.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 82.6016 | 17.1129 | 0.011075 | 8.4273e-06 | 2.29 | 1 | 375.1504 | 112903.7419 | 0.017261 | 225 | 132.1734 | 19.0579
|  |  | 2.25 | 87.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 82.7346 | 17.1129 | 0.011057 | 8.4352e-06 | 2.29 | 1 | 375.7805 | 112797.8855 | 0.017265 | 225 | 132.4265 | 19.0565
|  |  | 2.25 | 90 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 82.8676 | 17.1129 | 0.011038 | 8.4431e-06 | 2.29 | 1 | 376.4107 | 112692.2274 | 0.017269 | 225 | 132.6797 | 19.0552
|  |  | 2.25 | 92.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 83.0006 | 17.1129 | 0.01102 | 8.451e-06 | 2.29 | 1 | 377.0411 | 112586.767 | 0.017273 | 225 | 132.933 | 19.0539
|  |  | 2.25 | 94.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 83.1336 | 17.1129 | 0.011001 | 8.459e-06 | 2.29 | 1 | 377.6716 | 112481.5039 | 0.017277 | 225 | 133.1864 | 19.0525
|  |  | 2.25 | 96.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 83.2666 | 17.1129 | 0.010983 | 8.4669e-06 | 2.29 | 1 | 378.3023 | 112376.4374 | 0.017281 | 225 | 133.44 | 19.0512
|  |  | 2.25 | 99 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 83.3996 | 17.1129 | 0.010965 | 8.4748e-06 | 2.29 | 1 | 378.9331 | 112271.567 | 0.017285 | 225 | 133.6937 | 19.0499
|  |  | 2.25 | 101.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 83.5326 | 17.1129 | 0.010947 | 8.4827e-06 | 2.29 | 1 | 379.564 | 112166.8921 | 0.017289 | 225 | 133.9475 | 19.0485
Section 4 | 177.1875 |  | 2.25 | 103.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  | 177.1875 |  | 5.19 | 83.6656 | 17.1129 | 0.010928 | 8.4906e-06 | 2.29 | 1 | 380.1951 | 112062.4122 | 0.017293 | 225 | 134.2015 | 19.0472
|  |  | 2.25 | 105.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 83.7986 | 17.1129 | 0.01091 | 8.4985e-06 | 2.29 | 1 | 380.8263 | 111958.1268 | 0.017297 | 225 | 134.4556 | 19.0458
|  |  | 2.25 | 108 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 83.9316 | 17.1129 | 0.010892 | 8.5064e-06 | 2.29 | 1 | 381.4577 | 111854.0353 | 0.017301 | 225 | 134.7098 | 19.0445
|  |  | 2.25 | 110.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.0646 | 17.1129 | 0.010874 | 8.5143e-06 | 2.29 | 1 | 382.0891 | 111750.1372 | 0.017305 | 225 | 134.9642 | 19.0431
|  |  | 2.25 | 112.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.1976 | 17.1129 | 0.010856 | 8.5222e-06 | 2.29 | 1 | 382.7208 | 111646.432 | 0.017309 | 225 | 135.2187 | 19.0418
|  |  | 2.25 | 114.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.3306 | 17.1129 | 0.010838 | 8.5301e-06 | 2.29 | 1 | 383.3526 | 111542.919 | 0.017313 | 225 | 135.4733 | 19.0404
|  |  | 2.25 | 117 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.4636 | 17.1129 | 0.010821 | 8.538e-06 | 2.29 | 1 | 383.9845 | 111439.5978 | 0.017317 | 225 | 135.7281 | 19.0391
|  |  | 2.25 | 119.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.5966 | 17.1129 | 0.010803 | 8.546e-06 | 2.29 | 1 | 384.6165 | 111336.4678 | 0.017321 | 225 | 135.9829 | 19.0377
|  |  | 2.25 | 121.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.7296 | 17.1129 | 0.010785 | 8.5539e-06 | 2.29 | 1 | 385.2487 | 111233.5285 | 0.017325 | 225 | 136.238 | 19.0364
|  |  | 2.25 | 123.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.8626 | 17.1129 | 0.010767 | 8.5618e-06 | 2.29 | 1 | 385.8811 | 111130.7794 | 0.017329 | 225 | 136.4931 | 19.035
|  |  | 2.25 | 126 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 84.9956 | 17.1129 | 0.01075 | 8.5697e-06 | 2.29 | 1 | 386.5135 | 111028.22 | 0.017333 | 225 | 136.7484 | 19.0336
|  |  | 2.25 | 128.25 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 85.1286 | 17.1129 | 0.010732 | 8.5776e-06 | 2.29 | 1 | 387.1462 | 110925.8497 | 0.017337 | 225 | 137.0038 | 19.0323
|  |  | 2.25 | 130.5 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 85.2616 | 17.1129 | 0.010715 | 8.5855e-06 | 2.29 | 1 | 387.7789 | 110823.6679 | 0.017341 | 225 | 137.2594 | 19.0309
|  |  | 2.25 | 132.75 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 85.3946 | 17.1129 | 0.010697 | 8.5934e-06 | 2.29 | 1 | 388.4118 | 110721.6743 | 0.017345 | 225 | 137.515 | 19.0295
|  |  | 2.25 | 135 | 5.25 | 11.8125 |  | 0 | 0 | 5.25 | 11.8125 |  |  |  | 5.19 | 85.5276 | 17.1129 | 0.01068 | 8.6013e-06 | 2.29 | 1 | 389.0449 | 110619.8682 | 0.017349 | 225 | 137.7708 | 19.0281
Far end | [19 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | 80.8225 | 19.0273
Total dynamic heat = | 708.75 | W | [9 empty] | Total system heat = | 708.75 | W | [10 empty] | Pressure drop in pipe (Pa) = | 7898.7767
[25 empty] | Pressure drop in pipe (bar) = | 0.078988

## Trace Tube Helium
|  |  | Helium temperature for the supply end of the tube in K. |  |  |  |  | 85.4245 | K
|  |  | Helium pressure for the supply end of the tube in bar. |  |  |  |  | #NUM! | bar
|  |  | This pressure and temperature will be used to find an initial helium density. | [10 empty] | Calculation of pressure drop for helium gas | [9 empty] | T. Peterson
[14 empty] | through a pipe with pressure drop and heat added | [9 empty] | 2000-01-22
[5 empty] | Enter the desired delta-T in K |  |  | 21 | K | Calc'd del-P | #NUM! | bar
[5 empty] | Enter a linear heat flux (W/m) |  | Heat = | 5 | W/m per beam | [6 empty] | Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar
| Heat per |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 0.533 | cm | [14 empty] | f incl factor
| section in |  |  |  | Enter a total pipe length (m) |  | Length = | 135 | m |  |  |  | Total heat |  |  | Helium |  | Helium | Helium |  | Number | Overall avg |  | 4 for D
| Watts: |  | Bin | [7 empty] | Total heat |  | in each |  | Specific heat | temperature | mt | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| Qsect (W) |  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | section |  | (J/gK) | (K) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
|  |  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin) |  | Qsect (W)
Supply end |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 5.19 | 85.4245 | 6.1932 | #NUM! | 8.5952e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 0 | #NUM! | #NUM!
Section 1 | 168.75 |  | 2.25 | 2.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  | 168.75 |  | 5.19 | 85.7745 | 6.1932 | #NUM! | 8.616e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 4.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 86.1245 | 6.1932 | #NUM! | 8.6368e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 6.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 86.4745 | 6.1932 | #NUM! | 8.6576e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 9 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 86.8245 | 6.1932 | #NUM! | 8.6784e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 11.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 87.1745 | 6.1932 | #NUM! | 8.6992e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 13.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 87.5245 | 6.1932 | #NUM! | 8.7201e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 15.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 87.8745 | 6.1932 | #NUM! | 8.7409e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 18 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 88.2245 | 6.1932 | #NUM! | 8.7617e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 20.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 88.5745 | 6.1932 | #NUM! | 8.7825e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 22.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 88.9245 | 6.1932 | #NUM! | 8.8033e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 24.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 89.2745 | 6.1932 | #NUM! | 8.8241e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 27 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 89.6245 | 6.1932 | #NUM! | 8.8449e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 29.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 89.9745 | 6.1932 | #NUM! | 8.8657e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 31.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 90.3245 | 6.1932 | #NUM! | 8.8866e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 33.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 90.6745 | 6.1932 | #NUM! | 8.9074e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Section 2 | 168.75 |  | 2.25 | 36 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  | 168.75 |  | 5.19 | 91.0245 | 6.1932 | #NUM! | 8.9282e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 38.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 91.3745 | 6.1932 | #NUM! | 8.949e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 40.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 91.7245 | 6.1932 | #NUM! | 8.9698e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 42.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 92.0745 | 6.1932 | #NUM! | 8.9906e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 45 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 92.4245 | 6.1932 | #NUM! | 9.0114e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 47.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 92.7745 | 6.1932 | #NUM! | 9.0322e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 49.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 93.1245 | 6.1932 | #NUM! | 9.0531e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 51.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 93.4745 | 6.1932 | #NUM! | 9.0739e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 54 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 93.8245 | 6.1932 | #NUM! | 9.0947e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 56.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 94.1745 | 6.1932 | #NUM! | 9.1155e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 58.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 94.5245 | 6.1932 | #NUM! | 9.1363e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 60.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 94.8745 | 6.1932 | #NUM! | 9.1571e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 63 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 95.2245 | 6.1932 | #NUM! | 9.1779e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 65.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 95.5745 | 6.1932 | #NUM! | 9.1987e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 67.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 95.9245 | 6.1932 | #NUM! | 9.2196e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Section 3 | 168.75 |  | 2.25 | 69.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  | 168.75 |  | 5.19 | 96.2745 | 6.1932 | #NUM! | 9.2404e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 72 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 96.6245 | 6.1932 | #NUM! | 9.2612e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 74.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 96.9745 | 6.1932 | #NUM! | 9.282e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 76.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 97.3245 | 6.1932 | #NUM! | 9.3028e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 78.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 97.6745 | 6.1932 | #NUM! | 9.3236e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 81 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 98.0245 | 6.1932 | #NUM! | 9.3444e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 83.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 98.3745 | 6.1932 | #NUM! | 9.3652e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 85.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 98.7245 | 6.1932 | #NUM! | 9.3861e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 87.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 99.0745 | 6.1932 | #NUM! | 9.4069e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 90 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 99.4245 | 6.1932 | #NUM! | 9.4277e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 92.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 99.7745 | 6.1932 | #NUM! | 9.4485e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 94.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 100.1245 | 6.1932 | #NUM! | 9.4693e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 96.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 100.4745 | 6.1932 | #NUM! | 9.4901e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 99 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 100.8245 | 6.1932 | #NUM! | 9.5109e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 101.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 101.1745 | 6.1932 | #NUM! | 9.5317e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Section 4 | 168.75 |  | 2.25 | 103.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  | 168.75 |  | 5.19 | 101.5245 | 6.1932 | #NUM! | 9.5526e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 105.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 101.8745 | 6.1932 | #NUM! | 9.5734e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 108 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 102.2245 | 6.1932 | #NUM! | 9.5942e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 110.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 102.5745 | 6.1932 | #NUM! | 9.615e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 112.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 102.9245 | 6.1932 | #NUM! | 9.6358e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 114.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 103.2745 | 6.1932 | #NUM! | 9.6566e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 117 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 103.6245 | 6.1932 | #NUM! | 9.6774e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 119.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 103.9745 | 6.1932 | #NUM! | 9.6982e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 121.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 104.3245 | 6.1932 | #NUM! | 9.719e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 123.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 104.6745 | 6.1932 | #NUM! | 9.7399e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 126 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 105.0245 | 6.1932 | #NUM! | 9.7607e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 128.25 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 105.3745 | 6.1932 | #NUM! | 9.7815e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 130.5 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 105.7245 | 6.1932 | #NUM! | 9.8023e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 132.75 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 106.0745 | 6.1932 | #NUM! | 9.8231e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
|  |  | 2.25 | 135 | 5 | 11.25 |  | 0 | 0 | 5 | 11.25 |  |  |  | 5.19 | 106.4245 | 6.1932 | #NUM! | 9.8439e-06 | 0.533 | 8 | #NUM! | #NUM! | #NUM! | 225 | #NUM! | #NUM!
Far end | [19 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | #NUM! | #NUM!
Total dynamic heat = | 675 | W | [9 empty] | Total system heat = | 675 | W | [10 empty] | Pressure drop in pipe (Pa) = | #NUM!
[25 empty] | Pressure drop in pipe (bar) = | #NUM!
[22 empty] | Shield plus beam screen delta-T (K) = |  |  |  | 29.82
|  |  | Helium temperature for the supply end of the tube in K. |  |  |  |  | 85.5276 | K
|  |  | Helium pressure for the supply end of the tube in bar. |  |  |  |  | 19.0273 | bar
|  |  | This pressure and temperature will be used to find an initial helium density. | [10 empty] | Calculation of pressure drop for helium gas | [9 empty] | T. Peterson
[14 empty] | through a pipe with pressure drop and heat added | [9 empty] | 2000-01-22
[5 empty] | Enter the desired delta-T in K |  |  | 19 | K | Calc'd del-P | 1.7764 | bar
[5 empty] | Enter a linear heat flux (W/m) |  | Heat = | 6.25 | W/m per beam | [6 empty] | Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar
| Heat per |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 0.533 | cm | [14 empty] | f incl factor
| section in |  |  |  | Enter a total pipe length (m) |  | Length = | 135 | m |  |  |  | Total heat |  |  | Helium |  | Helium | Helium |  | Number | Overall avg |  | 4 for D
| Watts: |  | Bin | [7 empty] | Total heat |  | in each |  | Specific heat | temperature | mt | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| Qsect (W) |  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | section |  | (J/gK) | (K) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
|  |  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin) |  | Qsect (W)
Supply end |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 5.19 | 85.5276 | 8.5564 | 0.010679 | 8.6013e-06 | 0.533 | 5 | 718.2343 | 47527.1104 | 0.021429 | 0 | 0 | 19.0273
Section 1 | 210.9375 |  | 2.25 | 2.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  | 210.9375 |  | 5.19 | 85.8442 | 8.5564 | 0.010639 | 8.6201e-06 | 0.533 | 5 | 720.8936 | 47423.2898 | 0.021441 | 225 | 2502.1534 | 19.0023
|  |  | 2.25 | 4.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 86.1609 | 8.5564 | 0.010586 | 8.639e-06 | 0.533 | 5 | 724.5056 | 47319.9218 | 0.021452 | 225 | 2516.0625 | 18.9771
|  |  | 2.25 | 6.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 86.4776 | 8.5564 | 0.010533 | 8.6578e-06 | 0.533 | 5 | 728.1325 | 47217.0034 | 0.021464 | 225 | 2530.0348 | 18.9518
|  |  | 2.25 | 9 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 86.7942 | 8.5564 | 0.010481 | 8.6766e-06 | 0.533 | 5 | 731.7744 | 47114.5318 | 0.021476 | 225 | 2544.0707 | 18.9264
|  |  | 2.25 | 11.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 87.1109 | 8.5564 | 0.010429 | 8.6955e-06 | 0.533 | 5 | 735.4315 | 47012.504 | 0.021487 | 225 | 2558.1709 | 18.9008
|  |  | 2.25 | 13.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 87.4276 | 8.5564 | 0.010377 | 8.7143e-06 | 0.533 | 5 | 739.104 | 46910.9171 | 0.021499 | 225 | 2572.3362 | 18.8751
|  |  | 2.25 | 15.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 87.7442 | 8.5564 | 0.010326 | 8.7331e-06 | 0.533 | 5 | 742.7919 | 46809.7683 | 0.021511 | 225 | 2586.567 | 18.8492
|  |  | 2.25 | 18 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 88.0609 | 8.5564 | 0.010274 | 8.752e-06 | 0.533 | 5 | 746.4956 | 46709.0547 | 0.021522 | 225 | 2600.8642 | 18.8232
|  |  | 2.25 | 20.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 88.3776 | 8.5564 | 0.010223 | 8.7708e-06 | 0.533 | 5 | 750.2152 | 46608.7736 | 0.021534 | 225 | 2615.2283 | 18.7971
|  |  | 2.25 | 22.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 88.6942 | 8.5564 | 0.010173 | 8.7896e-06 | 0.533 | 5 | 753.9508 | 46508.9222 | 0.021545 | 225 | 2629.6601 | 18.7708
|  |  | 2.25 | 24.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 89.0109 | 8.5564 | 0.010122 | 8.8084e-06 | 0.533 | 5 | 757.7026 | 46409.4976 | 0.021557 | 225 | 2644.1602 | 18.7443
|  |  | 2.25 | 27 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 89.3276 | 8.5564 | 0.010072 | 8.8273e-06 | 0.533 | 5 | 761.4709 | 46310.4973 | 0.021568 | 225 | 2658.7294 | 18.7177
|  |  | 2.25 | 29.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 89.6442 | 8.5564 | 0.010022 | 8.8461e-06 | 0.533 | 5 | 765.2558 | 46211.9184 | 0.02158 | 225 | 2673.3683 | 18.691
|  |  | 2.25 | 31.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 89.9609 | 8.5564 | 0.0099729 | 8.8649e-06 | 0.533 | 5 | 769.0574 | 46113.7584 | 0.021591 | 225 | 2688.0778 | 18.6641
|  |  | 2.25 | 33.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 90.2776 | 8.5564 | 0.0099236 | 8.8838e-06 | 0.533 | 5 | 772.8761 | 46016.0144 | 0.021603 | 225 | 2702.8584 | 18.6371
Section 2 | 210.9375 |  | 2.25 | 36 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  | 210.9375 |  | 5.19 | 90.5942 | 8.5564 | 0.0098746 | 8.9026e-06 | 0.533 | 5 | 776.7119 | 45918.6839 | 0.021614 | 225 | 2717.7111 | 18.6099
|  |  | 2.25 | 38.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 90.9109 | 8.5564 | 0.0098258 | 8.9214e-06 | 0.533 | 5 | 780.5651 | 45821.7643 | 0.021626 | 225 | 2732.6364 | 18.5826
|  |  | 2.25 | 40.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 91.2276 | 8.5564 | 0.0097774 | 8.9403e-06 | 0.533 | 5 | 784.4359 | 45725.253 | 0.021637 | 225 | 2747.6353 | 18.5551
|  |  | 2.25 | 42.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 91.5442 | 8.5564 | 0.0097291 | 8.9591e-06 | 0.533 | 5 | 788.3244 | 45629.1474 | 0.021648 | 225 | 2762.7084 | 18.5275
|  |  | 2.25 | 45 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 91.8609 | 8.5564 | 0.0096812 | 8.9779e-06 | 0.533 | 5 | 792.2309 | 45533.4449 | 0.02166 | 225 | 2777.8567 | 18.4997
|  |  | 2.25 | 47.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 92.1776 | 8.5564 | 0.0096334 | 8.9967e-06 | 0.533 | 5 | 796.1556 | 45438.143 | 0.021671 | 225 | 2793.0807 | 18.4718
|  |  | 2.25 | 49.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 92.4942 | 8.5564 | 0.009586 | 9.0156e-06 | 0.533 | 5 | 800.0987 | 45343.2392 | 0.021682 | 225 | 2808.3815 | 18.4437
|  |  | 2.25 | 51.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 92.8109 | 8.5564 | 0.0095387 | 9.0344e-06 | 0.533 | 5 | 804.0604 | 45248.7311 | 0.021694 | 225 | 2823.7598 | 18.4155
|  |  | 2.25 | 54 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 93.1276 | 8.5564 | 0.0094917 | 9.0532e-06 | 0.533 | 5 | 808.041 | 45154.6161 | 0.021705 | 225 | 2839.2165 | 18.3871
|  |  | 2.25 | 56.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 93.4442 | 8.5564 | 0.009445 | 9.0721e-06 | 0.533 | 5 | 812.0405 | 45060.8917 | 0.021716 | 225 | 2854.7524 | 18.3585
|  |  | 2.25 | 58.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 93.7609 | 8.5564 | 0.0093985 | 9.0909e-06 | 0.533 | 5 | 816.0594 | 44967.5557 | 0.021728 | 225 | 2870.3684 | 18.3298
|  |  | 2.25 | 60.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 94.0776 | 8.5564 | 0.0093522 | 9.1097e-06 | 0.533 | 5 | 820.0978 | 44874.6055 | 0.021739 | 225 | 2886.0654 | 18.301
|  |  | 2.25 | 63 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 94.3942 | 8.5564 | 0.0093061 | 9.1286e-06 | 0.533 | 5 | 824.1559 | 44782.0388 | 0.02175 | 225 | 2901.8442 | 18.2719
|  |  | 2.25 | 65.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 94.7109 | 8.5564 | 0.0092603 | 9.1474e-06 | 0.533 | 5 | 828.234 | 44689.8532 | 0.021761 | 225 | 2917.7058 | 18.2428
|  |  | 2.25 | 67.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 95.0276 | 8.5564 | 0.0092147 | 9.1662e-06 | 0.533 | 5 | 832.3323 | 44598.0463 | 0.021772 | 225 | 2933.6511 | 18.2134
Section 3 | 210.9375 |  | 2.25 | 69.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  | 210.9375 |  | 5.19 | 95.3442 | 8.5564 | 0.0091693 | 9.1851e-06 | 0.533 | 5 | 836.451 | 44506.6159 | 0.021784 | 225 | 2949.681 | 18.1839
|  |  | 2.25 | 72 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 95.6609 | 8.5564 | 0.0091242 | 9.2039e-06 | 0.533 | 5 | 840.5905 | 44415.5595 | 0.021795 | 225 | 2965.7966 | 18.1543
|  |  | 2.25 | 74.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 95.9776 | 8.5564 | 0.0090793 | 9.2227e-06 | 0.533 | 5 | 844.7509 | 44324.8751 | 0.021806 | 225 | 2981.9987 | 18.1244
|  |  | 2.25 | 76.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 96.2942 | 8.5564 | 0.0090345 | 9.2415e-06 | 0.533 | 5 | 848.9325 | 44234.5601 | 0.021817 | 225 | 2998.2884 | 18.0945
|  |  | 2.25 | 78.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 96.6109 | 8.5564 | 0.00899 | 9.2604e-06 | 0.533 | 5 | 853.1355 | 44144.6125 | 0.021828 | 225 | 3014.6666 | 18.0643
|  |  | 2.25 | 81 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 96.9276 | 8.5564 | 0.0089457 | 9.2792e-06 | 0.533 | 5 | 857.3603 | 44055.0299 | 0.021839 | 225 | 3031.1344 | 18.034
|  |  | 2.25 | 83.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 97.2442 | 8.5564 | 0.0089016 | 9.298e-06 | 0.533 | 5 | 861.6071 | 43965.8101 | 0.02185 | 225 | 3047.6928 | 18.0035
|  |  | 2.25 | 85.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 97.5609 | 8.5564 | 0.0088577 | 9.3169e-06 | 0.533 | 5 | 865.8762 | 43876.9511 | 0.021861 | 225 | 3064.3428 | 17.9729
|  |  | 2.25 | 87.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 97.8776 | 8.5564 | 0.0088141 | 9.3357e-06 | 0.533 | 5 | 870.1678 | 43788.4504 | 0.021872 | 225 | 3081.0856 | 17.9421
|  |  | 2.25 | 90 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 98.1942 | 8.5564 | 0.0087706 | 9.3545e-06 | 0.533 | 5 | 874.4822 | 43700.3061 | 0.021883 | 225 | 3097.9222 | 17.9111
|  |  | 2.25 | 92.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 98.5109 | 8.5564 | 0.0087273 | 9.3734e-06 | 0.533 | 5 | 878.8197 | 43612.5159 | 0.021894 | 225 | 3114.8537 | 17.8799
|  |  | 2.25 | 94.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 98.8276 | 8.5564 | 0.0086842 | 9.3922e-06 | 0.533 | 5 | 883.1806 | 43525.0777 | 0.021905 | 225 | 3131.8813 | 17.8486
|  |  | 2.25 | 96.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 99.1442 | 8.5564 | 0.0086413 | 9.411e-06 | 0.533 | 5 | 887.5652 | 43437.9894 | 0.021916 | 225 | 3149.0061 | 17.8171
|  |  | 2.25 | 99 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 99.4609 | 8.5564 | 0.0085986 | 9.4298e-06 | 0.533 | 5 | 891.9737 | 43351.249 | 0.021927 | 225 | 3166.2291 | 17.7855
|  |  | 2.25 | 101.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 99.7776 | 8.5564 | 0.0085561 | 9.4487e-06 | 0.533 | 5 | 896.4066 | 43264.8543 | 0.021938 | 225 | 3183.5518 | 17.7536
Section 4 | 210.9375 |  | 2.25 | 103.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  | 210.9375 |  | 5.19 | 100.0942 | 8.5564 | 0.0085137 | 9.4675e-06 | 0.533 | 5 | 900.8641 | 43178.8032 | 0.021949 | 225 | 3200.9751 | 17.7216
|  |  | 2.25 | 105.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 100.4109 | 8.5564 | 0.0084716 | 9.4863e-06 | 0.533 | 5 | 905.3465 | 43093.0938 | 0.02196 | 225 | 3218.5004 | 17.6894
|  |  | 2.25 | 108 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 100.7276 | 8.5564 | 0.0084296 | 9.5052e-06 | 0.533 | 5 | 909.8541 | 43007.7239 | 0.021971 | 225 | 3236.1289 | 17.6571
|  |  | 2.25 | 110.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 101.0442 | 8.5564 | 0.0083878 | 9.524e-06 | 0.533 | 5 | 914.3873 | 42922.6917 | 0.021982 | 225 | 3253.8619 | 17.6245
|  |  | 2.25 | 112.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 101.3609 | 8.5564 | 0.0083462 | 9.5428e-06 | 0.533 | 5 | 918.9463 | 42837.995 | 0.021993 | 225 | 3271.7006 | 17.5918
|  |  | 2.25 | 114.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 101.6776 | 8.5564 | 0.0083048 | 9.5617e-06 | 0.533 | 5 | 923.5317 | 42753.6319 | 0.022004 | 225 | 3289.6463 | 17.5589
|  |  | 2.25 | 117 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 101.9942 | 8.5564 | 0.0082635 | 9.5805e-06 | 0.533 | 5 | 928.1435 | 42669.6004 | 0.022014 | 225 | 3307.7005 | 17.5259
|  |  | 2.25 | 119.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 102.3109 | 8.5564 | 0.0082224 | 9.5993e-06 | 0.533 | 5 | 932.7823 | 42585.8986 | 0.022025 | 225 | 3325.8644 | 17.4926
|  |  | 2.25 | 121.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 102.6276 | 8.5564 | 0.0081815 | 9.6181e-06 | 0.533 | 5 | 937.4484 | 42502.5245 | 0.022036 | 225 | 3344.1394 | 17.4592
|  |  | 2.25 | 123.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 102.9442 | 8.5564 | 0.0081407 | 9.637e-06 | 0.533 | 5 | 942.1421 | 42419.4763 | 0.022047 | 225 | 3362.527 | 17.4255
|  |  | 2.25 | 126 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 103.2609 | 8.5564 | 0.0081001 | 9.6558e-06 | 0.533 | 5 | 946.8639 | 42336.752 | 0.022058 | 225 | 3381.0285 | 17.3917
|  |  | 2.25 | 128.25 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 103.5776 | 8.5564 | 0.0080597 | 9.6746e-06 | 0.533 | 5 | 951.614 | 42254.3497 | 0.022068 | 225 | 3399.6455 | 17.3577
|  |  | 2.25 | 130.5 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 103.8942 | 8.5564 | 0.0080194 | 9.6935e-06 | 0.533 | 5 | 956.3928 | 42172.2675 | 0.022079 | 225 | 3418.3793 | 17.3235
|  |  | 2.25 | 132.75 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 104.2109 | 8.5564 | 0.0079793 | 9.7123e-06 | 0.533 | 5 | 961.2008 | 42090.5037 | 0.02209 | 225 | 3437.2316 | 17.2892
|  |  | 2.25 | 135 | 6.25 | 14.0625 |  | 0 | 0 | 6.25 | 14.0625 |  |  |  | 5.19 | 104.5276 | 8.5564 | 0.0079393 | 9.7311e-06 | 0.533 | 5 | 966.0384 | 42009.0562 | 0.0221 | 225 | 3456.2038 | 17.2546
Far end | [19 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | 370.4617 | 17.2509
Total dynamic heat = | 843.75 | W | [9 empty] | Total system heat = | 843.75 | W | [10 empty] | Pressure drop in pipe (Pa) = | 177641.8419
[25 empty] | Pressure drop in pipe (bar) = | 1.7764
[22 empty] | Shield plus beam screen delta-T (K) = |  |  |  | 26.98

## Return helium
| Helium pressure for the supply end of the pipe in bar. |  |  |  |  | #NUM! | bar
| This pressure and temperature will be used to find an initial helium density. | [8 empty] | Calculation of pressure drop for helium gas | [13 empty] | T. Peterson
[10 empty] | through a pipe with pressure drop and heat added | [13 empty] | 2000-01-02
Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar
|  |  | Linear heat flux (W/m) |  | Heat = | 2.2 | W/m T-line shield heat load
|  |  | Enter a pipe inner dia (cm) |  | Diameter = | 26.62 | cm |  |  |  |  | Shield plus | Shield plus | Joining | [9 empty] | f incl factor
|  |  | Total pipe length (m) |  | Length = | 9700 | m |  |  |  | Supply pipe | beam screen | beam screen | pipe helium | Combined |  |  | Helium | Helium |  | Number | Overall avg |  | 4 for D
| Bin | [7 empty] | Total heat | Specific heat | temperature | delta-T | exit temperature | temperature | temperature | mt | mTraceTube | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin | (J/gK) | (K) | (K) | (K) | (K) | (K) | (g/s) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
| (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin)
Turnaround end | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 5.19 | 76.6045 | 29.82 | 106.4245 | 76.6045 | 76.6045 | -750.7202 | 6.1932 | #NUM! | 8.0707e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 0 | #NUM! | #NUM!
| 270 | 270 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5995 | 29.82 | 106.4195 | 76.452 | 75.4294 | -725.9473 | 6.1932 | #NUM! | 8.0008e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 540 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5945 | 29.82 | 106.4145 | 75.2717 | 74.1714 | -701.1744 | 6.1932 | #NUM! | 7.926e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 810 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5893 | 29.82 | 106.4093 | 74.0082 | 72.8215 | -676.4015 | 6.1932 | #NUM! | 7.8458e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 1080 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.584 | 29.82 | 106.404 | 72.6523 | 71.3692 | -651.6286 | 6.1932 | #NUM! | 7.7594e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 1350 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5786 | 29.82 | 106.3986 | 71.1935 | 69.8022 | -626.8557 | 6.1932 | #NUM! | 7.6662e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 1620 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5731 | 29.82 | 106.3931 | 69.6197 | 68.1066 | -602.0828 | 6.1932 | #NUM! | 7.5654e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 1890 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5673 | 29.82 | 106.3873 | 67.9165 | 66.2657 | -577.3098 | 6.1932 | #NUM! | 7.4559e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 2160 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5614 | 29.82 | 106.3814 | 66.0674 | 64.26 | -552.5369 | 6.1932 | #NUM! | 7.3367e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 2430 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5554 | 29.82 | 106.3754 | 64.0528 | 62.0662 | -527.764 | 6.1932 | #NUM! | 7.2062e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 2700 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5492 | 29.82 | 106.3692 | 61.8494 | 59.6567 | -502.9911 | 6.1932 | #NUM! | 7.0629e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 2970 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5427 | 29.82 | 106.3627 | 59.4292 | 56.9979 | -478.2182 | 6.1932 | #NUM! | 6.9048e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 3240 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5361 | 29.82 | 106.3561 | 56.7586 | 54.0489 | -453.4453 | 6.1932 | #NUM! | 6.7295e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 3510 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5293 | 29.82 | 106.3493 | 53.7965 | 50.7595 | -428.6724 | 6.1932 | #NUM! | 6.5339e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 3780 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5222 | 29.82 | 106.3422 | 50.4925 | 47.067 | -403.8994 | 6.1932 | #NUM! | 6.3143e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 4050 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5149 | 29.82 | 106.3349 | 46.7837 | 42.8925 | -379.1265 | 6.1932 | #NUM! | 6.0661e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 4320 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5073 | 29.82 | 106.3273 | 42.5906 | 38.1347 | -354.3536 | 6.1932 | #NUM! | 5.7831e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 4590 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4994 | 29.82 | 106.3194 | 37.8118 | 32.6624 | -329.5807 | 6.1932 | #NUM! | 5.4577e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 4860 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4913 | 29.82 | 106.3113 | 32.3151 | 26.3012 | -304.8078 | 6.1932 | #NUM! | 5.0795e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 5130 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4828 | 29.82 | 106.3028 | 25.9257 | 18.8152 | -280.0349 | 6.1932 | #NUM! | 4.6343e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 5400 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4739 | 29.82 | 106.2939 | 18.4065 | 9.8771 | -255.262 | 6.1932 | #NUM! | 4.1028e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 5670 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4646 | 29.82 | 106.2846 | 9.4288 | -0.98127 | -230.489 | 6.1932 | #NUM! | 3.4571e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 5940 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.455 | 29.82 | 106.275 | -1.4778 | -14.4537 | -205.7161 | 6.1932 | #NUM! | 2.656e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 6210 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4448 | 29.82 | 106.2648 | -15.0101 | -31.6138 | -180.9432 | 6.1932 | #NUM! | 1.6356e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 6480 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4342 | 29.82 | 106.2542 | -32.2463 | -54.2163 | -156.1703 | 6.1932 | #NUM! | 2.9158e-07 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 6750 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4229 | 29.82 | 106.2429 | -54.9492 | -85.3394 | -131.3974 | 6.1932 | #NUM! | -1.5591e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 7020 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4111 | 29.82 | 106.2311 | -86.2105 | -130.9219 | -106.6245 | 6.1932 | #NUM! | -4.2696e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 7290 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.3985 | 29.82 | 106.2185 | -131.9953 | -204.0923 | -81.8515 | 6.1932 | #NUM! | -8.6206e-06 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 7560 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.3851 | 29.82 | 106.2051 | -205.4906 | -340.7709 | -57.0786 | 6.1932 | #NUM! | -1.6748e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 7830 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.3708 | 29.82 | 106.1908 | -342.776 | -687.0562 | -32.3057 | 6.1932 | #NUM! | -3.734e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 8100 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.3555 | 29.82 | 106.1755 | -690.5989 | -3310.9288 | -7.5328 | 6.1932 | #NUM! | -0.00019337 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 8370 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.3389 | 29.82 | 106.1589 | -3326.1225 | 1605.8412 | 17.2401 | 6.1932 | #NUM! | 9.9005e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 8640 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.321 | 29.82 | 106.141 | 1612.4799 | 724.2696 | 42.013 | 6.1932 | #NUM! | 4.6583e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 8910 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.3013 | 29.82 | 106.1213 | 726.9937 | 496.6935 | 66.7859 | 6.1932 | #NUM! | 3.3051e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 9180 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.2797 | 29.82 | 106.0997 | 498.4072 | 392.2613 | 91.5589 | 6.1932 | #NUM! | 2.6841e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 9450 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.2555 | 29.82 | 106.0755 | 393.5113 | 332.3017 | 116.3318 | 6.1932 | #NUM! | 2.3275e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 9720 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.2282 | 29.82 | 106.0482 | 333.2855 | 293.3908 | 141.1047 | 6.1932 | #NUM! | 2.0962e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 9990 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.1969 | 29.82 | 106.0169 | 294.2019 | 266.0975 | 165.8776 | 6.1932 | #NUM! | 1.9339e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 10260 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.16 | 29.82 | 105.98 | 266.7875 | 245.8923 | 190.6505 | 6.1932 | #NUM! | 1.8137e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 10530 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.1153 | 29.82 | 105.9353 | 246.4927 | 230.3291 | 215.4234 | 6.1932 | #NUM! | 1.7212e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 10800 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.0585 | 29.82 | 105.8785 | 230.8604 | 217.9702 | 240.1963 | 6.1932 | #NUM! | 1.6477e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 11070 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 75.9806 | 29.82 | 105.8006 | 218.4467 | 207.915 | 264.9693 | 6.1932 | #NUM! | 1.5879e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 11340 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 75.8568 | 29.82 | 105.6768 | 208.347 | 199.5687 | 289.7422 | 6.1932 | #NUM! | 1.5383e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 11610 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 75.555 | 29.82 | 105.375 | 199.9637 | 192.5134 | 314.5151 | 6.1932 | #NUM! | 1.4963e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 11880 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.2456 | 29.82 | 106.0656 | 192.8773 | 186.5388 | 339.288 | 6.1932 | #NUM! | 1.4608e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 12150 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4067 | 29.82 | 106.2267 | 186.8761 | 181.3882 | 364.0609 | 6.1932 | #NUM! | 1.4302e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 12420 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.4978 | 29.82 | 106.3178 | 181.7026 | 176.8998 | 388.8338 | 6.1932 | #NUM! | 1.4035e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 12690 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.5614 | 29.82 | 106.3814 | 177.1941 | 172.9528 | 413.6068 | 6.1932 | #NUM! | 1.38e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 12960 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.6101 | 29.82 | 106.4301 | 173.2295 | 169.4547 | 438.3797 | 6.1932 | #NUM! | 1.3592e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 13230 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.6497 | 29.82 | 106.4697 | 169.7157 | 166.3329 | 463.1526 | 6.1932 | #NUM! | 1.3406e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 13500 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.6831 | 29.82 | 106.5031 | 166.58 | 163.5297 | 487.9255 | 6.1932 | #NUM! | 1.324e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 13770 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.7118 | 29.82 | 106.5318 | 163.7643 | 160.9989 | 512.6984 | 6.1932 | #NUM! | 1.3089e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 14040 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.7371 | 29.82 | 106.5571 | 161.2221 | 158.7025 | 537.4713 | 6.1932 | #NUM! | 1.2953e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 14310 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.7597 | 29.82 | 106.5797 | 158.9155 | 156.6095 | 562.2442 | 6.1932 | #NUM! | 1.2828e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 14580 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.78 | 29.82 | 106.6 | 156.8131 | 154.694 | 587.0172 | 6.1932 | #NUM! | 1.2714e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 14850 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.7986 | 29.82 | 106.6186 | 154.889 | 152.9344 | 611.7901 | 6.1932 | #NUM! | 1.261e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 15120 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.8157 | 29.82 | 106.6357 | 153.1215 | 151.3124 | 636.563 | 6.1932 | #NUM! | 1.2513e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 15390 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.8315 | 29.82 | 106.6515 | 151.4922 | 149.8125 | 661.3359 | 6.1932 | #NUM! | 1.2424e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 15660 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.8462 | 29.82 | 106.6662 | 149.9856 | 148.4215 | 686.1088 | 6.1932 | #NUM! | 1.2341e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 15930 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.8599 | 29.82 | 106.6799 | 148.5883 | 147.1279 | 710.8817 | 6.1932 | #NUM! | 1.2264e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 16200 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.8728 | 29.82 | 106.6928 | 147.2889 | 145.9218 | 735.6546 | 6.1932 | #NUM! | 1.2193e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 16470 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.8849 | 29.82 | 106.7049 | 146.0774 | 144.7947 | 760.4276 | 6.1932 | #NUM! | 1.2126e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 16740 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.8964 | 29.82 | 106.7164 | 144.9452 | 143.7391 | 785.2005 | 6.1932 | #NUM! | 1.2063e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 17010 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9072 | 29.82 | 106.7272 | 143.8849 | 142.7484 | 809.9734 | 6.1932 | #NUM! | 1.2004e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 17280 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9176 | 29.82 | 106.7376 | 142.8897 | 141.8168 | 834.7463 | 6.1932 | #NUM! | 1.1948e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 17550 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9274 | 29.82 | 106.7474 | 141.9539 | 140.9392 | 859.5192 | 6.1932 | #NUM! | 1.1896e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 17820 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9369 | 29.82 | 106.7569 | 141.0724 | 140.111 | 884.2921 | 6.1932 | #NUM! | 1.1847e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 18090 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9459 | 29.82 | 106.7659 | 140.2405 | 139.3283 | 909.0651 | 6.1932 | #NUM! | 1.1801e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 18360 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9545 | 29.82 | 106.7745 | 139.4542 | 138.5872 | 933.838 | 6.1932 | #NUM! | 1.1756e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 18630 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9628 | 29.82 | 106.7828 | 138.7098 | 137.8847 | 958.6109 | 6.1932 | #NUM! | 1.1715e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 18900 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9708 | 29.82 | 106.7908 | 138.0041 | 137.2178 | 983.3838 | 6.1932 | #NUM! | 1.1675e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 19170 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9785 | 29.82 | 106.7985 | 137.3342 | 136.5838 | 1008.1567 | 6.1932 | #NUM! | 1.1637e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 19440 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9859 | 29.82 | 106.8059 | 136.6974 | 135.9805 | 1032.9296 | 6.1932 | #NUM! | 1.1601e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 19710 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 76.9931 | 29.82 | 106.8131 | 136.0913 | 135.4055 | 1057.7025 | 6.1932 | #NUM! | 1.1567e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
| 270 | 19980 | 2.2 | 594 |  | 0 | 0 | 2.2 | 594 | 5.19 | 77 | 29.82 | 106.82 | 135.5137 | 134.8571 | 1082.4755 | 6.1932 | #NUM! | 1.1535e-05 | 26.62 | 1 | #NUM! | #NUM! | #NUM! | 27000 | #NUM! | #NUM!
Refrigerator end
[20 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | #NUM! | #NUM!
[7 empty] | Total system heat = | 43956 | W
[25 empty] | Pressure drop in pipe (Pa) = | #NUM!
[25 empty] | Pressure drop in pipe (bar) = | #NUM!
| Helium pressure for the supply end of the pipe in bar. |  |  |  |  | 17.2509 | bar
| This pressure and temperature will be used to find an initial helium density. | [8 empty] | Calculation of pressure drop for helium gas | [13 empty] | T. Peterson
[10 empty] | through a pipe with pressure drop and heat added | [13 empty] | 2000-03-19
Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar
|  |  | Linear heat flux (W/m) |  | Heat = | 2.75 | W/m T-line shield heat load
|  |  | Enter a pipe inner dia (cm) |  | Diameter = | 16.27 | cm |  |  |  |  | Shield plus | Shield plus | Joining | [9 empty] | f incl factor
|  |  | Total pipe length (m) |  | Length = | 9700 | m |  |  |  | Supply pipe | beam screen | beam screen | pipe helium | Combined |  |  | Helium | Helium |  | Number | Overall avg |  | 4 for D
| Bin | [7 empty] | Total heat | Specific heat | temperature | delta-T | exit temperature | temperature | temperature | mt | mTraceTube | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin | (J/gK) | (K) | (K) | (K) | (K) | (K) | (g/s) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
| (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin)
Turnaround end | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 5.19 | 77.5476 | 26.98 | 104.5276 | 77.5476 | 77.5476 | 83.5425 | 8.5564 | 0.010678 | 8.1268e-06 | 16.27 | 1 | 37.6321 | 80447.2801 | 0.018787 | 0 | 0 | 17.2509
| 135 | 135 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5451 | 26.98 | 104.5251 | 78.4038 | 82.8448 | 100.6554 | 8.5564 | 0.010678 | 8.4418e-06 | 16.27 | 1 | 45.3406 | 93309.4449 | 0.018103 | 13500 | 16.4866 | 17.2507
| 135 | 270 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5427 | 26.98 | 104.5227 | 83.5555 | 86.6022 | 117.7682 | 8.5564 | 0.009995 | 8.6652e-06 | 16.27 | 1 | 56.6735 | 106358.3992 | 0.01752 | 13500 | 23.3348 | 17.2505
| 135 | 405 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5402 | 26.98 | 104.5202 | 87.2096 | 89.4059 | 134.8811 | 8.5564 | 0.0095612 | 8.8319e-06 | 16.27 | 1 | 67.8535 | 119513.8959 | 0.017017 | 13500 | 31.0783 | 17.2502
| 135 | 540 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5376 | 26.98 | 104.5176 | 89.9362 | 91.5779 | 151.994 | 8.5564 | 0.0092612 | 8.9611e-06 | 16.27 | 1 | 78.9392 | 132735.9369 | 0.016576 | 13500 | 39.6881 | 17.2498
| 135 | 675 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5351 | 26.98 | 104.5151 | 92.0485 | 93.3101 | 169.1068 | 8.5564 | 0.0090414 | 9.0641e-06 | 16.27 | 1 | 89.9626 | 146002.3509 | 0.016186 | 13500 | 49.1384 | 17.2493
| 135 | 810 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5324 | 26.98 | 104.5124 | 93.7331 | 94.7237 | 186.2197 | 8.5564 | 0.0088733 | 9.1481e-06 | 16.27 | 1 | 100.9431 | 159299.8584 | 0.015837 | 13500 | 59.4069 | 17.2487
| 135 | 945 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5298 | 26.98 | 104.5098 | 95.1078 | 95.8991 | 203.3326 | 8.5564 | 0.0087406 | 9.218e-06 | 16.27 | 1 | 111.893 | 172620.0207 | 0.015523 | 13500 | 70.4734 | 17.248
| 135 | 1080 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5271 | 26.98 | 104.5071 | 96.2509 | 96.8918 | 220.4454 | 8.5564 | 0.0086331 | 9.2771e-06 | 16.27 | 1 | 122.8205 | 185957.2187 | 0.015236 | 13500 | 82.3203 | 17.2472
| 135 | 1215 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5244 | 26.98 | 104.5044 | 97.2163 | 97.7413 | 237.5583 | 8.5564 | 0.0085442 | 9.3276e-06 | 16.27 | 1 | 133.7313 | 199307.5669 | 0.014975 | 13500 | 94.9315 | 17.2462
| 135 | 1350 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5216 | 26.98 | 104.5016 | 98.0424 | 98.4764 | 254.6712 | 8.5564 | 0.0084695 | 9.3713e-06 | 16.27 | 1 | 144.6298 | 212668.2925 | 0.014734 | 13500 | 108.2929 | 17.2452
| 135 | 1485 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5188 | 26.98 | 104.4988 | 98.7573 | 99.1188 | 271.784 | 8.5564 | 0.0084057 | 9.4095e-06 | 16.27 | 1 | 155.519 | 226037.3646 | 0.014511 | 13500 | 122.3913 | 17.2439
| 135 | 1620 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.516 | 26.98 | 104.496 | 99.382 | 99.685 | 288.8969 | 8.5564 | 0.0083507 | 9.4432e-06 | 16.27 | 1 | 166.4014 | 239413.2615 | 0.014304 | 13500 | 137.2148 | 17.2426
| 135 | 1755 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5131 | 26.98 | 104.4931 | 99.9326 | 100.1876 | 306.0098 | 8.5564 | 0.0083026 | 9.4731e-06 | 16.27 | 1 | 177.2791 | 252794.821 | 0.014111 | 13500 | 152.7527 | 17.241
| 135 | 1890 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5102 | 26.98 | 104.4902 | 100.4214 | 100.6368 | 323.1227 | 8.5564 | 0.0082602 | 9.4998e-06 | 16.27 | 1 | 188.1535 | 266181.1406 | 0.01393 | 13500 | 168.9949 | 17.2393
| 135 | 2025 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5072 | 26.98 | 104.4872 | 100.8582 | 101.0407 | 340.2355 | 8.5564 | 0.0082225 | 9.5238e-06 | 16.27 | 1 | 199.0262 | 279571.5086 | 0.01376 | 13500 | 185.9323 | 17.2375
| 135 | 2160 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5042 | 26.98 | 104.4842 | 101.251 | 101.4058 | 357.3484 | 8.5564 | 0.0081888 | 9.5455e-06 | 16.27 | 1 | 209.8982 | 292965.3571 | 0.0136 | 13500 | 203.5563 | 17.2354
| 135 | 2295 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.5011 | 26.98 | 104.4811 | 101.606 | 101.7374 | 374.4613 | 8.5564 | 0.0081583 | 9.5652e-06 | 16.27 | 1 | 220.7707 | 306362.2269 | 0.013449 | 13500 | 221.8593 | 17.2332
| 135 | 2430 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.498 | 26.98 | 104.478 | 101.9284 | 102.0398 | 391.5741 | 8.5564 | 0.0081307 | 9.5832e-06 | 16.27 | 1 | 231.6446 | 319761.7435 | 0.013305 | 13500 | 240.8339 | 17.2308
| 135 | 2565 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4948 | 26.98 | 104.4748 | 102.2225 | 102.3168 | 408.687 | 8.5564 | 0.0081055 | 9.5997e-06 | 16.27 | 1 | 242.5207 | 333163.5984 | 0.01317 | 13500 | 260.4734 | 17.2282
| 135 | 2700 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4916 | 26.98 | 104.4716 | 102.4919 | 102.5714 | 425.7999 | 8.5564 | 0.0080823 | 9.6148e-06 | 16.27 | 1 | 253.4 | 346567.5355 | 0.01304 | 13500 | 280.7716 | 17.2254
| 135 | 2835 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4883 | 26.98 | 104.4683 | 102.7394 | 102.8062 | 442.9127 | 8.5564 | 0.0080609 | 9.6288e-06 | 16.27 | 1 | 264.283 | 359973.3404 | 0.012917 | 13500 | 301.7227 | 17.2224
| 135 | 2970 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.485 | 26.98 | 104.465 | 102.9677 | 103.0234 | 460.0256 | 8.5564 | 0.0080411 | 9.6417e-06 | 16.27 | 1 | 275.1707 | 373380.8327 | 0.0128 | 13500 | 323.3213 | 17.2192
| 135 | 3105 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4816 | 26.98 | 104.4616 | 103.1789 | 103.2249 | 477.1385 | 8.5564 | 0.0080226 | 9.6537e-06 | 16.27 | 1 | 286.0637 | 386789.8595 | 0.012687 | 13500 | 345.5624 | 17.2157
| 135 | 3240 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4781 | 26.98 | 104.4581 | 103.3748 | 103.4123 | 494.2513 | 8.5564 | 0.0080054 | 9.6648e-06 | 16.27 | 1 | 296.9627 | 400200.2907 | 0.01258 | 13500 | 368.4415 | 17.212
| 135 | 3375 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4746 | 26.98 | 104.4546 | 103.5571 | 103.5871 | 511.3642 | 8.5564 | 0.0079891 | 9.6752e-06 | 16.27 | 1 | 307.8684 | 413612.0151 | 0.012476 | 13500 | 391.9542 | 17.2081
| 135 | 3510 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.471 | 26.98 | 104.451 | 103.727 | 103.7504 | 528.4771 | 8.5564 | 0.0079739 | 9.6849e-06 | 16.27 | 1 | 318.7816 | 427024.9372 | 0.012377 | 13500 | 416.0966 | 17.2039
| 135 | 3645 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4673 | 26.98 | 104.4473 | 103.8858 | 103.9034 | 545.59 | 8.5564 | 0.0079594 | 9.694e-06 | 16.27 | 1 | 329.7028 | 440438.9747 | 0.012282 | 13500 | 440.8651 | 17.1995
| 135 | 3780 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4636 | 26.98 | 104.4436 | 104.0345 | 104.047 | 562.7028 | 8.5564 | 0.0079456 | 9.7025e-06 | 16.27 | 1 | 340.6329 | 453854.0564 | 0.01219 | 13500 | 466.2563 | 17.1949
| 135 | 3915 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4598 | 26.98 | 104.4398 | 104.1741 | 104.1819 | 579.8157 | 8.5564 | 0.0079325 | 9.7106e-06 | 16.27 | 1 | 351.5724 | 467270.121 | 0.012102 | 13500 | 492.2671 | 17.1899
| 135 | 4050 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4559 | 26.98 | 104.4359 | 104.3053 | 104.309 | 596.9286 | 8.5564 | 0.00792 | 9.7181e-06 | 16.27 | 1 | 362.5221 | 480687.1151 | 0.012016 | 13500 | 518.8948 | 17.1847
| 135 | 4185 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4519 | 26.98 | 104.4319 | 104.4289 | 104.429 | 614.0414 | 8.5564 | 0.0079079 | 9.7253e-06 | 16.27 | 1 | 373.4827 | 494104.9925 | 0.011934 | 13500 | 546.1368 | 17.1793
| 135 | 4320 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4479 | 26.98 | 104.4279 | 104.5454 | 104.5423 | 631.1543 | 8.5564 | 0.0078963 | 9.732e-06 | 16.27 | 1 | 384.4549 | 507523.7132 | 0.011854 | 13500 | 573.9908 | 17.1735
| 135 | 4455 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4437 | 26.98 | 104.4237 | 104.6556 | 104.6495 | 648.2672 | 8.5564 | 0.0078851 | 9.7384e-06 | 16.27 | 1 | 395.4395 | 520943.2424 | 0.011777 | 13500 | 602.4548 | 17.1675
| 135 | 4590 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4395 | 26.98 | 104.4195 | 104.7598 | 104.7511 | 665.38 | 8.5564 | 0.0078743 | 9.7444e-06 | 16.27 | 1 | 406.437 | 534363.5503 | 0.011702 | 13500 | 631.527 | 17.1612
| 135 | 4725 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4352 | 26.98 | 104.4152 | 104.8586 | 104.8475 | 682.4929 | 8.5564 | 0.0078638 | 9.7501e-06 | 16.27 | 1 | 417.4484 | 547784.611 | 0.01163 | 13500 | 661.2057 | 17.1546
| 135 | 4860 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4308 | 26.98 | 104.4108 | 104.9523 | 104.939 | 699.6058 | 8.5564 | 0.0078535 | 9.7556e-06 | 16.27 | 1 | 428.4744 | 561206.4025 | 0.01156 | 13500 | 691.4897 | 17.1477
| 135 | 4995 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4262 | 26.98 | 104.4062 | 105.0413 | 105.0261 | 716.7186 | 8.5564 | 0.0078435 | 9.7608e-06 | 16.27 | 1 | 439.5157 | 574628.9062 | 0.011492 | 13500 | 722.3777 | 17.1405
| 135 | 5130 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4216 | 26.98 | 104.4016 | 105.1259 | 105.109 | 733.8315 | 8.5564 | 0.0078337 | 9.7657e-06 | 16.27 | 1 | 450.5731 | 588052.1063 | 0.011426 | 13500 | 753.8688 | 17.1329
| 135 | 5265 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4168 | 26.98 | 104.3968 | 105.2065 | 105.188 | 750.9444 | 8.5564 | 0.0078241 | 9.7704e-06 | 16.27 | 1 | 461.6475 | 601475.99 | 0.011361 | 13500 | 785.9624 | 17.1251
| 135 | 5400 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4119 | 26.98 | 104.3919 | 105.2833 | 105.2634 | 768.0572 | 8.5564 | 0.0078146 | 9.7749e-06 | 16.27 | 1 | 472.7396 | 614900.5468 | 0.011299 | 13500 | 818.6579 | 17.1169
| 135 | 5535 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4069 | 26.98 | 104.3869 | 105.3566 | 105.3354 | 785.1701 | 8.5564 | 0.0078053 | 9.7792e-06 | 16.27 | 1 | 483.8503 | 628325.7687 | 0.011238 | 13500 | 851.9549 | 17.1084
| 135 | 5670 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.4018 | 26.98 | 104.3818 | 105.4265 | 105.4042 | 802.283 | 8.5564 | 0.0077961 | 9.7833e-06 | 16.27 | 1 | 494.9804 | 641751.6499 | 0.011179 | 13500 | 885.8535 | 17.0995
| 135 | 5805 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3965 | 26.98 | 104.3765 | 105.4934 | 105.4701 | 819.3959 | 8.5564 | 0.0077869 | 9.7872e-06 | 16.27 | 1 | 506.1308 | 655178.1864 | 0.011121 | 13500 | 920.3536 | 17.0903
| 135 | 5940 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.391 | 26.98 | 104.371 | 105.5574 | 105.5331 | 836.5087 | 8.5564 | 0.0077779 | 9.7909e-06 | 16.27 | 1 | 517.3023 | 668605.3765 | 0.011065 | 13500 | 955.4556 | 17.0807
| 135 | 6075 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3854 | 26.98 | 104.3654 | 105.6186 | 105.5935 | 853.6216 | 8.5564 | 0.0077689 | 9.7945e-06 | 16.27 | 1 | 528.496 | 682033.2201 | 0.01101 | 13500 | 991.16 | 17.0708
| 135 | 6210 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3796 | 26.98 | 104.3596 | 105.6773 | 105.6514 | 870.7345 | 8.5564 | 0.0077599 | 9.798e-06 | 16.27 | 1 | 539.7126 | 695461.7193 | 0.010956 | 13500 | 1027.4674 | 17.0606
| 135 | 6345 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3737 | 26.98 | 104.3537 | 105.7336 | 105.707 | 887.8473 | 8.5564 | 0.007751 | 9.8013e-06 | 16.27 | 1 | 550.9531 | 708890.8776 | 0.010904 | 13500 | 1064.3787 | 17.0499
| 135 | 6480 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3675 | 26.98 | 104.3475 | 105.7875 | 105.7603 | 904.9602 | 8.5564 | 0.0077421 | 9.8044e-06 | 16.27 | 1 | 562.2185 | 722320.7005 | 0.010853 | 13500 | 1101.895 | 17.0389
| 135 | 6615 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3612 | 26.98 | 104.3412 | 105.8393 | 105.8115 | 922.0731 | 8.5564 | 0.0077332 | 9.8075e-06 | 16.27 | 1 | 573.5098 | 735751.1955 | 0.010803 | 13500 | 1140.0176 | 17.0275
| 135 | 6750 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3546 | 26.98 | 104.3346 | 105.8891 | 105.8608 | 939.1859 | 8.5564 | 0.0077243 | 9.8104e-06 | 16.27 | 1 | 584.828 | 749182.3716 | 0.010754 | 13500 | 1178.7478 | 17.0157
| 135 | 6885 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3478 | 26.98 | 104.3278 | 105.9369 | 105.9082 | 956.2988 | 8.5564 | 0.0077154 | 9.8132e-06 | 16.27 | 1 | 596.174 | 762614.24 | 0.010707 | 13500 | 1218.0875 | 17.0035
| 135 | 7020 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3407 | 26.98 | 104.3207 | 105.983 | 105.9537 | 973.4117 | 8.5564 | 0.0077064 | 9.8159e-06 | 16.27 | 1 | 607.5489 | 776046.8138 | 0.01066 | 13500 | 1258.0384 | 16.9909
| 135 | 7155 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3334 | 26.98 | 104.3134 | 106.0272 | 105.9976 | 990.5245 | 8.5564 | 0.0076974 | 9.8185e-06 | 16.27 | 1 | 618.9538 | 789480.1082 | 0.010615 | 13500 | 1298.6026 | 16.978
| 135 | 7290 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3257 | 26.98 | 104.3057 | 106.0698 | 106.0399 | 1007.6374 | 8.5564 | 0.0076883 | 9.8211e-06 | 16.27 | 1 | 630.3898 | 802914.1408 | 0.01057 | 13500 | 1339.7823 | 16.9646
| 135 | 7425 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3178 | 26.98 | 104.2978 | 106.1108 | 106.0806 | 1024.7503 | 8.5564 | 0.0076792 | 9.8235e-06 | 16.27 | 1 | 641.8578 | 816348.9315 | 0.010526 | 13500 | 1381.5799 | 16.9507
| 135 | 7560 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3095 | 26.98 | 104.2895 | 106.1504 | 106.1198 | 1041.8631 | 8.5564 | 0.00767 | 9.8258e-06 | 16.27 | 1 | 653.3592 | 829784.503 | 0.010483 | 13500 | 1423.9982 | 16.9365
| 135 | 7695 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.3008 | 26.98 | 104.2808 | 106.1885 | 106.1576 | 1058.976 | 8.5564 | 0.0076607 | 9.8281e-06 | 16.27 | 1 | 664.895 | 843220.881 | 0.010441 | 13500 | 1467.0399 | 16.9218
| 135 | 7830 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2917 | 26.98 | 104.2717 | 106.2252 | 106.1941 | 1076.0889 | 8.5564 | 0.0076513 | 9.8302e-06 | 16.27 | 1 | 676.4664 | 856658.0943 | 0.0104 | 13500 | 1510.7082 | 16.9067
| 135 | 7965 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2821 | 26.98 | 104.2621 | 106.2606 | 106.2293 | 1093.2018 | 8.5564 | 0.0076419 | 9.8323e-06 | 16.27 | 1 | 688.0746 | 870096.1756 | 0.01036 | 13500 | 1555.0061 | 16.8912
| 135 | 8100 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2721 | 26.98 | 104.2521 | 106.2947 | 106.2633 | 1110.3146 | 8.5564 | 0.0076323 | 9.8343e-06 | 16.27 | 1 | 699.7208 | 883535.1619 | 0.01032 | 13500 | 1599.9373 | 16.8752
| 135 | 8235 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2614 | 26.98 | 104.2414 | 106.3277 | 106.296 | 1127.4275 | 8.5564 | 0.0076227 | 9.8363e-06 | 16.27 | 1 | 711.4063 | 896975.0949 | 0.010281 | 13500 | 1645.5053 | 16.8587
| 135 | 8370 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2502 | 26.98 | 104.2302 | 106.3595 | 106.3276 | 1144.5404 | 8.5564 | 0.0076129 | 9.8382e-06 | 16.27 | 1 | 723.1322 | 910416.0222 | 0.010243 | 13500 | 1691.714 | 16.8418
| 135 | 8505 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2382 | 26.98 | 104.2182 | 106.3901 | 106.3581 | 1161.6532 | 8.5564 | 0.007603 | 9.84e-06 | 16.27 | 1 | 734.9 | 923857.9979 | 0.010206 | 13500 | 1738.5674 | 16.8244
| 135 | 8640 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2254 | 26.98 | 104.2054 | 106.4197 | 106.3876 | 1178.7661 | 8.5564 | 0.0075929 | 9.8417e-06 | 16.27 | 1 | 746.7109 | 937301.0842 | 0.010169 | 13500 | 1786.0699 | 16.8066
| 135 | 8775 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.2118 | 26.98 | 104.1918 | 106.4482 | 106.416 | 1195.879 | 8.5564 | 0.0075828 | 9.8434e-06 | 16.27 | 1 | 758.5663 | 950745.353 | 0.010133 | 13500 | 1834.2259 | 16.7882
| 135 | 8910 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.197 | 26.98 | 104.177 | 106.4758 | 106.4433 | 1212.9918 | 8.5564 | 0.0075725 | 9.845e-06 | 16.27 | 1 | 770.4675 | 964190.888 | 0.010097 | 13500 | 1883.04 | 16.7694
| 135 | 9045 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.181 | 26.98 | 104.161 | 106.5023 | 106.4697 | 1230.1047 | 8.5564 | 0.0075621 | 9.8466e-06 | 16.27 | 1 | 782.4159 | 977637.7876 | 0.010062 | 13500 | 1932.5171 | 16.7501
| 135 | 9180 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.1636 | 26.98 | 104.1436 | 106.5279 | 106.4952 | 1247.2176 | 8.5564 | 0.0075515 | 9.8481e-06 | 16.27 | 1 | 794.4129 | 991086.1693 | 0.010028 | 13500 | 1982.6623 | 16.7302
| 135 | 9315 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.1443 | 26.98 | 104.1243 | 106.5525 | 106.5197 | 1264.3304 | 8.5564 | 0.0075407 | 9.8496e-06 | 16.27 | 1 | 806.4599 | 1004536.1747 | 0.0099941 | 13500 | 2033.4807 | 16.7099
| 135 | 9450 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.1229 | 26.98 | 104.1029 | 106.5762 | 106.5432 | 1281.4433 | 8.5564 | 0.0075298 | 9.851e-06 | 16.27 | 1 | 818.5583 | 1017987.9783 | 0.009961 | 13500 | 2084.9778 | 16.689
| 135 | 9585 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.0988 | 26.98 | 104.0788 | 106.599 | 106.5658 | 1298.5562 | 8.5564 | 0.0075188 | 9.8523e-06 | 16.27 | 1 | 830.7095 | 1031441.7996 | 0.0099283 | 13500 | 2137.159 | 16.6677
| 135 | 9720 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.0712 | 26.98 | 104.0512 | 106.6209 | 106.5875 | 1315.669 | 8.5564 | 0.0075076 | 9.8536e-06 | 16.27 | 1 | 842.915 | 1044897.9227 | 0.0098962 | 13500 | 2190.0298 | 16.6458
| 135 | 9855 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77.0389 | 26.98 | 104.0189 | 106.6419 | 106.6082 | 1332.7819 | 8.5564 | 0.0074962 | 9.8548e-06 | 16.27 | 1 | 855.1759 | 1058356.7293 | 0.0098646 | 13500 | 2243.5958 | 16.6233
| 135 | 9990 | 2.75 | 371.25 |  | 0 | 0 | 2.75 | 371.25 | 5.19 | 77 | 26.98 | 103.98 | 106.6618 | 106.6278 | 1349.8948 | 8.5564 | 0.0074846 | 9.856e-06 | 16.27 | 1 | 867.4938 | 1071818.7587 | 0.0098335 | 13500 | 2297.8624 | 16.6004
Refrigerator end
[20 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | 186.8427 | 16.5985
[7 empty] | Total system heat = | 27472.5 | W
[25 empty] | Pressure drop in pipe (Pa) = | 65241.2993
[25 empty] | Pressure drop in pipe (bar) = | 0.65241

## Comparison
Tom Peterson
2001-03-20
| Comparison of helium gas and nitrogen cooling |  |  | System summary
of long systems with large heat flux
|  |  | Helium gas | Helium gas | Thermal shield | Helium | Helium gas
| Two-phase nitrogen | Subcooled nitrogen | (scratch work) | supply |  | trace tube | return
(one beam)
Heat flux (W/m) | 40 | 40 | 6.8 | 0.125 | 5.25 | 6.25 | 2.75
Total length (m) | 20000 | 20000 | 135 | 9700 | 135 | 135 | 9700
Total heat (kW) | 800 | 800 | 0.918 | 1.2488 | 708.75 | 60.625 | 27.4725
Number of parallel tubes | 1 | 1 | 1 | 1 | 1 | 5 | 1
Inlet pressure (bar) | 5 | 8 | 19.5 | 20 | 19.1063 | 19.0273 | 17.2509
Exit pressure (bar) | 2.8007 | 5.5868 | 19.4938 | 19.1063 | 19.0273 | 17.2509 | 16.5985
Pressure drop (bar) | 2.1993 | 2.4132 | 0.0062416 | 0.89369 | 0.078988 | 1.7764 | 0.65241
Inlet temperature (K) | 95.2557 | 70 | 65 | 77 | 77.5476 | 85.5276 | 77.5476
Exit temperature (K) | 87.6041 | 89.8791 | 75 | 77.5476 | 85.5276 | 104.5276 | 106.6278
Temperature change (K) | -7.6516 | 19.8791 | 10 | 0.54758 | 7.98 | 19 | 29.0803
Subcooling left (K) |  | 6.9153
Mass flow (g/sec) | 4822.4604 | 19611.4001 | 17.6879 | 1349.8948 | 17.1129 | 8.5564 | 1349.8948
Pipe inner diameter (cm) | 21.35 | 21.35 | 3.8 | 13.58 | 2.29 | 0.533 | 16.27
Pipe ID (inches) | 8.4055 | 8.4055 | 1.4961 | 5.3465 | 0.90157 | 0.20984 | 6.4055

## Comments
Comments
Tom Peterson
2001-01-05
I include an additional factor of 1.5 in the friction factor for 2-phase nitrogen flow
based on the data and analysis in "Pressure Drop Considerations in the Transfer
of Fluids," by Timmerhaus and Sugden, Advances Vol 10, p 367.
The data, however, are for 2-phase freon and hydrogen, and the authors also
warn that adjustments should be a function of vapor fraction. So the 2-phase
nitrogen pressure drop estimates need refinement based on real LN2 data.
I include an additional factor of 1.3 for liquid nitrogen flow based on a
recommendation for single phase flow in the same paper.
I do not include any additional fudge factors for friction factor or pressure drop for
helium gas since my experience has been that the standard correlations work
well for single phase helium, especially for gas.

## Draft He Calcs
|  |  | Enter a helium temperature for the supply end of the pipe in K. |  |  |  |  | 65 | K
|  |  | Enter a helium pressure for the supply end of the pipe in bar. |  |  |  |  | 19.5 | bar
|  |  | This pressure and temperature will be used to find an initial helium density. | [10 empty] | Calculation of pressure drop for helium gas | [9 empty] | T. Peterson
[14 empty] | through a pipe with pressure drop and heat added | [9 empty] | 2000-01-02
[5 empty] | Enter the desired delta-T in K |  |  | 10 | K
[5 empty] | Enter a linear heat flux (W/m) |  | Heat = | 6.8 | W/m | [6 empty] | Pipe pressure drop details using properties of helium from 50 to 150 K and 1 to 20 bar
| Heat per |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 3.8 | cm | [14 empty] | f incl factor
| section in |  |  |  | Enter a total pipe length (m) |  | Length = | 135 | m |  |  |  | Total heat |  |  | Helium |  | Helium | Helium |  | Number | Overall avg |  | 4 for D
| Watts: |  | Bin | [7 empty] | Total heat |  | in each |  | Specific heat | temperature | mt | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| Qsect (W) |  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | section |  | (J/gK) | (K) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
|  |  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin) |  | Qsect (W)
Supply end |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 5.19 | 65 | 17.6879 | 0.0144 | 7.3807e-06 | 3.8 | 1 | 108.3069 | 80298.4224 | 0.018796 | 0 | 0 | 19.5
Section 1 | 229.5 |  | 2.25 | 2.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  | 229.5 |  | 5.19 | 65.1667 | 17.6879 | 0.014363 | 7.3906e-06 | 3.8 | 1 | 108.5846 | 80190.7432 | 0.018802 | 225 | 9.4267 | 19.4999
|  |  | 2.25 | 4.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 65.3333 | 17.6879 | 0.014326 | 7.4005e-06 | 3.8 | 1 | 108.8628 | 80083.3523 | 0.018808 | 225 | 9.4541 | 19.4998
|  |  | 2.25 | 6.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 65.5 | 17.6879 | 0.01429 | 7.4104e-06 | 3.8 | 1 | 109.1411 | 79976.2488 | 0.018815 | 225 | 9.4814 | 19.4997
|  |  | 2.25 | 9 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 65.6667 | 17.6879 | 0.014254 | 7.4203e-06 | 3.8 | 1 | 109.4193 | 79869.4313 | 0.018821 | 225 | 9.5087 | 19.4996
|  |  | 2.25 | 11.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 65.8333 | 17.6879 | 0.014217 | 7.4302e-06 | 3.8 | 1 | 109.6976 | 79762.8988 | 0.018827 | 225 | 9.5361 | 19.4995
|  |  | 2.25 | 13.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 66 | 17.6879 | 0.014181 | 7.4401e-06 | 3.8 | 1 | 109.9758 | 79656.6501 | 0.018833 | 225 | 9.5635 | 19.4994
|  |  | 2.25 | 15.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 66.1667 | 17.6879 | 0.014146 | 7.45e-06 | 3.8 | 1 | 110.2541 | 79550.6841 | 0.01884 | 225 | 9.5909 | 19.4993
|  |  | 2.25 | 18 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 66.3333 | 17.6879 | 0.01411 | 7.4599e-06 | 3.8 | 1 | 110.5324 | 79444.9996 | 0.018846 | 225 | 9.6183 | 19.4992
|  |  | 2.25 | 20.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 66.5 | 17.6879 | 0.014075 | 7.4699e-06 | 3.8 | 1 | 110.8106 | 79339.5956 | 0.018852 | 225 | 9.6457 | 19.4991
|  |  | 2.25 | 22.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 66.6667 | 17.6879 | 0.014039 | 7.4798e-06 | 3.8 | 1 | 111.0889 | 79234.4709 | 0.018859 | 225 | 9.6731 | 19.499
|  |  | 2.25 | 24.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 66.8333 | 17.6879 | 0.014004 | 7.4897e-06 | 3.8 | 1 | 111.3672 | 79129.6244 | 0.018865 | 225 | 9.7006 | 19.4989
|  |  | 2.25 | 27 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 67 | 17.6879 | 0.013969 | 7.4996e-06 | 3.8 | 1 | 111.6454 | 79025.055 | 0.018871 | 225 | 9.728 | 19.4989
|  |  | 2.25 | 29.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 67.1667 | 17.6879 | 0.013935 | 7.5095e-06 | 3.8 | 1 | 111.9237 | 78920.7616 | 0.018877 | 225 | 9.7555 | 19.4988
|  |  | 2.25 | 31.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 67.3333 | 17.6879 | 0.0139 | 7.5194e-06 | 3.8 | 1 | 112.202 | 78816.7432 | 0.018883 | 225 | 9.783 | 19.4987
|  |  | 2.25 | 33.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 67.5 | 17.6879 | 0.013866 | 7.5293e-06 | 3.8 | 1 | 112.4803 | 78712.9985 | 0.01889 | 225 | 9.8104 | 19.4986
Section 2 | 229.5 |  | 2.25 | 36 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  | 229.5 |  | 5.19 | 67.6667 | 17.6879 | 0.013831 | 7.5392e-06 | 3.8 | 1 | 112.7586 | 78609.5267 | 0.018896 | 225 | 9.838 | 19.4985
|  |  | 2.25 | 38.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 67.8333 | 17.6879 | 0.013797 | 7.5491e-06 | 3.8 | 1 | 113.0369 | 78506.3265 | 0.018902 | 225 | 9.8655 | 19.4984
|  |  | 2.25 | 40.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 68 | 17.6879 | 0.013764 | 7.5591e-06 | 3.8 | 1 | 113.3152 | 78403.3969 | 0.018908 | 225 | 9.893 | 19.4983
|  |  | 2.25 | 42.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 68.1667 | 17.6879 | 0.01373 | 7.569e-06 | 3.8 | 1 | 113.5935 | 78300.7369 | 0.018915 | 225 | 9.9206 | 19.4982
|  |  | 2.25 | 45 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 68.3333 | 17.6879 | 0.013696 | 7.5789e-06 | 3.8 | 1 | 113.8718 | 78198.3453 | 0.018921 | 225 | 9.9481 | 19.4981
|  |  | 2.25 | 47.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 68.5 | 17.6879 | 0.013663 | 7.5888e-06 | 3.8 | 1 | 114.1502 | 78096.2212 | 0.018927 | 225 | 9.9757 | 19.498
|  |  | 2.25 | 49.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 68.6667 | 17.6879 | 0.01363 | 7.5987e-06 | 3.8 | 1 | 114.4285 | 77994.3635 | 0.018933 | 225 | 10.0033 | 19.4979
|  |  | 2.25 | 51.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 68.8333 | 17.6879 | 0.013597 | 7.6086e-06 | 3.8 | 1 | 114.7068 | 77892.7712 | 0.018939 | 225 | 10.0309 | 19.4978
|  |  | 2.25 | 54 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 69 | 17.6879 | 0.013564 | 7.6185e-06 | 3.8 | 1 | 114.9851 | 77791.4431 | 0.018945 | 225 | 10.0585 | 19.4977
|  |  | 2.25 | 56.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 69.1667 | 17.6879 | 0.013531 | 7.6284e-06 | 3.8 | 1 | 115.2635 | 77690.3784 | 0.018952 | 225 | 10.0861 | 19.4976
|  |  | 2.25 | 58.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 69.3333 | 17.6879 | 0.013498 | 7.6383e-06 | 3.8 | 1 | 115.5418 | 77589.5759 | 0.018958 | 225 | 10.1138 | 19.4975
|  |  | 2.25 | 60.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 69.5 | 17.6879 | 0.013466 | 7.6482e-06 | 3.8 | 1 | 115.8202 | 77489.0346 | 0.018964 | 225 | 10.1414 | 19.4974
|  |  | 2.25 | 63 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 69.6667 | 17.6879 | 0.013434 | 7.6582e-06 | 3.8 | 1 | 116.0985 | 77388.7536 | 0.01897 | 225 | 10.1691 | 19.4973
|  |  | 2.25 | 65.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 69.8333 | 17.6879 | 0.013401 | 7.6681e-06 | 3.8 | 1 | 116.3769 | 77288.7318 | 0.018976 | 225 | 10.1967 | 19.4972
|  |  | 2.25 | 67.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 70 | 17.6879 | 0.013369 | 7.678e-06 | 3.8 | 1 | 116.6552 | 77188.9682 | 0.018982 | 225 | 10.2244 | 19.4971
Section 3 | 229.5 |  | 2.25 | 69.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  | 229.5 |  | 5.19 | 70.1667 | 17.6879 | 0.013338 | 7.6879e-06 | 3.8 | 1 | 116.9336 | 77089.4618 | 0.018988 | 225 | 10.2521 | 19.497
|  |  | 2.25 | 72 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 70.3333 | 17.6879 | 0.013306 | 7.6978e-06 | 3.8 | 1 | 117.212 | 76990.2117 | 0.018994 | 225 | 10.2799 | 19.4968
|  |  | 2.25 | 74.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 70.5 | 17.6879 | 0.013274 | 7.7077e-06 | 3.8 | 1 | 117.4903 | 76891.2168 | 0.019001 | 225 | 10.3076 | 19.4967
|  |  | 2.25 | 76.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 70.6667 | 17.6879 | 0.013243 | 7.7176e-06 | 3.8 | 1 | 117.7687 | 76792.4761 | 0.019007 | 225 | 10.3353 | 19.4966
|  |  | 2.25 | 78.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 70.8333 | 17.6879 | 0.013212 | 7.7275e-06 | 3.8 | 1 | 118.0471 | 76693.9887 | 0.019013 | 225 | 10.3631 | 19.4965
|  |  | 2.25 | 81 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 71 | 17.6879 | 0.013181 | 7.7374e-06 | 3.8 | 1 | 118.3255 | 76595.7536 | 0.019019 | 225 | 10.3909 | 19.4964
|  |  | 2.25 | 83.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 71.1667 | 17.6879 | 0.01315 | 7.7474e-06 | 3.8 | 1 | 118.6039 | 76497.7698 | 0.019025 | 225 | 10.4186 | 19.4963
|  |  | 2.25 | 85.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 71.3333 | 17.6879 | 0.013119 | 7.7573e-06 | 3.8 | 1 | 118.8823 | 76400.0364 | 0.019031 | 225 | 10.4464 | 19.4962
|  |  | 2.25 | 87.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 71.5 | 17.6879 | 0.013088 | 7.7672e-06 | 3.8 | 1 | 119.1607 | 76302.5524 | 0.019037 | 225 | 10.4742 | 19.4961
|  |  | 2.25 | 90 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 71.6667 | 17.6879 | 0.013058 | 7.7771e-06 | 3.8 | 1 | 119.4391 | 76205.3169 | 0.019043 | 225 | 10.5021 | 19.496
|  |  | 2.25 | 92.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 71.8333 | 17.6879 | 0.013027 | 7.787e-06 | 3.8 | 1 | 119.7175 | 76108.3289 | 0.019049 | 225 | 10.5299 | 19.4959
|  |  | 2.25 | 94.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 72 | 17.6879 | 0.012997 | 7.7969e-06 | 3.8 | 1 | 119.9959 | 76011.5874 | 0.019055 | 225 | 10.5577 | 19.4958
|  |  | 2.25 | 96.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 72.1667 | 17.6879 | 0.012967 | 7.8068e-06 | 3.8 | 1 | 120.2743 | 75915.0916 | 0.019061 | 225 | 10.5856 | 19.4957
|  |  | 2.25 | 99 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 72.3333 | 17.6879 | 0.012937 | 7.8167e-06 | 3.8 | 1 | 120.5527 | 75818.8404 | 0.019067 | 225 | 10.6135 | 19.4956
|  |  | 2.25 | 101.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 72.5 | 17.6879 | 0.012907 | 7.8266e-06 | 3.8 | 1 | 120.8312 | 75722.8331 | 0.019073 | 225 | 10.6413 | 19.4955
Section 4 | 229.5 |  | 2.25 | 103.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  | 229.5 |  | 5.19 | 72.6667 | 17.6879 | 0.012878 | 7.8366e-06 | 3.8 | 1 | 121.1096 | 75627.0685 | 0.01908 | 225 | 10.6692 | 19.4954
|  |  | 2.25 | 105.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 72.8333 | 17.6879 | 0.012848 | 7.8465e-06 | 3.8 | 1 | 121.388 | 75531.5459 | 0.019086 | 225 | 10.6971 | 19.4953
|  |  | 2.25 | 108 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 73 | 17.6879 | 0.012819 | 7.8564e-06 | 3.8 | 1 | 121.6665 | 75436.2642 | 0.019092 | 225 | 10.7251 | 19.4952
|  |  | 2.25 | 110.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 73.1667 | 17.6879 | 0.01279 | 7.8663e-06 | 3.8 | 1 | 121.9449 | 75341.2227 | 0.019098 | 225 | 10.753 | 19.4951
|  |  | 2.25 | 112.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 73.3333 | 17.6879 | 0.01276 | 7.8762e-06 | 3.8 | 1 | 122.2234 | 75246.4203 | 0.019104 | 225 | 10.7809 | 19.4949
|  |  | 2.25 | 114.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 73.5 | 17.6879 | 0.012731 | 7.8861e-06 | 3.8 | 1 | 122.5018 | 75151.8562 | 0.01911 | 225 | 10.8089 | 19.4948
|  |  | 2.25 | 117 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 73.6667 | 17.6879 | 0.012703 | 7.896e-06 | 3.8 | 1 | 122.7803 | 75057.5295 | 0.019116 | 225 | 10.8369 | 19.4947
|  |  | 2.25 | 119.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 73.8333 | 17.6879 | 0.012674 | 7.9059e-06 | 3.8 | 1 | 123.0588 | 74963.4393 | 0.019122 | 225 | 10.8649 | 19.4946
|  |  | 2.25 | 121.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 74 | 17.6879 | 0.012645 | 7.9158e-06 | 3.8 | 1 | 123.3372 | 74869.5847 | 0.019128 | 225 | 10.8929 | 19.4945
|  |  | 2.25 | 123.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 74.1667 | 17.6879 | 0.012617 | 7.9257e-06 | 3.8 | 1 | 123.6157 | 74775.9648 | 0.019134 | 225 | 10.9209 | 19.4944
|  |  | 2.25 | 126 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 74.3333 | 17.6879 | 0.012588 | 7.9357e-06 | 3.8 | 1 | 123.8942 | 74682.5788 | 0.01914 | 225 | 10.9489 | 19.4943
|  |  | 2.25 | 128.25 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 74.5 | 17.6879 | 0.01256 | 7.9456e-06 | 3.8 | 1 | 124.1727 | 74589.4257 | 0.019146 | 225 | 10.9769 | 19.4942
|  |  | 2.25 | 130.5 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 74.6667 | 17.6879 | 0.012532 | 7.9555e-06 | 3.8 | 1 | 124.4512 | 74496.5047 | 0.019151 | 225 | 11.005 | 19.4941
|  |  | 2.25 | 132.75 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 74.8333 | 17.6879 | 0.012504 | 7.9654e-06 | 3.8 | 1 | 124.7297 | 74403.815 | 0.019157 | 225 | 11.033 | 19.494
|  |  | 2.25 | 135 | 6.8 | 15.3 |  | 0 | 0 | 6.8 | 15.3 |  |  |  | 5.19 | 75 | 17.6879 | 0.012476 | 7.9753e-06 | 3.8 | 1 | 125.0082 | 74311.3556 | 0.019163 | 225 | 11.0611 | 19.4939
Far end | [19 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | 9.7483 | 19.4938
Total dynamic heat = | 918 | W | [9 empty] | Total system heat = | 918 | W | [10 empty] | Pressure drop in pipe (Pa) = | 624.162
[25 empty] | Pressure drop in pipe (bar) = | 0.0062416

## 2-phase N2
|  |  | Enter a saturated vapor pressure for the supply end of the pipe. | [11 empty] | Calculation of pressure drop for nitrogen | [15 empty] | T. Peterson
|  |  | This pressure will be used to find an initial vapor density. | [5 empty] | 5 | bar |  |  |  |  | through a pipe with boiling 2-phase flow | [15 empty] | 2000-12-28
[5 empty] | Enter a linear heat flux (W/m) |  | Heat = | 40 | W/m | [7 empty] | Pipe pressure drop details using properties of saturated nitrogen from 1 to 20 bar and a homogeneous flow model | [13 empty] | f incl factors
| Heat per |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 21.35 | cm | [21 empty] | 4 for D
| section in |  |  |  | Enter a total pipe length (m) |  | Length = | 20000 | m |  |  |  |  | Total heat | Enter | [7 empty] | Overall avg. |  |  |  |  | Number | Overall avg |  | and 1.5 for 2ph
| Watts: |  | Bin | [8 empty] | Total heat |  | in each | vapor mass | Latent heat | ml | mv | mt |  | Vapor density | Liquid density | density | Vapor viscosity | Liquid viscosity | Avg viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P
| Qsect (W) |  | size |  | Q in | Q in |  | Qstatic | Qstatic |  | Total heat | in each bin |  | section | fraction @ inlet | (J/g) | (g/s) | (g/s) | (g/s) |  | (g/cm3) | (g/cm3) | (g/cm3) | (Pa s) | (Pa s) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar)
|  |  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) |  | (W/m) | (W per bin) |  | Qsect (W) | X |  |  |  |  | X |  |  |  | 1 Pa s=10 g/cm s
Supply end |  |  | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  |  | 0.05 | 174.6215 | 4581.3373 | 241.123 | 4822.4604 | 0.05 | 0.020435 | 0.73125 | 0.26696 | 6.5551e-06 | 8.969e-05 | 5.4886e-05 | 21.35 | 1 | 50.4592 | 523990.6652 | 0.01764 | 0 | 0 | 5
Section 1 | 200000 |  | 333.3333 | 333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  | 200000 | 0.05 | 174.6215 | 4504.9817 | 317.4786 | 4822.4604 | 0.065833 | 0.020435 | 0.73125 | 0.22227 | 6.519e-06 | 8.969e-05 | 4.8747e-05 | 21.35 | 1 | 60.6046 | 589975.5214 | 0.017125 | 33333.3333 | 100.3363 | 4.999
|  |  | 333.3333 | 666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.6257 | 4428.6279 | 393.8324 | 4822.4604 | 0.081666 | 0.020431 | 0.73127 | 0.19037 | 6.5189e-06 | 8.9697e-05 | 4.3925e-05 | 21.35 | 1 | 70.7599 | 654735.2826 | 0.016684 | 33333.3333 | 133.2385 | 4.9977
|  |  | 333.3333 | 1000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.6313 | 4352.2766 | 470.1838 | 4822.4604 | 0.097499 | 0.020425 | 0.73128 | 0.16646 | 6.5186e-06 | 8.9706e-05 | 3.9972e-05 | 21.35 | 1 | 80.925 | 719494.8342 | 0.016296 | 33333.3333 | 170.1589 | 4.996
|  |  | 333.3333 | 1333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.6384 | 4275.9284 | 546.532 | 4822.4604 | 0.11333 | 0.020418 | 0.7313 | 0.14786 | 6.5183e-06 | 8.9718e-05 | 3.6671e-05 | 21.35 | 1 | 91.1017 | 784255.7846 | 0.015948 | 33333.3333 | 210.9715 | 4.9939
|  |  | 333.3333 | 1666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.6473 | 4199.5841 | 622.8763 | 4822.4604 | 0.12916 | 0.020408 | 0.73133 | 0.13299 | 6.5178e-06 | 8.9733e-05 | 3.3874e-05 | 21.35 | 1 | 101.293 | 849020.0897 | 0.015635 | 33333.3333 | 255.5736 | 4.9913
|  |  | 333.3333 | 2000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.658 | 4123.2444 | 699.216 | 4822.4604 | 0.14499 | 0.020397 | 0.73136 | 0.12081 | 6.5173e-06 | 8.9751e-05 | 3.1473e-05 | 21.35 | 1 | 111.5025 | 913790.0387 | 0.01535 | 33333.3333 | 303.8808 | 4.9883
|  |  | 333.3333 | 2333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.6708 | 4046.9103 | 775.55 | 4822.4604 | 0.16082 | 0.020384 | 0.73139 | 0.11066 | 6.5167e-06 | 8.9772e-05 | 2.9389e-05 | 21.35 | 1 | 121.7341 | 978568.2434 | 0.01509 | 33333.3333 | 355.8236 | 4.9847
|  |  | 333.3333 | 2666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.6857 | 3970.5828 | 851.8776 | 4822.4604 | 0.17665 | 0.020368 | 0.73143 | 0.10206 | 6.516e-06 | 8.9797e-05 | 2.7564e-05 | 21.35 | 1 | 131.9918 | 1043357.6294 | 0.01485 | 33333.3333 | 411.3461 | 4.9806
|  |  | 333.3333 | 3000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.703 | 3894.2628 | 928.1976 | 4822.4604 | 0.19247 | 0.02035 | 0.73148 | 0.094676 | 6.5152e-06 | 8.9826e-05 | 2.5952e-05 | 21.35 | 1 | 142.2801 | 1108161.43 | 0.014628 | 33333.3333 | 470.4036 | 4.9759
|  |  | 333.3333 | 3333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.7227 | 3817.9514 | 1004.509 | 4822.4604 | 0.2083 | 0.020329 | 0.73153 | 0.088271 | 6.5143e-06 | 8.9859e-05 | 2.4518e-05 | 21.35 | 1 | 152.6039 | 1172983.1815 | 0.014421 | 33333.3333 | 532.9622 | 4.9706
|  |  | 333.3333 | 3666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.7451 | 3741.6498 | 1080.8106 | 4822.4604 | 0.22412 | 0.020305 | 0.73159 | 0.082657 | 6.5133e-06 | 8.9896e-05 | 2.3234e-05 | 21.35 | 1 | 162.9685 | 1237826.7207 | 0.014229 | 33333.3333 | 598.9977 | 4.9646
|  |  | 333.3333 | 4000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.7703 | 3665.3591 | 1157.1012 | 4822.4604 | 0.23994 | 0.020278 | 0.73166 | 0.077694 | 6.5121e-06 | 8.9938e-05 | 2.2077e-05 | 21.35 | 1 | 173.3793 | 1302696.1829 | 0.014048 | 33333.3333 | 668.4951 | 4.9579
|  |  | 333.3333 | 4333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.7983 | 3589.0808 | 1233.3796 | 4822.4604 | 0.25576 | 0.020249 | 0.73174 | 0.073272 | 6.5108e-06 | 8.9985e-05 | 2.1029e-05 | 21.35 | 1 | 183.8424 | 1367596.0023 | 0.013878 | 33333.3333 | 741.4485 | 4.9505
|  |  | 333.3333 | 4666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.8294 | 3512.816 | 1309.6444 | 4822.4604 | 0.27157 | 0.020216 | 0.73183 | 0.069305 | 6.5093e-06 | 9.0038e-05 | 2.0076e-05 | 21.35 | 1 | 194.364 | 1432530.9132 | 0.013718 | 33333.3333 | 817.8605 | 4.9423
|  |  | 333.3333 | 5000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.8638 | 3436.5661 | 1385.8942 | 4822.4604 | 0.28738 | 0.02018 | 0.73192 | 0.065725 | 6.5077e-06 | 9.0095e-05 | 1.9205e-05 | 21.35 | 1 | 204.9509 | 1497505.9526 | 0.013567 | 33333.3333 | 897.742 | 4.9333
Section 2 | 200000 |  | 333.3333 | 5333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  | 200000 | 0.05 | 174.9015 | 3360.3327 | 1462.1277 | 4822.4604 | 0.30319 | 0.02014 | 0.73202 | 0.062476 | 6.506e-06 | 9.0159e-05 | 1.8406e-05 | 21.35 | 1 | 215.6103 | 1562526.4645 | 0.013424 | 33333.3333 | 981.1129 | 4.9235
|  |  | 333.3333 | 5666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.9426 | 3284.1173 | 1538.3431 | 4822.4604 | 0.319 | 0.020096 | 0.73214 | 0.059512 | 6.504e-06 | 9.0228e-05 | 1.767e-05 | 21.35 | 1 | 226.35 | 1627598.1051 | 0.013287 | 33333.3333 | 1068.0012 | 4.9128
|  |  | 333.3333 | 6000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 174.9875 | 3207.9213 | 1614.539 | 4822.4604 | 0.3348 | 0.020049 | 0.73226 | 0.056795 | 6.5019e-06 | 9.0304e-05 | 1.699e-05 | 21.35 | 1 | 237.1779 | 1692726.8497 | 0.013158 | 33333.3333 | 1158.4442 | 4.9012
|  |  | 333.3333 | 6333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.0361 | 3131.7466 | 1690.7138 | 4822.4604 | 0.35059 | 0.019998 | 0.73239 | 0.054294 | 6.4997e-06 | 9.0387e-05 | 1.636e-05 | 21.35 | 1 | 248.103 | 1757919.0008 | 0.013034 | 33333.3333 | 1252.4878 | 4.8887
|  |  | 333.3333 | 6666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.0887 | 3055.5947 | 1766.8657 | 4822.4604 | 0.36638 | 0.019942 | 0.73254 | 0.051983 | 6.4972e-06 | 9.0476e-05 | 1.5774e-05 | 21.35 | 1 | 259.1343 | 1823181.1984 | 0.012916 | 33333.3333 | 1350.1874 | 4.8752
|  |  | 333.3333 | 7000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.1454 | 2979.4674 | 1842.9929 | 4822.4604 | 0.38217 | 0.019882 | 0.73269 | 0.049839 | 6.4945e-06 | 9.0573e-05 | 1.5229e-05 | 21.35 | 1 | 270.2818 | 1888520.4311 | 0.012803 | 33333.3333 | 1451.6084 | 4.8607
|  |  | 333.3333 | 7333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.2063 | 2903.3667 | 1919.0937 | 4822.4604 | 0.39795 | 0.019818 | 0.73286 | 0.047843 | 6.4917e-06 | 9.0677e-05 | 1.4719e-05 | 21.35 | 1 | 281.5561 | 1953944.0497 | 0.012694 | 33333.3333 | 1556.8262 | 4.8451
|  |  | 333.3333 | 7666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.2716 | 2827.2943 | 1995.1661 | 4822.4604 | 0.41372 | 0.019749 | 0.73304 | 0.045979 | 6.4886e-06 | 9.0789e-05 | 1.4241e-05 | 21.35 | 1 | 292.9685 | 2019459.782 | 0.01259 | 33333.3333 | 1665.9274 | 4.8285
|  |  | 333.3333 | 8000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.3416 | 2751.2522 | 2071.2082 | 4822.4604 | 0.42949 | 0.019675 | 0.73323 | 0.044234 | 6.4854e-06 | 9.0909e-05 | 1.3793e-05 | 21.35 | 1 | 304.5309 | 2085075.7504 | 0.01249 | 33333.3333 | 1779.0099 | 4.8107
|  |  | 333.3333 | 8333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.4162 | 2675.2425 | 2147.2178 | 4822.4604 | 0.44525 | 0.019596 | 0.73344 | 0.042594 | 6.4819e-06 | 9.1038e-05 | 1.3372e-05 | 21.35 | 1 | 316.2565 | 2150800.4914 | 0.012393 | 33333.3333 | 1896.1844 | 4.7917
|  |  | 333.3333 | 8666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.4958 | 2599.2673 | 2223.1931 | 4822.4604 | 0.46101 | 0.019512 | 0.73366 | 0.041049 | 6.4781e-06 | 9.1176e-05 | 1.2974e-05 | 21.35 | 1 | 328.1591 | 2216642.9773 | 0.0123 | 33333.3333 | 2017.5747 | 4.7715
|  |  | 333.3333 | 9000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.5805 | 2523.3287 | 2299.1316 | 4822.4604 | 0.47675 | 0.019423 | 0.73389 | 0.03959 | 6.4742e-06 | 9.1323e-05 | 1.2599e-05 | 21.35 | 1 | 340.2537 | 2282612.6415 | 0.01221 | 33333.3333 | 2143.3193 | 4.7501
|  |  | 333.3333 | 9333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.6705 | 2447.4291 | 2375.0313 | 4822.4604 | 0.49249 | 0.019328 | 0.73414 | 0.038208 | 6.47e-06 | 9.148e-05 | 1.2245e-05 | 21.35 | 1 | 352.5564 | 2348719.4059 | 0.012123 | 33333.3333 | 2273.5724 | 4.7274
|  |  | 333.3333 | 9666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.7659 | 2371.5706 | 2450.8898 | 4822.4604 | 0.50822 | 0.019227 | 0.7344 | 0.036897 | 6.4655e-06 | 9.1648e-05 | 1.1909e-05 | 21.35 | 1 | 365.0847 | 2414973.7119 | 0.012039 | 33333.3333 | 2408.5054 | 4.7033
|  |  | 333.3333 | 10000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 175.867 | 2295.7558 | 2526.7046 | 4822.4604 | 0.52395 | 0.01912 | 0.73468 | 0.03565 | 6.4608e-06 | 9.1826e-05 | 1.159e-05 | 21.35 | 1 | 377.8573 | 2481386.5561 | 0.011958 | 33333.3333 | 2548.3086 | 4.6778
Section 3 | 200000 |  | 333.3333 | 10333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  | 200000 | 0.05 | 175.974 | 2219.987 | 2602.4734 | 4822.4604 | 0.53966 | 0.019007 | 0.73497 | 0.034461 | 6.4558e-06 | 9.2016e-05 | 1.1287e-05 | 21.35 | 1 | 390.8948 | 2547969.5289 | 0.011879 | 33333.3333 | 2693.193 | 4.6509
|  |  | 333.3333 | 10666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 176.0871 | 2144.2669 | 2678.1935 | 4822.4604 | 0.55536 | 0.018888 | 0.73528 | 0.033325 | 6.4505e-06 | 9.2218e-05 | 1.0999e-05 | 21.35 | 1 | 404.2194 | 2614734.859 | 0.011802 | 33333.3333 | 2843.3928 | 4.6224
|  |  | 333.3333 | 11000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 176.2064 | 2068.5981 | 2753.8623 | 4822.4604 | 0.57105 | 0.018762 | 0.73561 | 0.032237 | 6.4449e-06 | 9.2432e-05 | 1.0724e-05 | 21.35 | 1 | 417.8553 | 2681695.463 | 0.011728 | 33333.3333 | 2999.1677 | 4.5924
|  |  | 333.3333 | 11333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 176.3323 | 1992.9833 | 2829.4771 | 4822.4604 | 0.58673 | 0.018629 | 0.73596 | 0.031194 | 6.439e-06 | 9.2659e-05 | 1.0462e-05 | 21.35 | 1 | 431.829 | 2748865.0008 | 0.011656 | 33333.3333 | 3160.8057 | 4.5608
|  |  | 333.3333 | 11666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 176.465 | 1917.4253 | 2905.0351 | 4822.4604 | 0.6024 | 0.018489 | 0.73632 | 0.030191 | 6.4328e-06 | 9.29e-05 | 1.0212e-05 | 21.35 | 1 | 446.1695 | 2816257.9391 | 0.011585 | 33333.3333 | 3328.6271 | 4.5275
|  |  | 333.3333 | 12000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 176.6047 | 1841.9271 | 2980.5332 | 4822.4604 | 0.61805 | 0.018341 | 0.73671 | 0.029226 | 6.4263e-06 | 9.3156e-05 | 9.9725e-06 | 21.35 | 1 | 460.9089 | 2883889.6227 | 0.011517 | 33333.3333 | 3502.9877 | 4.4925
|  |  | 333.3333 | 12333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 176.7518 | 1766.4918 | 3055.9686 | 4822.4604 | 0.63369 | 0.018186 | 0.73711 | 0.028294 | 6.4194e-06 | 9.3427e-05 | 9.7431e-06 | 21.35 | 1 | 476.0821 | 2951776.3547 | 0.01145 | 33333.3333 | 3684.2842 | 4.4557
|  |  | 333.3333 | 12666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 176.9064 | 1691.1224 | 3131.338 | 4822.4604 | 0.64932 | 0.018022 | 0.73753 | 0.027394 | 6.4121e-06 | 9.3715e-05 | 9.5232e-06 | 21.35 | 1 | 491.7283 | 3019935.4887 | 0.011385 | 33333.3333 | 3872.9594 | 4.4169
|  |  | 333.3333 | 13000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 177.069 | 1615.8222 | 3206.6382 | 4822.4604 | 0.66494 | 0.017851 | 0.73798 | 0.026522 | 6.4045e-06 | 9.402e-05 | 9.3121e-06 | 21.35 | 1 | 507.8905 | 3088385.5335 | 0.011321 | 33333.3333 | 4069.5085 | 4.3762
|  |  | 333.3333 | 13333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 177.2398 | 1540.5945 | 3281.8659 | 4822.4604 | 0.68054 | 0.01767 | 0.73845 | 0.025677 | 6.3966e-06 | 9.4343e-05 | 9.1093e-06 | 21.35 | 1 | 524.617 | 3157146.2726 | 0.011259 | 33333.3333 | 4274.4869 | 4.3335
|  |  | 333.3333 | 13666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 177.4193 | 1465.443 | 3357.0174 | 4822.4604 | 0.69612 | 0.017481 | 0.73894 | 0.024855 | 6.3882e-06 | 9.4686e-05 | 8.9142e-06 | 21.35 | 1 | 541.9615 | 3226238.9022 | 0.011198 | 33333.3333 | 4488.5194 | 4.2886
|  |  | 333.3333 | 14000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 177.6077 | 1390.3711 | 3432.0892 | 4822.4604 | 0.71169 | 0.017282 | 0.73946 | 0.024055 | 6.3793e-06 | 9.5049e-05 | 8.7264e-06 | 21.35 | 1 | 559.9846 | 3295686.1894 | 0.011139 | 33333.3333 | 4712.3109 | 4.2415
|  |  | 333.3333 | 14333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 177.8055 | 1315.3828 | 3507.0776 | 4822.4604 | 0.72724 | 0.017073 | 0.74001 | 0.023275 | 6.3701e-06 | 9.5435e-05 | 8.5454e-06 | 21.35 | 1 | 578.7543 | 3365512.6565 | 0.011081 | 33333.3333 | 4946.6597 | 4.192
|  |  | 333.3333 | 14666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 178.0131 | 1240.482 | 3581.9784 | 4822.4604 | 0.74277 | 0.016854 | 0.74058 | 0.022513 | 6.3604e-06 | 9.5845e-05 | 8.3707e-06 | 21.35 | 1 | 598.3481 | 3435744.7949 | 0.011024 | 33333.3333 | 5192.4736 | 4.1401
|  |  | 333.3333 | 15000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 178.2311 | 1165.6727 | 3656.7877 | 4822.4604 | 0.75828 | 0.016623 | 0.74118 | 0.021767 | 6.3502e-06 | 9.628e-05 | 8.202e-06 | 21.35 | 1 | 618.8538 | 3506411.3158 | 0.010968 | 33333.3333 | 5450.7888 | 4.0856
Section 4 | 200000 |  | 333.3333 | 15333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  | 200000 | 0.05 | 178.4599 | 1090.9594 | 3731.501 | 4822.4604 | 0.77378 | 0.016382 | 0.7418 | 0.021035 | 6.3395e-06 | 9.6743e-05 | 8.0389e-06 | 21.35 | 1 | 640.3722 | 3577543.445 | 0.010913 | 33333.3333 | 5722.7945 | 4.0284
|  |  | 333.3333 | 15666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 178.7001 | 1016.3465 | 3806.1139 | 4822.4604 | 0.78925 | 0.016128 | 0.74246 | 0.020317 | 6.3282e-06 | 9.7235e-05 | 7.8811e-06 | 21.35 | 1 | 663.0194 | 3649175.2727 | 0.010859 | 33333.3333 | 6009.8618 | 3.9683
|  |  | 333.3333 | 16000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 178.9524 | 941.8388 | 3880.6216 | 4822.4604 | 0.8047 | 0.015862 | 0.74316 | 0.01961 | 6.3164e-06 | 9.776e-05 | 7.7283e-06 | 21.35 | 1 | 686.9296 | 3721344.1703 | 0.010806 | 33333.3333 | 6313.5816 | 3.9051
|  |  | 333.3333 | 16333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 179.2174 | 867.4413 | 3955.0191 | 4822.4604 | 0.82012 | 0.015582 | 0.74389 | 0.018912 | 6.304e-06 | 9.832e-05 | 7.5801e-06 | 21.35 | 1 | 712.2597 | 3794091.2913 | 0.010754 | 33333.3333 | 6635.8106 | 3.8388
|  |  | 333.3333 | 16666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 179.496 | 793.1592 | 4029.3012 | 4822.4604 | 0.83553 | 0.015288 | 0.74465 | 0.018223 | 6.291e-06 | 9.8919e-05 | 7.4363e-06 | 21.35 | 1 | 739.1939 | 3867462.178 | 0.010702 | 33333.3333 | 6978.7316 | 3.769
|  |  | 333.3333 | 17000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 179.7889 | 718.9981 | 4103.4622 | 4822.4604 | 0.85091 | 0.014978 | 0.74546 | 0.017541 | 6.2773e-06 | 9.9559e-05 | 7.2966e-06 | 21.35 | 1 | 767.9505 | 3941507.5027 | 0.010652 | 33333.3333 | 7344.9301 | 3.6955
|  |  | 333.3333 | 17333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 180.0972 | 644.9641 | 4177.4963 | 4822.4604 | 0.86626 | 0.014653 | 0.7463 | 0.016864 | 6.2629e-06 | 0.00010025 | 7.1607e-06 | 21.35 | 1 | 798.7901 | 4016283.9832 | 0.010602 | 33333.3333 | 7737.4953 | 3.6182
|  |  | 333.3333 | 17666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 180.422 | 571.0633 | 4251.3971 | 4822.4604 | 0.88158 | 0.01431 | 0.7472 | 0.01619 | 6.2477e-06 | 0.00010099 | 7.0285e-06 | 21.35 | 1 | 832.0274 | 4091855.5231 | 0.010552 | 33333.3333 | 8160.1528 | 3.5366
|  |  | 333.3333 | 18000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 180.7646 | 497.3025 | 4325.1579 | 4822.4604 | 0.89688 | 0.013948 | 0.74814 | 0.015518 | 6.2316e-06 | 0.00010178 | 6.8996e-06 | 21.35 | 1 | 868.0462 | 4168294.6518 | 0.010504 | 33333.3333 | 8617.4441 | 3.4504
|  |  | 333.3333 | 18333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 181.1263 | 423.689 | 4398.7713 | 4822.4604 | 0.91214 | 0.013566 | 0.74913 | 0.014846 | 6.2147e-06 | 0.00010264 | 6.7738e-06 | 21.35 | 1 | 907.3204 | 4245684.3653 | 0.010455 | 33333.3333 | 9114.9717 | 3.3592
|  |  | 333.3333 | 18666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 181.5089 | 350.2308 | 4472.2296 | 4822.4604 | 0.92738 | 0.013162 | 0.75018 | 0.014173 | 6.1968e-06 | 0.00010358 | 6.6509e-06 | 21.35 | 1 | 950.4432 | 4324120.5144 | 0.010408 | 33333.3333 | 9659.7399 | 3.2626
|  |  | 333.3333 | 19000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 181.9144 | 276.9362 | 4545.5241 | 4822.4604 | 0.94257 | 0.012733 | 0.7513 | 0.013495 | 6.1778e-06 | 0.0001046 | 6.5307e-06 | 21.35 | 1 | 998.1684 | 4403714.9551 | 0.01036 | 33333.3333 | 10260.6418 | 3.16
|  |  | 333.3333 | 19333.3333 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 182.3451 | 203.8148 | 4618.6456 | 4822.4604 | 0.95774 | 0.012278 | 0.75248 | 0.012811 | 6.1577e-06 | 0.00010571 | 6.4129e-06 | 21.35 | 1 | 1051.4714 | 4484599.7819 | 0.010313 | 33333.3333 | 10929.168 | 3.0507
|  |  | 333.3333 | 19666.6667 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 182.8039 | 130.8769 | 4691.5835 | 4822.4604 | 0.97286 | 0.011794 | 0.75374 | 0.012118 | 6.1362e-06 | 0.00010694 | 6.2973e-06 | 21.35 | 1 | 1111.6402 | 4566933.1402 | 0.010266 | 33333.3333 | 11680.4719 | 2.9339
|  |  | 333.3333 | 20000 | 40 | 13333.3333 |  | 0 | 0 |  | 40 | 13333.3333 |  |  | 0.05 | 183.2942 | 58.1341 | 4764.3263 | 4822.4604 | 0.98795 | 0.011276 | 0.75509 | 0.011412 | 6.1133e-06 | 0.00010831 | 6.1836e-06 | 21.35 | 1 | 1180.4171 | 4650907.4049 | 0.01022 | 33333.3333 | 12535.0199 | 2.8086
Far end | [26 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | 785.5989 | 2.8007
Total dynamic heat = | 800000 | W | [10 empty] | Total system heat = | 800000 | W | [16 empty] | Pressure drop in pipe (Pa) = | 219926.8888
[32 empty] | Pressure drop in pipe (bar) = | 2.1993
[28 empty] | The nitrogen temperatures through the pipe are |  |  |  | 95.2557 | K at start to | 87.6041 | K at exit

## Subcooled N2
|  |  | Enter a nitrogen temperature for the supply end of the pipe in K. |  |  |  |  | 70 | K
|  |  | Enter a nitrogen pressure for the supply end of the pipe in bar. |  |  |  |  | 8 | bar
[14 empty] | Calculation of pressure drop for subcooled nitrogen | [9 empty] | T. Peterson
[14 empty] | through a pipe with pressure drop and heat added | [9 empty] | 2000-01-02
[5 empty] | Enter the desired delta-T in K |  |  | 20 | K
[5 empty] | Enter a linear heat flux (W/m) |  | Heat = | 40 | W/m | [6 empty] | Pipe pressure drop details using properties of nitrogen from 70 to 100 K and 5 to 20 bar | [7 empty] | f incl factor
| Heat per |  |  |  | Enter a pipe inner dia (cm) |  | Diameter = | 21.35 | cm | [14 empty] | 4 for D
| section in |  |  |  | Enter a total pipe length (m) |  | Length = | 20000 | m |  |  |  | Total heat |  |  | Nitrogen |  | Nitrogen | Nitrogen |  | Number | Overall avg |  | and 1.3 safety
| Watts: |  | Bin | [7 empty] | Total heat |  | in each |  | Specific heat | temperature | mt | density | viscosity | Pipe inner dia. | of parallel | fluid velocity | Re | f | dL | DP | P | Sat T at P
| Qsect (W) |  | size |  | Q in | Q in |  | Qstatic | Qstatic | Total heat | in each bin |  | section |  | (J/gK) | (K) | (g/s) | (g/cm3) | (Pa s) | (cm) | pipes | (cm/s) |  |  | (cm) | (Pa) | (bar) | (K)
|  |  | (m) | Z (m) | (W/m) | (W per bin) |  | (W/m) | (W per bin) | (W/m) | (W per bin) |  | Qsect (W)
Supply end |  |  | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 |  |  |  | 2.0396 | 70 | 19611.4001 | 0.84808 | 0.00020424 | 21.35 | 1 | 64.5931 | 572624.5787 | 0.014952 | 0 | 0 | 8 | 101.5138
Section 1 | 200000 |  | 333.3333 | 333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  | 200000 |  | 2.0396 | 70.3333 | 19611.4001 | 0.84808 | 0.00020424 | 21.35 | 1 | 64.5931 | 572624.5787 | 0.014952 | 33333.3333 | 4130.2137 | 7.9587 | 101.4458
|  |  | 333.3333 | 666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0384 | 70.6669 | 19611.4001 | 0.8464 | 0.00020189 | 21.35 | 1 | 64.7213 | 579292.7583 | 0.014909 | 33333.3333 | 4126.4534 | 7.9174 | 101.3775
|  |  | 333.3333 | 1000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0373 | 71.0006 | 19611.4001 | 0.84472 | 0.00019956 | 21.35 | 1 | 64.8502 | 586061.8636 | 0.014866 | 33333.3333 | 4122.6767 | 7.8762 | 101.3088
|  |  | 333.3333 | 1333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0363 | 71.3344 | 19611.4001 | 0.84304 | 0.00019725 | 21.35 | 1 | 64.9796 | 592933.1183 | 0.014823 | 33333.3333 | 4118.8842 | 7.835 | 101.2399
|  |  | 333.3333 | 1666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0354 | 71.6685 | 19611.4001 | 0.84135 | 0.00019496 | 21.35 | 1 | 65.1096 | 599907.7341 | 0.014779 | 33333.3333 | 4115.0766 | 7.7939 | 101.1707
|  |  | 333.3333 | 2000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0345 | 72.0026 | 19611.4001 | 0.83967 | 0.00019268 | 21.35 | 1 | 65.2402 | 606986.9093 | 0.014736 | 33333.3333 | 4111.2546 | 7.7528 | 101.1012
|  |  | 333.3333 | 2333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0338 | 72.3369 | 19611.4001 | 0.83798 | 0.00019043 | 21.35 | 1 | 65.3714 | 614171.8264 | 0.014693 | 33333.3333 | 4107.4191 | 7.7117 | 101.0313
|  |  | 333.3333 | 2666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0331 | 72.6714 | 19611.4001 | 0.8363 | 0.00018819 | 21.35 | 1 | 65.5031 | 621463.6504 | 0.01465 | 33333.3333 | 4103.5707 | 7.6706 | 100.9612
|  |  | 333.3333 | 3000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0325 | 73.0059 | 19611.4001 | 0.83461 | 0.00018598 | 21.35 | 1 | 65.6354 | 628863.5263 | 0.014606 | 33333.3333 | 4099.7104 | 7.6296 | 100.8908
|  |  | 333.3333 | 3333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0319 | 73.3405 | 19611.4001 | 0.83293 | 0.00018378 | 21.35 | 1 | 65.7683 | 636372.5768 | 0.014563 | 33333.3333 | 4095.839 | 7.5887 | 100.82
|  |  | 333.3333 | 3666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0315 | 73.6751 | 19611.4001 | 0.83124 | 0.00018161 | 21.35 | 1 | 65.9018 | 643991.9003 | 0.01452 | 33333.3333 | 4091.9575 | 7.5478 | 100.7489
|  |  | 333.3333 | 4000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0312 | 74.0098 | 19611.4001 | 0.82955 | 0.00017946 | 21.35 | 1 | 66.0358 | 651722.5676 | 0.014477 | 33333.3333 | 4088.0666 | 7.5069 | 100.6775
|  |  | 333.3333 | 4333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0309 | 74.3446 | 19611.4001 | 0.82786 | 0.00017732 | 21.35 | 1 | 66.1704 | 659565.6198 | 0.014433 | 33333.3333 | 4084.1675 | 7.466 | 100.6058
|  |  | 333.3333 | 4666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0307 | 74.6794 | 19611.4001 | 0.82618 | 0.00017521 | 21.35 | 1 | 66.3056 | 667522.0652 | 0.01439 | 33333.3333 | 4080.2611 | 7.4252 | 100.5338
|  |  | 333.3333 | 5000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0306 | 75.0142 | 19611.4001 | 0.82449 | 0.00017312 | 21.35 | 1 | 66.4414 | 675592.8768 | 0.014347 | 33333.3333 | 4076.3484 | 7.3845 | 100.4614
Section 2 | 200000 |  | 333.3333 | 5333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  | 200000 |  | 2.0306 | 75.349 | 19611.4001 | 0.8228 | 0.00017104 | 21.35 | 1 | 66.5777 | 683778.9885 | 0.014304 | 33333.3333 | 4072.4306 | 7.3438 | 100.3887
|  |  | 333.3333 | 5666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0307 | 75.6838 | 19611.4001 | 0.82111 | 0.00016899 | 21.35 | 1 | 66.7145 | 692081.2929 | 0.014261 | 33333.3333 | 4068.5087 | 7.3031 | 100.3157
|  |  | 333.3333 | 6000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0308 | 76.0186 | 19611.4001 | 0.81942 | 0.00016696 | 21.35 | 1 | 66.852 | 700500.637 | 0.014218 | 33333.3333 | 4064.5839 | 7.2624 | 100.2424
|  |  | 333.3333 | 6333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0311 | 76.3533 | 19611.4001 | 0.81774 | 0.00016495 | 21.35 | 1 | 66.99 | 709037.8195 | 0.014175 | 33333.3333 | 4060.6574 | 7.2218 | 100.1687
|  |  | 333.3333 | 6666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0314 | 76.688 | 19611.4001 | 0.81605 | 0.00016296 | 21.35 | 1 | 67.1285 | 717693.5867 | 0.014132 | 33333.3333 | 4056.7304 | 7.1813 | 100.0946
|  |  | 333.3333 | 7000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0318 | 77.0226 | 19611.4001 | 0.81436 | 0.00016099 | 21.35 | 1 | 67.2676 | 726468.6291 | 0.014089 | 33333.3333 | 4052.8043 | 7.1407 | 100.0202
|  |  | 333.3333 | 7333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0323 | 77.3572 | 19611.4001 | 0.81267 | 0.00015904 | 21.35 | 1 | 67.4072 | 735363.5774 | 0.014046 | 33333.3333 | 4048.8802 | 7.1002 | 99.9455
|  |  | 333.3333 | 7666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0329 | 77.6916 | 19611.4001 | 0.81099 | 0.00015712 | 21.35 | 1 | 67.5474 | 744378.9984 | 0.014003 | 33333.3333 | 4044.9596 | 7.0598 | 99.8704
|  |  | 333.3333 | 8000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0336 | 78.0259 | 19611.4001 | 0.8093 | 0.00015521 | 21.35 | 1 | 67.6881 | 753515.3911 | 0.013961 | 33333.3333 | 4041.0439 | 7.0194 | 99.7949
|  |  | 333.3333 | 8333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0343 | 78.3601 | 19611.4001 | 0.80762 | 0.00015333 | 21.35 | 1 | 67.8294 | 762773.182 | 0.013918 | 33333.3333 | 4037.1345 | 6.979 | 99.7191
|  |  | 333.3333 | 8666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0352 | 78.6942 | 19611.4001 | 0.80593 | 0.00015147 | 21.35 | 1 | 67.9712 | 772152.7212 | 0.013876 | 33333.3333 | 4033.2329 | 6.9387 | 99.6429
|  |  | 333.3333 | 9000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0361 | 79.0281 | 19611.4001 | 0.80425 | 0.00014963 | 21.35 | 1 | 68.1136 | 781654.2772 | 0.013833 | 33333.3333 | 4029.3406 | 6.8984 | 99.5664
|  |  | 333.3333 | 9333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0371 | 79.3619 | 19611.4001 | 0.80256 | 0.00014781 | 21.35 | 1 | 68.2564 | 791278.0327 | 0.013791 | 33333.3333 | 4025.4592 | 6.8581 | 99.4894
|  |  | 333.3333 | 9666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0382 | 79.6954 | 19611.4001 | 0.80088 | 0.00014601 | 21.35 | 1 | 68.3999 | 801024.0795 | 0.013749 | 33333.3333 | 4021.5903 | 6.8179 | 99.4121
|  |  | 333.3333 | 10000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0393 | 80.0288 | 19611.4001 | 0.7992 | 0.00014423 | 21.35 | 1 | 68.5438 | 810892.4135 | 0.013707 | 33333.3333 | 4017.7355 | 6.7777 | 99.3344
Section 3 | 200000 |  | 333.3333 | 10333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  | 200000 |  | 2.0406 | 80.362 | 19611.4001 | 0.79752 | 0.00014248 | 21.35 | 1 | 68.6883 | 820882.9296 | 0.013665 | 33333.3333 | 4013.8967 | 6.7376 | 99.2564
|  |  | 333.3333 | 10666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0419 | 80.695 | 19611.4001 | 0.79584 | 0.00014074 | 21.35 | 1 | 68.8332 | 830995.4167 | 0.013623 | 33333.3333 | 4010.0755 | 6.6975 | 99.1779
|  |  | 333.3333 | 11000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0433 | 81.0277 | 19611.4001 | 0.79416 | 0.00013903 | 21.35 | 1 | 68.9787 | 841229.5518 | 0.013582 | 33333.3333 | 4006.2737 | 6.6574 | 99.099
|  |  | 333.3333 | 11333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0448 | 81.3602 | 19611.4001 | 0.79248 | 0.00013734 | 21.35 | 1 | 69.1247 | 851584.8951 | 0.01354 | 33333.3333 | 4002.4932 | 6.6174 | 99.0198
|  |  | 333.3333 | 11666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0464 | 81.6924 | 19611.4001 | 0.79081 | 0.00013567 | 21.35 | 1 | 69.2713 | 862060.884 | 0.013499 | 33333.3333 | 3998.7359 | 6.5774 | 98.9401
|  |  | 333.3333 | 12000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0481 | 82.0244 | 19611.4001 | 0.78913 | 0.00013402 | 21.35 | 1 | 69.4183 | 872656.8276 | 0.013458 | 33333.3333 | 3995.0037 | 6.5375 | 98.86
|  |  | 333.3333 | 12333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0498 | 82.3561 | 19611.4001 | 0.78746 | 0.0001324 | 21.35 | 1 | 69.5658 | 883371.9011 | 0.013417 | 33333.3333 | 3991.2986 | 6.4976 | 98.7795
|  |  | 333.3333 | 12666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0516 | 82.6874 | 19611.4001 | 0.78579 | 0.00013079 | 21.35 | 1 | 69.7139 | 894205.1394 | 0.013376 | 33333.3333 | 3987.6227 | 6.4577 | 98.6986
|  |  | 333.3333 | 13000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0535 | 83.0185 | 19611.4001 | 0.78411 | 0.00012921 | 21.35 | 1 | 69.8624 | 905155.4318 | 0.013335 | 33333.3333 | 3983.978 | 6.4178 | 98.6172
|  |  | 333.3333 | 13333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0555 | 83.3493 | 19611.4001 | 0.78245 | 0.00012765 | 21.35 | 1 | 70.0115 | 916221.5158 | 0.013295 | 33333.3333 | 3980.3667 | 6.378 | 98.5355
|  |  | 333.3333 | 13666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0576 | 83.6797 | 19611.4001 | 0.78078 | 0.00012611 | 21.35 | 1 | 70.161 | 927401.9709 | 0.013254 | 33333.3333 | 3976.791 | 6.3383 | 98.4532
|  |  | 333.3333 | 14000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0598 | 84.0098 | 19611.4001 | 0.77911 | 0.00012459 | 21.35 | 1 | 70.311 | 938695.213 | 0.013214 | 33333.3333 | 3973.2531 | 6.2985 | 98.3706
|  |  | 333.3333 | 14333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.062 | 84.3395 | 19611.4001 | 0.77745 | 0.0001231 | 21.35 | 1 | 70.4615 | 950099.4879 | 0.013175 | 33333.3333 | 3969.7553 | 6.2588 | 98.2875
|  |  | 333.3333 | 14666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0643 | 84.6688 | 19611.4001 | 0.77579 | 0.00012162 | 21.35 | 1 | 70.6125 | 961612.8658 | 0.013135 | 33333.3333 | 3966.2999 | 6.2192 | 98.2039
|  |  | 333.3333 | 15000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0667 | 84.9978 | 19611.4001 | 0.77413 | 0.00012017 | 21.35 | 1 | 70.764 | 973233.2347 | 0.013096 | 33333.3333 | 3962.8893 | 6.1795 | 98.1199
Section 4 | 200000 |  | 333.3333 | 15333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  | 200000 |  | 2.0692 | 85.3264 | 19611.4001 | 0.77247 | 0.00011874 | 21.35 | 1 | 70.9159 | 984958.2952 | 0.013056 | 33333.3333 | 3959.5259 | 6.1399 | 98.0354
|  |  | 333.3333 | 15666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0717 | 85.6545 | 19611.4001 | 0.77081 | 0.00011733 | 21.35 | 1 | 71.0683 | 996785.5541 | 0.013018 | 33333.3333 | 3956.2121 | 6.1004 | 97.9504
|  |  | 333.3333 | 16000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0743 | 85.9823 | 19611.4001 | 0.76916 | 0.00011595 | 21.35 | 1 | 71.2212 | 1008712.319 | 0.012979 | 33333.3333 | 3952.9507 | 6.0609 | 97.865
|  |  | 333.3333 | 16333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.077 | 86.3096 | 19611.4001 | 0.7675 | 0.00011458 | 21.35 | 1 | 71.3745 | 1020735.6925 | 0.012941 | 33333.3333 | 3949.7439 | 6.0214 | 97.779
|  |  | 333.3333 | 16666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0798 | 86.6365 | 19611.4001 | 0.76585 | 0.00011324 | 21.35 | 1 | 71.5283 | 1032852.5669 | 0.012902 | 33333.3333 | 3946.5946 | 5.9819 | 97.6926
|  |  | 333.3333 | 17000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0827 | 86.963 | 19611.4001 | 0.7642 | 0.00011191 | 21.35 | 1 | 71.6826 | 1045059.6188 | 0.012865 | 33333.3333 | 3943.5054 | 5.9425 | 97.6056
|  |  | 333.3333 | 17333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0856 | 87.289 | 19611.4001 | 0.76256 | 0.00011061 | 21.35 | 1 | 71.8373 | 1057353.3044 | 0.012827 | 33333.3333 | 3940.4789 | 5.9031 | 97.5182
|  |  | 333.3333 | 17666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0886 | 87.6145 | 19611.4001 | 0.76092 | 0.00010933 | 21.35 | 1 | 71.9925 | 1069729.8546 | 0.01279 | 33333.3333 | 3937.5179 | 5.8637 | 97.4302
|  |  | 333.3333 | 18000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0917 | 87.9395 | 19611.4001 | 0.75927 | 0.00010807 | 21.35 | 1 | 72.1481 | 1082185.2701 | 0.012753 | 33333.3333 | 3934.6252 | 5.8243 | 97.3417
|  |  | 333.3333 | 18333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0949 | 88.2641 | 19611.4001 | 0.75764 | 0.00010684 | 21.35 | 1 | 72.3041 | 1094715.318 | 0.012716 | 33333.3333 | 3931.8036 | 5.785 | 97.2527
|  |  | 333.3333 | 18666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.0981 | 88.5881 | 19611.4001 | 0.756 | 0.00010562 | 21.35 | 1 | 72.4606 | 1107315.5276 | 0.01268 | 33333.3333 | 3929.0561 | 5.7457 | 97.1631
|  |  | 333.3333 | 19000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.1014 | 88.9116 | 19611.4001 | 0.75437 | 0.00010443 | 21.35 | 1 | 72.6176 | 1119981.1868 | 0.012644 | 33333.3333 | 3926.3855 | 5.7065 | 97.073
|  |  | 333.3333 | 19333.3333 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.1048 | 89.2347 | 19611.4001 | 0.75273 | 0.00010325 | 21.35 | 1 | 72.7749 | 1132707.3398 | 0.012608 | 33333.3333 | 3923.7947 | 5.6672 | 96.9823
|  |  | 333.3333 | 19666.6667 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.1082 | 89.5571 | 19611.4001 | 0.75111 | 0.0001021 | 21.35 | 1 | 72.9327 | 1145488.7841 | 0.012573 | 33333.3333 | 3921.2868 | 5.628 | 96.891
|  |  | 333.3333 | 20000 | 40 | 13333.3333 |  | 0 | 0 | 40 | 13333.3333 |  |  |  | 2.1118 | 89.8791 | 19611.4001 | 0.74948 | 0.00010097 | 21.35 | 1 | 73.0909 | 1158320.0687 | 0.012538 | 33333.3333 | 3918.8649 | 5.5888 | 96.7991
Far end | [19 empty] | Pressure drop for sudden expansion into collector volume is (one velocity head, in Pa) = | [5 empty] | 200.1966 | 5.5868 | 96.7944
Total dynamic heat = | 800000 | W | [9 empty] | Total system heat = | 800000 | W | [10 empty] | Pressure drop in pipe (Pa) = | 241318.2673
[25 empty] | Pressure drop in pipe (bar) = | 2.4132

## HeatSummary
| Predicted | Design | Design | Installed ring
| Avg heat flux | sector load | ring load | power
Location | (W/m) | (kW) | (kW) | (MW)
80 - 90 K thermal shield | 6.5 | 78.8125 | 1891.5 | 22.9778
90 - 110 K beam screen | 10 | 97.8 | 2347.2 | 27.9579
4.5 - 5.5 K cold mass | 0.83 | 10.0637 | 241.53 | 67.3162
Corrector leads at 80 K | 0.2225 | 5.5625 | 133.5 | 1.603
Corrector leads at 5 K | 0.002 | 0.05 | 1.2 | 0.33564
4.5 K liquefaction (g/s) |  | 1.125 | 27 | 0.92299
80 K liquefaction (g/s) |  | 7.4063 | 177.75 | 0.97731
Total for VLHC |  |  |  | 122.0908

## Equations
|  | pipe | Thermal shield | Beam screen | and thermal shield | (Magnet and | Magnet cold mass
|  | (in transfer line) | (magnet) | (two beams) | (transfer line) | transfer line)
Temp in | (K) | 77 | 77.3506 | 84.4636 | 0 | 77 | 4.5
Press in | (bar) | 20 | 19.1097 | 19.0377 | 17.4926 | 20 | 4
Enthalpy in | (J/g) | 416.809 | 418.6379 | 455.7465 | 15.1 | 416.809 | 12.09 | hin
Entropy in | (J/gK) | 18.3584 | 18.467 | 18.9371 | #NUM! | 18.3584 | 3.522 | sin
Temp out | (K) | 77.3506 | 84.4636 | 101.9942 | 106.4433 | 106.4433 | 5.5
Press out | (bar) | 19.1097 | 19.0377 | 17.4926 | 16.7302 | 16.7302 | 1.8
Enthalpy out | (J/g) | 418.6379 | 455.7465 | 547.204 | 570.4149 | 570.4149 | 35.9 | hout
Entropy out | (J/gK) | 18.467 | 18.9371 | 20.0875 | 20.3958 | 20.3958 | 8.706 | sout
Predicted heat load | (W/m) | 0.1 | 4.2 | 10 | 2.2 | 16.0745 | 0.83 | Qpred
Heat uncertainty factor |  | 1.25 | 1.25 | 1.25 | 1.25 |  | 1.25 | f1
Design heat load | (W/m) | 0.125 | 5.25 | 12.5 | 2.75 | 20.625 | 1.0375 | Qdesign
Distance | (m) | 9700 | 9700 | 7824 | 9700 | 9700 | 9700 | D
Design total heat | (kW) | 1.2125 | 50.925 | 97.8 | 26.675 | 200.0625 | 10.0637 | Qtotal
Design mass flow | (g/s) | 662.9616 | 1372.3249 | 1069.3493 | 48.0358 | 1302.4401 | 422.669 | mdot
Design mass flow | (g/s) | 0 | 18.4512 | 9.2256 | 1212.9918 |  | 422.669 | mdot
Segment distance | (m) |  | 135 | 135
Segment heat | (W) |  | 708.75 | 1687.5
Segment mass flow | (g/s) |  | 19.0994 | 18.4512
Segments per sector |  |  | 71.8519 | 57.9556
Design ideal power | (kW) | 20.3992 | 142.6196 | 271.2581 | #NUM! | 596.0452 | 647.2712 | Pideal
4.5 K equiv design power | (kW) | 0.31068 | 2.1721 | 4.1313 | #NUM! | 9.0778 | 9.8579 | P4.5equiv
Efficiency (fraction Carnot) |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | E
Efficiency in Watts/Watt | (W/W) | 56.0802 | 9.3353 | 9.2453 | #NUM! | 9.931 | 214.3903 | Especific
Nominal operating power | (kW) | 67.9973 | 475.3987 | 904.1937 | #NUM! | 1986.8174 | 2157.5705 | Pnominal
Overcapacity factor |  | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | f2
Installed operating power | (kW) | 88.3965 | 618.0183 | 1175.4518 | #NUM! | 2582.8626 | 2804.8417 | Pinstalled