## A
| Company | City (County) | General Project Description | Added Capacity (MWe) | Date of Application | Proposal Received in Regional Office | Date Permit Issued | NSR & 112(g) Regulated Pollutants | Projected Commence Construction Date | Actual Commence Construction Date | Operational Startup Date | BACT-LAER-112(g) Standards | BACT-LAER-112(g) Control Techniques | Pollutant Emission Increases (TPY) | Pollution Control Cost Effectiveness | Issuing Agency | State-Local Contact | General Comments
EPA Region 1
Connecticut | None
Maine | None
New Hampshire | None
Rhode Island | None
Vermont | None
EPA Region 2
New Jersey | None
New York | None
Puerto Rico | None
Virgin Islands | None
EPA Region 3
Delaware | None
Washington, DC | None
Maryland | AES Cumberland | (Garrett) | Circulating Fluidized Bed Boiler | 180 | Pre-application Only | [11 empty] | Bill Paul, (410) 631-3276
Pennsylvania | Reliant Energy, Seward Power Plant | (Indiana) | CFB boiler to replace existing unit, on-line by 2004 | 520 | 2000-09-30 |  | 2001-06-08 |  |  |  |  | NOx-0.15lb/mmBtu | SNCR |  |  | PADEP | Nashad Bhat | see http://www.reliantenergy.com/news/pressreleases/press_release_197.asp; http://pe.pennnet.com/Articles/Article_Display.cfm?Section=Articles&Subsection=Display&ARTICLE_ID=102413&KEYWORD=reliant ... Reliant a net out (repowering) for NOx, state BAT for all but CO.
Pennsylvania | Greene Energy (Wellington Development) | Greene | Circulating Fluidized Bed Boiler | 525 |  |  | 2005-06-21 |  |  |  |  | 1931 TPY NOx @.10 lb /mmbtu 289.7 TPY pm10@.012 lb/mmbtu 3767 TPY SO2@.156lb/mmbtu Hg Based on monthly calculation per NSPS Subpart Da 145 TPY H2SO4 | Filter Baghouse for PM,(CFB) Boiler and Dry SO2 Scrubber for SO2 ,(SNCR) and CFB Boiler for reducing NOx | 1,636 lb/hr for SO2 , 506 lb/hr for NOx |  | PADEP |  | Waste Coal properties: 6800-8800 BTU /LB This Project is under appeal
Pennsylvania | River Hill Power Facility | Clearfield | Circulating Fluidized Bed Boiler | 290 | 2004-07-01 |  | 2005-07-21 |  |  |  |  | 880.2 TPY NOx @ 0.07 lb/mmbtu (30 day avg) 2515.0 TPY CO @0.2 lb/mmbtu >70% load 2515 TPY SO2 @0.20 lb/mmbtu(30 day avg) (98.2% control) 150.9 TPY PM-10 @0.012 lb/mbtu Hg Based on monthly calculation per NSPS Subpart Da 125.7 TPY H2SO4 | SNCR - NOX, BAGHOUSE-PM10, LIMESTONE INJECTION-SO2 | 1900 TPY CO, 1300 TPY NOX, 4300S02, 15O TPY PM-10, 65 TPY VOC, 50 TPY H2SO4 |  | PADEP | RICHARD MAXWELL | WASTE COAL BEING BURNED
Pennsylvania | Beach Hollow Project (Robinson Power) | Washington | Circulating Fluidized Bed Boiler | 250 | 2004-05-27 |  | 2005-04-04 |  |  |  |  | 3154 TPY SO2@ 0.26lb/mmbtu (30 Day Avg) 232 TPY PM-10 @0.012 lb/mmbtu (30 Day Avg) 696 TPY NOX @0.08 lb/mmbtu (30 Day Avg) 1823 TPY CO@ 0.15 lb/mmbtu (30 day) 2.9^E-3 lb/mmbtu Hg 36.4 TPY H2SO4@0.003 lb/mmbtu |  |  |  |  | BILL CHARLTON | This power plant permit is being appealed
Pennsylvania | AES Beaver Valley |  | AES proposes to install a new 2,155MMBTU/HR CFB boiler and at the same time retire four existing pulverized coal boilers. This new configuration will generate approximate 180 MW, compared to the current 125 MW. | 180 | 2001-05-09 |  | 2001-11-21 |  |  |  |  | NOx-0.15lb/mmBtu | SNCR |  |  | PADEP | Nashad Bhat | Permitting staff reviewed the emissions data to see whether the modification would trigger major NSR requirements. Assuming past emissions were compliant, the modification would not trigger major NSR for any pollutant.
Virginia | None
West Virginia | Longview Power, LLC |  | Longview has proposed to construct a 600 megawatt (MW) (net) power generation facility with interconnection to Allegheny Energy Supply Company lines. The pulverized coal supercritical boiler burning 2.5 percent sulfur (nominal) bituminous coal would operate with a once-through, balanced draft, single reheat steam turbine/generator. A natural gas-fired auxiliary boiler would be used to supply startup steam to the main boiler. | 600 |  |  |  | NOx, |  |  |  | NOx-0.08 lb/MMBtu, SO2 - 0.15lb/MMBtu, PM - 0.018 lb/MMBtu, CO- 0.11 lb/MMBtu, H2SO4-0.0075 lb/MMBtu, Hg-6.38x10e-2 TPY | NOx burners and selective catalytic reduction | 3,214 tons per year (tpy) of sulfur dioxide, 2,142 tpy of nitrogen oxides, and 482 tpy of particulate matter. |  | PADEP | Edward S. Andrews, P.E.
West Virginia | Anker |  | Circulating Fluidized Bed Boiler | 1000 | Pre-application Only
EPA Region 4
Alabama | None
Florida | Tampa Electric Company- Polk Power | Mulberry (Polk) | 1994 PSD permit allowed construction of an Integrated Gasification Combined Cycle (IGCC) plant. The permit required a NOx BACT evaluation based on data gathered from the plant's operation to be submitted 12-18 months after operation began. On May 10, 2001, the permitting agency issued a proposed BACT determination to require SCR. Tampa Electric appealed the determination, and SCR was not required in final permit. | N/A | 2000-12-05 |  | 2002-02-05 | NOx |  |  |  | NOx - 15 ppm (syngas), 42 ppm (fuel oil) | NOx - DLN | N/A |  | Florida DEP | Al Linero | The original 1994 permit contained BACT limits for pollutants other than NOx.
Florida | JEA Northside Generating Station | Jacksonville (Duval) | Construct two new 297.5 MW CFB boilers as a repowering project to replace two existing boilers. Allowable fuels include coal and petroleum coke. | 595 |  |  | 1999-07-14 | NOx, SO2, PM/PM10, CO, VOC, HF, Hg, |  |  | 2003 | NOx-0.09 lb/mmBtu (30-day), PM/PM10-0.011 lb/mmBtu (3-hr), CO-350 lb/hr (24-hr), VOC-14 lb/hr (3-hr), HF- 0.43 lb/hr (3-hr), Hg-0.03 lb/hr (6-hr). [Note: Project nets out of review for SO2. SO2 emission limits are 0.20 lb/mmBtu (24-hr) and 0.15 lb/mmBtu (30-day). Project not subject to PSD review for SAM and Pb. SAM emission limit is 1.1 lb/hr (3-hr). Pb emission limit is 0.07 lb/hr (3-hr).] | NOx-CFB+SNCR, PM/PM10-FF, CO-GCP, VOC-GCP, Hg-CFB+FF, HF-CFB+polishing scrubber. [Note: Project not subject to BACT for SO2, SAM, and Pb. Emission control method for SO2 and SAM is CFB+polishing scrubber. Emission control for Pb is FF.] |  |  | DEP | Al Linero
Georgia | Longleaf Energy Associates, LLC (LS Power Development, LLC) | (Early) | Construct 2 new pulverized coal boilers (600 MW each) | 1200 | 2004-11-19 | 2005-01-14 |  | CO, NOx, SO2, PM/PM10, VOC, Fluorides, SAM, Hg |  |  |  | Proposed: NOx-0.07 lb/mmbtu (30-day), SO2-0.12 lb/mmbtu (30-day), PM/PM10-0.033 (30-day), CO-0.15 lb/mmbtu (30-day), VOC-0.006 lb/mmbtu (30-day), fluorides (as HF)-0.0024 lb/mmbtu (PRB) or 0.0031 lb/mmbtu (CAPP), SAM-0.005 lb/mmbtu (30-day), Hg-0.000006 lb/MWh (CAPP) or 0.000020 lb/MWh (PRB) | NOx-LNB+OFA+SCR, SO2-Dry Scrubber, PM/PM10-Baghouse, CO-GCP, VOC-GCP,fluorides-Dry Scrubber+Baghouse, SAM-Dry Scrubber+Baghouse, Hg-Dry Scrubber+Baghouse | NOx-3783, SO2-6456, PM/PM10-1861/1805, CO-8072, VOC-194, fluorides-159, SAM-265, Hg-0.11 |  | Georgia EPD | Heather Abrams | Applicant proposes either Powder River Basin (PRB) sub-bituminous coal, or Central Appalachian (CAPP) bituminous coal, or blends
Kentucky | Kentucky Mountain Power, LLC | Ary (Knott) | Construct coal-refuse-fired CFB boilers | 500 | 2000-04-19 |  | 2001-05-04 | NOx, CO, PM, VOC, SO2, SAM, Hg, Be, Pb, HF |  |  |  | NOx-0.07 lb/mmbtu, CO-0.27 lb/mmbtu, PM-0.015 lb/mmbtu, VOC-0.0072 lb/mmbtu, SO2-0.13 lb/mmbtu, SAM-0.010 lb/mmbtu, Be-0.0000217 lb/mmbtu, Hg-0.000081 lb/mmbtu, Pb-0.000194 lb/mmbtu, HF-0.0053 lb/mmbtu | NOx-SNCR, CO-GCP, PM-Baghouse, VOC-CFB Design, SO2-NIDS, SAM-CFB Design, Be-Baghouse, Hg-Baghouse, Pb-Baghouse, HF-Baghouse | NOx-2798, CO-6039, PM-341, VOC-161, SO2-2904, SAM-224, Hg-1.81, Be-0.2904, HF-118, Pb-4.34 |  | Kentucky DAQ | Don Newell | NIDS=Natural Integrated Desulfurization System, GCP=Good Combustion Practices; see http://enquirer.com/editions/2000/08/12/loc_power_company_aiming.html. Project still planned for development as of July-05. Original permit was extended.
Kentucky | Kentucky Eastern Power, LLC | (Martin) | Construct 2 new fluidized bed combustors. [Project on hold as of Feb 2003]; 500 MWe | [12 empty] | Kentucky DAQ | Don Newell | Project on hold as of February 2003.
Kentucky | Thoroughbred Generating Company, LLC (Peabody Energy) | Graham (Muhlenberg) | Construct an electric generating facility with 2 pulverized coal boilers (750 MWe each) | 1500 | 28-Feb-01; complete revised appl. 26-Oct-01 | 28-Feb-01; revised appl. 26-Oct-01 | 2002-10-11 | NOx, CO, PM, VOC, SO2, SAM, Hg, Be, Pb, Fluorides |  |  |  | NOx-0.08 lb/mmbtu (30-day), CO-0.1 lb/mmbtu (30-day), PM-0.018 lb/mmbtu (3-hr), VOC-0.0072 lb/mmbtu (30-day), SO2-0.167 lb/mmbtu (30-day) & 0.41 lb/mmbtu (24-hr) (see comment), SAM-0.00497 lb/mmbtu (30-day), Be-0.000000944 lb/mmbtu (quarterly), Hg-0.00000321 lb/mmbtu (quarterly), HF-0.000159 lb/mmbtu (30-day), Pb-0.00000386 lb/mmbtu (quarterly); also case-by-case MACT limits in tpy for VOC, Hg, HCl, HF, As, Be, Cr, Mn, Pb, Cd | NOx-LNB/SCR, CO-GCP, PM-ESP/wet ESP, VOC-GCP, SO2-wet limestone FGD, SAM-FGD/wet ESP, Be-Baghouse, Hg-baghouse/FGD, HF-FGD | NOx-6029, CO-6599, PM-1328, VOC-509, SO2-10954, SAM-326, Hg-0.21, Be-0.0615, Flourides (as HF)-10 |  | Kentucky DAQ | Ben Markin | GCP=Good Combustion Practices; permittee to perform a 2-year "optimization study" of 24-hr SO2 emissions to determine if the 24-hr limit can be decreased, with a "target" emission rate of 0.23 lb/mmbtu. Original PSD permit has been extended. PSD construction permit was appealed. After a lengthy appeal process, the Administrative Hearing Officer (AHO) on 8/9/05 recommended that parts of the permit be remanded. The AHO's recommendations were still under review as of 9/2/05.
Kentucky | Kentucky Pioneer Energy | Trapp (Clark) | Construct integrated gasification system producing synthetic gas (syngas) to combust for electricity generation. | 540 | 2000-01-31 |  | 2001-06-08 | NOx, CO, PM, VOC, SO2, Hg, Be, Pb |  |  |  | Draft Permit: NOx-0.072 lb/mmbtu, CO-0.032 lb/mmbtu, PM-0.011 lb/mmbtu, VOC-0.0044 lb/mmbtu, SO2-0.032 lb/mmbtu, SAM-0.010 lb/mmbtu, Be-6.0 e-7 lb/mmbtu, Hg-0.08 mg/dscf, Pb-0.02 mg/dscf | Draft Permit: NOx-Diluent Inj. (steam), CO-GCP, PM-GCP, VOC-GCP, SO2-Sulfur Recovery Unit, Be-GCP, Hg-GCP, Pb-GCP | NOx-1060, CO-555, PM-178, VOC-80, SO2-490, Hg-0.01, Be-0.0093, Pb-0.15 |  | Kentucky DAQ | Don Newell | see http://www.ekpc.com/news.html#PATTON
Kentucky | Calla Energy | Irvine (Estill) | Construct atmospheric fluidized-bed combustion circulating-bed boiler which will co-fire waste coal and syngas (from coal & biomass gasifier); 110 MWe |  | 04/25/01; complete revised appl. 10/01 | 2002-01-07 |  | NOx, CO, PM, SO2, SAM, Be, Fluorides |  |  |  | Proposed: NOx-0.07 lb/mmbtu, CO-0.15 lb/mmbtu, PM-0.015 lb/mmbtu, SO2-0.15 lb/mmbtu (avg)/0.46 lb/mmbtu (max), SAM-0.002 lb/mmbtu, Be-0.000002.1 lb/mmbtu, Fluorides (as HF)-0.0023 lb/mmbtu | Proposed: NOx-AFBC design/SCR, CO-GCP, PM-FF, SO2-AFBC design, SAM-FF, Be-/FF, Fluorides-AFBC design/FF | NOx-372, CO-795, PM-107, SO2-793, SAM-12.3, Be-0.01, Fluorides (as HF)-12 |  | Kentucky DAQ | Herbert Campbell | FF=Fabric Filter, GCP=Good Combustion Practices; see http://www.epsa.org/competition/index.cfm?section=competition, http://www.appalachianfocus.org/_mine1/00000152.htm
Kentucky | Kentucky Western Power, LLC | Calvert City (Marshall) | Construct 2 new fluidized bed combustors. [Project on hold as of Feb 2003]; 500 MWe |  | 2001-06-13 | 2001-06-25 |  | [Project on hold as of Feb 2003] |  |  |  | [Project on hold as of Feb 2003] |  |  |  | Kentucky DAQ | Don Newell | Project on hold as of February 2003.
Kentucky | East Kentucky Power Cooperative, Spurlock Generating Station | Maysville (Mason) | Construct 1 new circulating fluidized bed boiler | 270 | 2001-04-24 | 2002-02-14 | 2002-06-21 | NOx, CO, PM, SO2, VOC, SAM (also see comments) |  |  |  | NOx-0.07 lb/mmbtu (30-day), CO-0.15 lb/mmbtu (30-day), PM-0.015 lb/mmbtu (3-hr), SO2-0.20 lb/mmbtu (24-hr), SAM-0.0050 lb/mmbtu (also see comments) | Proposed: NOx-SNCR, CO-GCP, PM-Baghouse, SO2-CFB design/dry lime scrubber, SAM-CFB design/dry lime scrubber (also see comments) | NOx-767, CO-2190, PM-164, SO2-2190, SAM-55 (also see comments) |  | Kentucky DAQ | Koorosh Farhoudi | Emissions limits also established for VOC, Hg, flourides, Pb, Be. NOx limit is temporarily waived during an initial "optimization" period; final NOx limit shall not exceed 0.10 lb/mmbtu depending on results achieved during "optimization" period. CFB=Circulating Fluidized Bed (which includes limestone injection), GCP=Good Combustion Practices
Kentucky | East Kentucky Power Cooperative, Spurlock Generating Station (Unit 4) | Maysville (Mason) | Construct 1 new circulating fluidized bed boiler | 300 | 2004-09-13 | 2004-10-04 |  | NOx, CO, PM/PM10, SO2, SAM, Hg |  |  |  | Proposed: NOx-0.1 lb/mmbtu (?-day), CO-0.15 lb/mmbtu (?-hr), PM/PM10-0.015 lb/mmbtu (?-hr), SO2-0.20 lb/mmbtu (?-hr), VOC-nothing proposed, SAM-0.0050 lb/mmbtu (?-hr), Hg-0.0000026 lb/mmBtu (also see comments) | Proposed: NOx-SNCR, CO-GCP, PM/PM10-Baghouse, SO2-CFB design/dry lime scrubber, SAM-CFB design/dry lime scrubber, VOC-nothing proposed, Hg-Baghouse (also see comments) | NOx-1226, CO-1840, PM/PM10-184, SO2-2453, VOC-44, SAM-61, Hg-0.033 (also see comments) |  | Kentucky DAQ | Don Newell | As of Aug-05, application still under review by permitting agency. Boiler will be fired with coal and will have capability to burn tire-derived fuel. Applicant proposes an "optimization" study after start of operation to assess whether NOx emissions limit can be lowered.
Kentucky | Cash Creek | (Henderson) | Pulverized coal boilers, 1000 MWe |  | [See comment] | [12 empty] | Application not complete as of February 2003.
Kentucky | Cash Creek Generation, LLC | (Henderson) | Construct 2 new pulverized coal boilers (500 MW each) | 1000 | 25-Nov-03 revised | 2003-12-22 |  | (see comments) |  |  |  | (see comments) | (see comments) | (see comments) |  | Kentucky DAQ | Don Newell | A revised permit application is expected in first quarter of 2005.
Kentucky | Cash Creek Generation, LLC | (Henderson) | Construct IGCC facility with 2 combustion turbines | 677 nominal | 2005-07-20 | 2005-07-22 |  | PM/PM10, SO2, NOx, CO, VOC, SAM |  |  |  | Proposed for Combustion Turbines on Syngas: PM/PM10-0.007 lb/MMBtu (filterable) (3-hr), SO2-0.043 lb/MMBtu (3-hr), NOx-0.058 lb/MMBtu (24-hr), CO-0.036 lb/MMBtu (30-day), VOC-0.006 lb/MMBtu (24-hr), SAM-0.0049 lb/MMBtu (30-day) Proposed for Combustion Turbines on Natural Gas: same as syngas except NOx-0.087 lb/MMBtu (24-hr), CO-0.053 lb/MMBtu (30-day) | Proposed for Combustion Turbines on Syngas: PM/PM10-syngas scrubbing, SO2-acid gas removal by MDEA absorption in gasification process, NOx-diluent N2 injection, CO-GCP, VOC-GCP, SAM-acid gas removal by MDEA absoption in gasification process Proposed for Combustion Turbines on Natural Gas: PM/PM10-GCP and fuel characteristics, SO2-GCP and fuel characteristics, NOx-diluent N2 injection, CO-GCP, VOC-GCP | PM/PM10-108, SO2-649, NOx-875, CO-543, VOC-91, SAM-74 |  | Kentucky DAQ | Don Newell | General Electric gasification technology with MDEA absorption sulfur removal. GE 7FA combustion turbines.
Kentucky | Louisville Gas & Electric Company (LG&E), Trimble County Generating Station | (Trimble) | Construct 1 new pulverized coal boiler (750 MW) | 750 | 01-Dec-04 revised | 09-Dec-04 | 06-Jul-05 draft permit | PM/PM10, CO, VOC, SAM, fluorides (also see comments) |  |  |  | Proposed: CO-0.10 lb/mmbtu (3-hr), PM/PM10-0.0018 lb/mmbtu (3-hr), SAM-26.6 lb/hr (3-hr), VOC-0.0032 lb/mmbtu (3-hr), fluorides-no rate proposed, Hg-no rate proposed | Proposed: CO-GCP, PM/PM10-Baghouse, SAM-Wet ESP, VOC-GCP, fluorides-wet FGD, Hg-SCR+Baghouse+Wet FGD (also see comments) | CO-3041, PM/PM10-567, SAM-117, VOC-98, fluorides-6.8, Hg-not proposed (also see comments) |  | Kentucky DAQ | Don Newell | Applicant proposes to net out of PSD review for NOx and SO2. Proposed NOx control is SCR (0.05 lb/mmBtu) and proposed SO2 control is wet FGD (0.107 lb/mmBtu). Proposed primary boiler fuel is eastern bituminous coal. Boiler will also have capability of firing a blend containing eastern bituminous coal and up to 50% western coal.
Kentucky | Estill County Energy Partners | Irvine (Estill) | Construct 1 new circulating fluidized bed boiler. Fuel will be waste eastern bituminous coal. | 110 | 2004-08-31 | 2004-09-03 |  | PM/PM10, SO2, H2SO4, NOx, CO, VOC, Hg (and other HAPs listed) |  |  |  | Proposed: SO2-0.13 lb/mmbtu (30-day) and 0.15 lb/mmbtu (24-hr), PM/PM10-0.015 lb/mmbtu filterable (3-hr), NOx-0.07 lb/mmbtu (30-day), CO-0.15 lb/mmbtu (30-day), VOC-0.007 lb/mmbtu (30-day), H2SO4-0.005 lb/mmbtu (30-day); Hg-0.000004 lb/mmbtu or 90% removal | Proposed: SO2-inherent CFB andn polishing dry scrubber, PM/PM10 - baghouse, NOx-inherent CFB and SNCR, CO-GCP, VOC-GCP, H2SO4-inherent CFB and dry scrubber and baghouse; Hg-co-benefit from BACT controls | SO2-816, PM/PM10-109 (filterable), NOx - 454, CO - 944, VOC - 45, H2SO4-31; Hg-0.09 |  | Kentucky DAQ | Don Newell | As of 16-Dec-04, permitting agency considered the application to be deficient.
Mississippi | Tractebel Power Inc | Choctaw | Lignite Fired | 462 | [7 empty] | (see comments) | (see comments) | (see comments) |  | Mississippi DEQ | Maya Rao | Since this is a relatively old permit, BACT emissions limits and control techniques not shown.
North Carolina | None
South Carolina | Santee Cooper, Cross Generating Station | Cross (Berkeley) | Existing electric generating facility to be expanded with addition of two pulverized coal boilers (660 MWe each). | 1320 | [See comment (1)] |  | 2004-02-05 | PM/PM10, CO, VOC, Pb, Hg [See comments (2) and (4)] |  |  |  | PM (filterable only)-0.015 lb/mmBtu (3-hr), PM10 (filterable and condensible)-0.018 lb/mmBtu (3-hr), CO-0.16 lb/mmBtu (3-hr), VOC-0.0024 lb/mmBtu (3-hour), Pb-0.0000169 lb/mmBtu, Hg-0.0000036 lb/mmBtu [See comments (2), (3), (4)] | PM/PM10-dry ESP, CO-GCP, VOC-GCP, Pb-dry ESP, Hg-SCR, dry ESP, wet FGD [See comment (2)] | PM (filterable)-869, PM10 (filterable and condensible)-952, CO-8492, VOC-121, Pb-0.85, Hg-0.166 [See comments (2) and (4)] |  | South Carolina DHEC | Joe Eller | (1) Original permit application received in 2002; final revised application received in 2003. (2) Project netted out of PSD review for SO2, NOx, and SAM; therefore, emissions limits for these pollutants are not BACT limits. (3) Permit contains several emissions limits in addition to those shown; the limits shown are BACT or 112(g) limits. (4) HAPs with emissions limits also include HCl, HF, and several metals.
Tennessee | None
EPA Region 5
Illinois | Steelhead- Southern Illinois Clean Energy Center | (Williamson) | 544 MW IGCC unit, 95 MM ft3/day syn gas, using No. 6 Illinois coal | 544 | 2004-10-01 |  |  | SO2, NOx, PM, CO, VOM, F |  |  |  | SO2 0.033, Nox 0.059, PM filterable 0.00924, CO 0.04, VOM 0.0031, H2SO4 0.0042 | dilluent injection, syngas clean up, good controls |  |  | IL EPA | Bob Smet- 217-785-9250 | First IGCC project in IL, IEPA requires any new coal project to consider IGCC as part of the top down BACT analysis
Illinois | Taylorville Energy Center | Taylorville (Christian) | 577 MW IGCC unit | 577
Illinois | Enviropower | Benton (Franklin) | Two (2) CFB boilers, 250 MWe each | 500 | 2000-08-15 | 2000-03-24 | 2001-07-03 | SO2, NOx, PM, CO, VOM, F |  |  |  | SO2 92% redux, 0.25 lb/mmBtu; NOx 0.125, PM 0.015, CO 0.27, VOC 0.007 lb/mmBtu | CFB w/sorbent injection, baghouses | SO2 5595, NOx 2808, PM 466, CO 6040, VOC 162, F 9.6 |  | IL EPA | Shashi Shah - 217-782-2113 | see http://yosemite.epa.gov/r5/il_permt.nsf/133e3c6aefa1d1638625666a00563357/ff3340e245bc72a385256a2600672e0b/$FILE/EnviroPowerPS.PDF; Coal and tailings-fired. For Hg - An emission rate of 0.000004 lb/mmBtu or emissions below the detection level of established emission test methodology; http://www.epa.gov/region5/air/permits/ilonline.htm
Illinois | Southern Illinois Power Cooperative, Marion Power Station | (Williamson) | 1st Project - 1 CFB boiler to replace 3 existing coal fired generating units. 2nd Project - 2 simple cycle combustion turbines. 3rd Project- Installation of SCR on existing coal fired boiler | 120 | 2000-07-12 | 2001-03-05 | 2001-05-16 | CO |  |  |  | CO-0 .015lb/mmBtu | Combustion Controls | Net Emission Increase - NOx: (-3858 tpy), SO2: (-9084.6 tpy), CO: 833.5 tpy, VOC: 32.1 tpy, PM: (-5 tpy), PM10: 13.9. |  | IL EPA | Shashi Shah - 217-782-2113 | see http://www.epa.state.il.us/public-notices/2001/sipco-marion/index.html
Illinois | Cornbelt Energy | Elkhart (Logan) | Prairie Energy Power Plant. PSD for low-emitting power plant. | 91 | 3rd quarter, 2001 |  |  | NOx, PM, SO2 |  |  |  | NOx - 0.132, SO2 - 0.3 lb/mmBtu | SCR, ESP, FGD |  |  | IL EPA | Shashi Shah - 217-782-2113 | Design funded in part by IL Clean Coal Institute/US DOE. http://www.epa.gov/region5/air/permits/ilonline.htm; http://pepei.pennnet.com/articles/article_display.cfm?Section=ONART&Category=PRODJ&PUBLICATION_ID=6&ARTICLE_ID=164286
Illinois | Peabody - Prairie State Generating Station | (Washington) | Peabody will build the Prairie State Energy Campus -- a 1,500-megawatt (MW), coal-fired electricity plant, comprised of two 750 MWe pulverized coal boilers and one 400 mmBtu/hr auxillary boiler -- in Washington County in southern Illinois. Construction at Prairie is expected to last approximately four years. This permit is currently before the EAB on appeal. EPA conducted a Section 7 consultation with USFWS under the Endangered Species Act to address potential impacts on endangered species. | 1500 | 10/2001 | 2004-02-04 | Jan. 2005 | SO2, PM, NOx, CO, VOC, H2SO4, Pb, F |  |  |  | SO2 - 0.30 lb/mmBtu, PM10 - 0.018, NOx - 0.10, CO - 0.15, VOC - 0.01, H2SO4 - 0.039 | SCR, wet scrubber, fabric filter or ESP | SO2 - 19,964; PM10 - 1,255; NOx - 6,762; CO - 10,023; lead - 2; VOC - 675; H2SO4 - 2,615; Fluorides - 17 |  | IL EPA | Shashi Shah - 217-782-2113 | http://biz.yahoo.com/rf/011022/n22141122_1.html; Currently under EAB appeal.
Illinois | Dynegy-Illinois Power | Baldwin (Randolph) | $1.5 billion, two 650 MW coal-fired boilers. 4 - 5 million tons of coal a year by rail/barge. Adding to 2000 MW from 3 existing boilers. | 1300 | No app as of 12/4/01
Illinois | Indeck-Elwood | Elwood (Will) | Two (660 MW total capacity) circulating fluidized bed boilers firing pulverized coal. This project is currently under EAB appeal. USEPA conducted a Section 7 Endangered Species Act consultation with USFWS to addess potential impacts to endangered species. | 660 | 2002-03-21 | 2003-04-07 | 2003-10-10 | PM, SO2, NOx, CO, VOC, H2SO4, Pb, F |  |  |  | PM-.015 lb/MMBTU, SO2-.15 lb/MMBTU, NOx- .10 lb/MMBTU, CO-.10 lb/MMBTU, VOC- .004 lb/MMBTU | Baghouse, CFB boiler technology, limestone addtion to bed, SNCR | PM- 384 TPY, SO2- 3840 TPY, NOx- 2560 TPY, CO- 2816 TPY, VOC- 102 TPY |  | IL EPA | Shashi Shah- 217-782-2113 | The permit was appealed before the Environmental Appeals Board by the Sierra Club; EAB remanded the permit pending consultation on the Endangered Species Act between EPA and FWS
Illinois | Illinois Energy Group- Franklin Energy Coal Project | Ewing (Franklin) | Two 680 MW supercritical steam pulverized coal boilers, mine mouth plant | 1360 | 2002-06-07 |  |  | SO2, NOx, PM |  |  |  | SO2- .08 lb/mmBTU, NOx- .08lb/mmBTU, PM-.01 lb/mmBTU | SCR, ESP, SO2 scrubber | SO2 -4300 TPY, NOx-660 TPY, PM-660 TPY |  | IL EPA
Illinois | Midwest Generation | Morris (Grundy) | PSD to convert 2 of 5 Oil/NG boilers to coal. | 1000 | Application Received
Indiana | Enviropower | Petersburg (Pike) | 2 - 250 MWe CFB boilers, combusting waste coal | 500 | 2000-08-03 | [12 empty] | see http://www.state.in.us/idem/oam/permits/powerplt/summary/enviropike.html, http://enquirer.com/editions/2000/08/12/loc_power_company_aiming.html
Michigan | None
Minnesota | Minnesota Power & Blandin Paper Company |  | Addition of 225 MWe. | [14 empty] | Minnesota Power, an Allete company, announced in mid-August that it will build a 225-Megawatt power plant in cooperation with Blandin Paper Company. The plant will be fueled with a combination of biomass (mostly wood waste), low-sulfur coal, and natural gas. Using a circulating fluidized bed boiler, the plant will be capable of being powered with up to 40 percent wood waste. See <http://www.allete.com/placed/08-16-2001bland.html>. THIS PROJECT HAS BEEN CANCELED DUE TO ECONOMIC INFEASIBILITY.
Ohio | Dominion Energy | Ashtabula |  | 600 | 2004-03-08 | [12 empty] | NOx emissions are projected at 2,300 tons per year and VOC emissions are projected at 120 tons per year.
Wisconsin | Wisconsin Energy - Elm Road Generating Station (At existing Oak Creek Facility) | Oak Creek (Milwaukee) | Two 615 MW supercritical pulverized coal boilers; construction is proposed to begin in 2004, with in-service dates of 2007, and 2009 for these units. (One 600 MW integrated gasification combined cycle unit was proposed, but was not approved by the WI Public Service Comission.) | 1230 | June 18 2002 - October 1 2003 | October14, 2003 | January 14, 2004 | CO, NOx, PM/PM10, SO2, VOC, Hg, Be, HF, HCL, H2SO4, Pb | Permit has been contested. Hearings begin in October. |  |  | CO: 0.12 lb/mmbtu, NOx: 0.07 lb/mmbtu, PM/PM10: 0.018 lb/mmbtu, SO2: 0.15 lb/mmbtu, VOC: 0.0035 lb/mmbtu, Pb: 7.9 lb/tbtu, Hg: 1.12 lb/tbtu, Be: 0.35 lb/tbtu, HF: 0.00088 lb/mmbtu, H2SO4: 0.01lb/mmbtu, HCL: 2.56 lb/mmbtu | CO: LNB, NOx: LNB/SCR, PM/PM10: FF, SO2: Wet FGD, VOC: LNB, Pb/Hg/Be/HF,HCL: FF, H2SO4: FGD/Wet ESP | CO: 6542, NOx: 3849, PM: 1460, PM10: 1272, SO2: 8121, VOC: 194, Hg, 0.06, Be: 0.02, HF: 48.5, H2SO4: 541, Pb: 0.4, HCL: 139 |  | WI DNR | Raj Vakharia (608-267-2015) | see http://www.corporate-ir.net/ireye/ir_site.zhtml?ticker=wec&script=410&layout=7&item_id=154598, http://milwaukee.bcentral.com/milwaukee/stories/2001/09/10/story3.html For permits, see: http://www.dnr.state.wi.us/org/aw/air/permits/APM_toc.htm
Wisconsin | Wisconsin Power and Light |  | On-line by 2006 | 500 | [13 empty] | see http://www.alliantenergy.com/news/news.php?issueID=53
Wisconsin | Wisconsin Public Service Corporation | Wausau | The Weston Unit 4 plant, planned for construction at the existing Weston generating station located three miles south of Wausau in central Wisconsin, is being built to satisfy growing electric demand. | 500 | July 16, 2004 | September 2003 | October 19, 2004 | CO, NOx, PM/PM10, SO2, VOC, Hg, Be, HF, HCL, H2SO4, Pb |  |  |  | CO: 0.15 lb/mmbtu, NOx: 0.06 lb/mmbtu, PM/PM10: 0.020 lb/mmbtu/0.018 lb/mmbtu, SO2: 0.09 lb/mmbtu, VOC: 0.0036 lb/mmbtu, Pb: 0.13 lbs/hr, Hg: 1.7 lb/tbtu, Be: 1.3 lb/tbtu, HF: 0.000217 lb/mmbtu, H2SO4: 0.005 lb/mmbtu, HCL: 10.94 lbs/hr | CO: LNB, NOx: LNB/SCR, PM/PM10: FF, SO2: DRY FGD, VOC: LNB, Pb/Be/HF: FF, Hg: Sorbent Injection/FF, H2SO4/HCL: FGD | CO: 3421, NOx: 1613, PM: 535, PM10: 529.2, SO2: 2266, VOC: 85, Hg, 0.039, Be: 0.029, H2SO4: 113.3, Pb: 0.59 |  | WI DNR | Raj Vakharia (608-267-2015) | see http://pepei.pennnet.com/articles/article_display.cfm?Section=ONART&Category=PRODJ&PUBLICATION_ID=6&ARTICLE_ID=165311. http://www.dnr.state.wi.us/org/aw/air/permits/03-RV-248.zip
Wisconsin | Manitowoc Public Utilities | Manitowoc | Construction of a 64 MW CFB fired boiler. Project will include elimination of solid fuel burning capabilities at existing boiler #5. Boiler #5 will retain its ability to fire natural gas as the boiler is needed at peak usage periods. New boiler will fire coal, coke, and paper pellets as well as natural gas at startup. The emission reduction from the elimination of solid fuel burning capabilties at boiler #5 will be used to net out of PSD for PM, SO2, VOC, NOx, Pb, H2SO4, Be, Hg, and F. | 64 | October 13, 2003 | N/A | Decebmer 3, 2003 | CO | N/A |  |  | CO: 0.15 lb/mmbtu, NOx: 0.155 lb/mmbtu, PM/PM10: 0.03 lb/mmbtu, VOC: 0.013 lb/mmbtu, Pb: .0002 lb/mmbtu, HF: 0.00173 lb/mmbtu, H2SO4: 0.0045lb/mmbtu, | CO: GCP, NOx: GCP, PM/PM10: FF, SO2: Lime Injection & CFB Boiler Design, VOC: GCP, Pb/Hg/Be/HF: FF, H2SO4: CFB Boiler Design | CO: 373.2, NOx: 39.9, PM: 25, PM10: 115, SO2: 32.4, VOC: 37.5, Hg, 0.065, HF: 2.76, H2SO4: .49, Pb: 0.469, Be: -.001 |  | WI DNR | Rajen Vakharia | http://www.dnr.state.wi.us/org/aw/air/permits/APM_toc.htm#section_M
EPA Region 6
Arkansas | LS Power, Plum Pt. Energy, Plum Pt. Power Sta. | Osceola (MS) | Construct 1 pulverized Powder River basin coal fired boiler to yield 550-800 MW, fuel oil used for start-up. New power plant. | 800 | May 17, 2001 | 2001-05-22 | 2003-08-20 | NOx,CO,SO2,PM/PM10,VOC,Pb,Fl,H2SO4 | 2005-02-01 |  |  | NOx: 0.09 #/mmbtu; CO: 0.16 #/mmbtu; SO2: 0.16 #/mmbtu; PM/PM10; 0.018 #/mmbtu; VOC: 0.02 #/mmbtu; H2SO4: 0.0061 #/mmbtu | NOx: LNB/SCR; CO: cc; SO2: dry FGD; PM/PM10: FF; VOC-cc; H2SO4: dry FGD, FF | NOx-7812, CO-12474, SO2-12472, PM/PM10-1458, VOC-1561, H2SO4-191, Pb-2 |  | ADEQ | Tom Rheaume, 501-682-0762 | Original application for 2 boilers and 1000 MW to 1600 MW. Plant to be designed to fire primarily low sulfur sub-bituminous Powder River Basin coal, with flexibility to fire up to 17% alternate coals. Location on MS River, 40 miles upriver from Memphis, TN. Powder River basin coal to be barged in or railed in. Final is 1 boiler and 550-800 MW. As of October, 2005, the project has yet to commence construction.
Louisiana | NRG Energy, Inc., Big Cajun II Generating Station | New Roads (Pointe Coupee Parish) | Construct 1 675 MW supercritical boiler using low sulfur coal; add a 4th boiler at an existing station | 675 | 2001-09-18 |  | 2005-08-22 | NOx,CO,SO2, PM10,VOC,Fl, Hg, Pb, Be,HCL |  |  |  | NOx: 0.071 #/mmbtu; CO: 0.135 #/mmbtu; SO2: 0.10 #/mmbtu; PM/PM10; 0.018 #/mmbtu; VOC: 0.015 #/mmbtu | Low NOx burners w/ SCR on the boiler, wet scrubber for SO2, baghouse & ESP for PM, good combustion for CO and VOC. |  |  | LDEQ | Bryan Johnston 225-219-3073
New Mexico | Mustang (Peabody) Energy, Mustang Generating Station | 35 mi. no. of Milan, McKinley Co. | Construct 1 pulverized coal fired boiler to yield 300 MW, fuel oil or nat. gas used for start-up. Proposed with low NOx burners w/ SCR on the boiler, dry scrubber for SO2, baghouse or ESP for PM, good combustion for CO and VOC. | 300 | March '02 | April '02 |  | NOx,CO,SO2,PM/PM10,VOC, Fl, H2SO4, Be |  |  | 1905-06-29 | NOx: 0.09 #/mmbtu; CO: 0.15 #/mmbtu; SO2: 0.11 #/mmbtu; PM/PM10; 0.018 #/mmbtu; VOC: 0.01 #/mmbtu | Proposed with low NOx burners w/ SCR on the boiler, dry scrubber for SO2, baghouse or ESP for PM, good combustion for CO and VOC. | NOx-1307, CO-2127, SO2-1545, PM/PM10-275, VOC-143, H2SO4-94, Pb-0.35 |  | NMED | Mike Fowler, 505--955-8041 | BACT issues remain unresolved to date
Oklahoma | None
Texas | City Public Service of San Antonio, Calaveras Lake Station | San Antonio (Bexar) | Construct 1 pulverized Powder River basin coal fired boiler to yield 750 MW. Natural gas as start-up fuel. Existing power plant | 750 | November '03 | 2003-12-02 |  | NOx,CO,SO2, PM10,VOC,HF, H2SO4, Hg | 2005-01-01 |  | April, 2009 | NOx: 0.05 #/mmbtu; CO: 0.15 #/mmbtu; SO2: 0.06 #/mmbtu; PM/PM10; 0.022 #/mmbtu; VOC: 0.0025 #/mmbtu; H2SO4: 0.0037 #/mmbtu; Hg: 0.0000098 3/mmbtu | NOx: LNB/SCR; CO: cc; SO2: wet FGD; PM/PM10: FF, wet FGD; VOC-cc; H2SO4: wet FGD, FF; Hg: FF, wet FGD, SCR | NOx-1752, CO-5256, SO2-2102, PM/PM10-771, VOC-88, H2SO4-129, Pb-0.29, Hg-0.34 |  | TCEQ | Erik Hendrickson, 512-239-1095 | Public hearing scheduled for 12/05
Texas | LS Power, Sandy Creek Energy Station | Reisel (McClennan) | Construct 1 pulverized Powder River basin coal fired boiler to yield 800 MW. Fuel oil as start-up fuel. New power plant | 800 | January '04 | 2004-01-12 |  | NOx,CO,SO2, PM10,VOC,HF, H2SO4, Hg | Late 2004 |  | Late 2008 | NOx: 0.0 5 9#/mmbtu; CO: 0.15 #/mmbtu; SO2: 0.1 0 2 #/mmbtu; PM/PM10; 0.040 33 #/mmbtu; VOC: 0.0036 #/mmbtu; H2SO4: 0.0037 7 #/mmbtu, Hg: 0.000020 17 #/mmbtu | NOx: LNB/SCR; CO: cc; SO2: dry FGD; PM/PM10: FF; VOC-cc; H2SO4: dry FGD, FF; Hg: dry FGD, FF | NOx-1804, CO-5380, SO2-3585, PM/PM10-1490, VOC-135, H2SO4-133, Pb-0.4; Hg: 0.079 |  | TCEQ | Randy Hamilton, 512-239-1000 | Public hearing scheduled for 12/05
Texas | Sempra Generation, Twin Oaks Power Plant, Unit 3 | Bremond (Robertson) | Addition of one new 600 MW, lignite (and other) fired utility boiler. | 600 | July '05 | 2005-08-03 |  | NOx,CO,SO2, PM10,VOC, HF, H2SO4, Pb, Hg |  |  |  | NOx: 0.07#/mmbtu; CO: 0.15 #/mmbtu; SO2: 0.20 #/mmbtu; PM10; 0.035 #/mmbtu; VOC: 0.0030 #/mmbtu; H2SO4: 0.020, #/mmbtu, Hg: 0.430 tpy, Pb: 0.00042 #/mmbtu | NOx: LNB/SCR/OA; CO: cc; SO2: wet FGD; PM10: FF; VOC-cc; H2SO4: wet FGD, FF; Hg: wet FGD, FF, SCR | NOx-2038, CO-4364, SO2-5818, PM10-1045, VOC-87, H2SO4-582, Pb-0.91, Hg-0.43 |  | TCEQ
Texas | TXU Oak Grove | Bremond (Robertson) | New 1720 MW, lignite fired utility boilers (3). | 1720 | July '05 | 2005-07-28 |  | NOx,CO,SO2, PM10,VOC, HF, H2SO4, Pb, Hg |  |  |  | NOx: 0.1#/mmbtu; CO: 0.17 #/mmbtu; SO2: 0.2 #/mmbtu; PM10; 0.040 #/mmbtu; VOC: 0.0045 #/mmbtu; H2SO4: 0.0055 #/mmbtu, Pb: Hg: 0.000145 #/mmbtu | NOx: LNB/SCR/OA; CO: cc; SO2: wet FGD; PM10: FF; VOC-cc; H2SO4: wet FGD, FF; PB: Wet FGD, FF; Hg: SCR, wet FGD, FF | NOx-7590, CO-13524, SO2-15079, PM10-3170, VOC-352, H2SO4-963, Pb-0.248, Hg-1.09 |  | TCEQ
EPA Region 7
Iowa | MidAmerican | Council Bluffs | Installation of one 790 MWe supercritical pulverized coal fired boiler designed for base load operation on Powder River Basin coal. "Unit 4" will be co-located with existing Units 1-3. | 790 | September '02 | 2002-09-30 | 2003-07-16 | NOx, CO, SO2, PM (with condensibles), PM10, VOC, Pb, F, TRS, H2SO4, Hg, HCl, TSM | 06/03 |  |  | Final.... NOx: 0.07 #/mmBtu (30-day), SO2: 0.10 #/mmBtu (30-day), Pb: 0.00026 #/mmBtu, F: 0.0009 #/mmBtu, TRS: 0.001 #/mmBtu, H2SO4: 0.00421 #/mmBtu, PM-10: 0.025 #/mmBtu (3-hr with condensibles), VOC: 0.0036 #/mmBtu (3-hr), CO: 0.154 #/mmBtu (24-hour), 112(g) limits... Hg: 1.7#/Tbtu, HAP Acid Gases: 0.0029#/mmBtu HCl; Organic HAP: CO as surrogate; Metallic HAP: 1.04e-4 #/mmBtu "total selected metals" | NOx-SCR, CO-cc, PM10-FF, SO2-DLS, Pb-FF, VOC-cc, Hg-activated carbon, HAP Acid Gases-DLS, Metallic HAP-FF | NOx-2689, SO2-4034, CO-5166, PM10-605, VOC-126, Pb-0.88, H2SO4 mist-142, HF-22, TRS-30, RSC-30, Trace Metals-7.2, Organic HAPs-19.3, Acid Gas HAPs-82.0, |  | IDNR | Chris Roling (515) 242-6002 & Corey Detter (515) 281-4842 | http://desmoinesregister.com/news/stories/c4788998/16963218.html
Kansas | Sand Sage (colocated at existing Sunflower Holcomb Power Station) | Holcomb (Finney) | Installation of a 660 MWe (6,500 mmBtu/hr) pulverized PRB coal and gas-fired boiler, along with ancillary coal and ash handling equipment and cooling towers. Proposed with ultra-low NOx burners (no SCR), dry scrubber, and baghouse | 660 | June '01 | 2001-06-06 | 2002-10-08 | NOx, CO, PM10, SO2, Pb, VOC |  |  |  | Final.... SO2 (0.15,30d); NOx (0.15*/0.08, 30d); CO (0.15, 3h?); PM10 (0.018 6-hr); VOC (0.0035,3h?); Pb (0.0004,3h?), * for 3 yrs after performance test; accepted "de minimis" HAP limits to avoid 112(g) review | NOx-ULNB, CO-cc, PM10-FF, SO2-DLS, Pb-FF, VOC-cc | NOx-2278, SO2-4271, CO-4271, PM10-567, VOC-100, Pb-11.4 |  | KDHE | Rick Bolfing (785) 296-1576
Kansas | Great Plains Power, Atchison Generating Station | Atchison (Atchison) | Installation of one opposed-wall-fired, dry-bottom, boiler (8100 mmBtu/hr), subbituminous coal with No. 2 oil backup and associated equipment, including cooling tower | 820 | Jan '03 | 2003-03-17 | Appication Withdrawn | CO,SO2,NOx,PM10,VOC,Pb |  |  |  | Proposed in Application... NOx (0.08,30d), CO (0.16), PM10 (0.018), SO2 (0.12,30d), VOC (0.0036); all except startup/shudown/malfunction | NOx - LNB(75%) & SCR(60%), PM10-FF(99.77%), SO2-spray drier(94%) & low sulfur coal (5%S), CO-cc, | NOx-2838, SO2-4257, CO-5676, PM10-668, VOC-128, Pb-0.59 |  | KDHE | Rick Bolfing (785) 296-1576 | Identical project also proposed for Great Plains Weston Bend (MO). At this point, Great Plains is seeking approval of both projects, but it is unclear whether both will be built.
Missouri | Kansas City Power & Light, Hawthorn Power Station | Kansas City (Jackson) | Installation of a 570 MWe pulverized PRB coal and gas-fired boiler (Unit 5, completely rebuilt following catastrophic explosion of existing unit), with SCR, dry scrubber, and baghouse | 570 | May '99 | 1999-07-06 | 1999-08-17 | NOx, CO, PM10, SO2, Pb, VOC | 08/99 | 08/99 | 05/01 | Final... NOx: 0.08 #/mmBtu (30-day), 0.10 #/mmBtu (24-hr), SO2: 0.12 #/mmBtu (30-day), 0.13 #/mmBtu ( 3-hr)PM-10: 0.018 #/mmBtu, VOC: 0.0036 #/mmBtu, CO: 0.16 #/mmBtu, Pb: 0.6 ton/yr; 112(g) not applicable to plant since final permitting action preceded December 20, 2000 HAP finding. | NOx-SCR, CO-cc, PM10-FF, SO2-DLS, Pb-FF, VOC-cc | NOx-(530), SO2-(3795), CO-4136, PM10-359, VOC-66, H2SO4-(1), Pb-0.6 |  | MDNR-KCMO | Jeff Creason (816) 513-6167 | PSD triggered for all pollutants because of state's dual source definition, despite large reductions in NOx and SO2 emissions.
Missouri | Great Plains Power, Weston Bend Generating Station (colocated at existing KCPL, Iatan Station) | Weston (Platte) | Installation of one opposed-wall, dry-bottom boiler combusting low sulfur Wyoming subbituminous coal and oil (rated 8,100 mmBtu/hr) | 820 | Nov '01 |  | Currently Under Review | NOx, CO, PM10, SO2, VOC |  |  |  | Proposed in Application.... SO2 (0.12,30d); NOx (0.08, 30d); CO (0.16, 3h?); PM10 (0.018,3h?); VOC (0.0036,3h?); | NOx-SCR, CO-cc, PM10-FF, SO2-DLS/SDA (with PRB coal), Pb-FF, VOC-cc | NOx-2838, SO2-4257, CO-5676, PM10-639, VOC-128, Pb-0.59 |  | MDNR | Kyra Moore (573) 751-4817 | Identical project also proposed for Great Plains Atchison (KS). At this point, Great Plains is seeking approval of both projects, but it is unclear whether both will be built.
Missouri | City Utilities of Springfield, Southwest Power Station | Springfield (Greene) | Construction of a new 275 MW pulverized coal (low sulfur western subbituminous) utility boiler and associated equipment | 275 | April '03 | 2003-05-01 | 2004-12-15 | NOx, CO, PM10, SO2, VOC |  |  |  | Final.... SO2 (0.095,30d); NOx (0.08, 30d); CO (0.16, 3h); PM10 (0.018,3h); VOC (0.0036,3h); H2SO4 (1.84e-4,3h); Pb (2.56e-5) | NOx-SCR, CO-cc, PM10-FF, SO2-DLS/SDA (with PRB coal), Pb-FF, VOC-cc | 'NOx-954, SO2-1143, CO-1909, PM10-244, VOC-43, Pb-0.31, H2SO4-2.2, Hg-.090, Pb-0.31, HCl-8.84, HF-4.47 |  | MDNR | Kyra Moore (573) 751-4817 | Synthetic minor limits taken to avoid 112(g) HAP review; HAP limits are Hg (7.5e-6#/mmBtu); HCl (0.00073#/mmBtu); HF (0.00037#/mmBtu)
Missouri | Associated Electric Cooperative, Inc. | Norborne (Carroll) | Greenfield installation of a new 660 MW supercritical pulverized coal (low sulfur western subbituminous) utility boiler and associated equipment | 660 | September '05 (proposed)
Nebraska | Omaha Public Power District | Nebraska City | Addition of one 660 MWn (6478 mmBtu/hr) coal-fired unit at the existing Nebraska City power station. Also includes installation of 125 mmBtu/hr auxiliary boiler and 1837 hp diesel-fired emergency generator | 660 | February '04 | 2004-02-25 | 2005-03-09 | NOx, CO, PM10, SO2, VOC, H2SO4, Pb, Fluorides, HAPS | 12/05 |  | 05/09 | Final... SO2 (0.095#/mmBtu,30d); SO2 (0.163#/mmBtu, 24-h), SO2 (0.48#/mmBtu,3-h), H2SO4 (0.0042#/mmBtu, NOx (0.07#NOx/mmBtu, 30d, following 18-mo optimization, interim 0.12), CO (0.16#/mmBtu, RM-average), PM10 (0.018#/mmBtu, F+C, RM-average), VOC (0.0034#/mmBtu), Fl (0.0004#/mmBtu, RM-average), Hg-18e-6 #/MWhr(1.98#/TBtu) | NOx-SCR-LNB, CO-cc, PM10-FF, SO2-DLS/SDA (with PRB coal), Pb-FF, VOC-cc, Hg-MACT | NOx-2002, SO2-2697, CO-4544, PM10-538, VOC-96.9, Pb-0.12, H2SO4-119.2, Flourides-11.3, Hg-0.06, Total HAPs-55.4 |  | NDEQ | Clark Smith (402) 471-4204 | see http://www.oppd.com/news/news.htm#Explore
Nebraska | Municipal Energy Agency of Nebraska (colocated at existing City of Hastings, Gerald Whelan Energy Center) | Hastings | Addition of one 220 MW (2,210.5 MMBTU/hr) pulverized coal dry bottom boiler, 74 MMBTU/hr auxiliary boiler, diesel-fired 800 kW emergency generator, 50 hp diesel-fire fire pump | 220 | Oct '02 | Oct '02 | 2004-03-30 | NOx, CO, PM10, SO2, Fluorides |  |  |  | SO2 (0.12 #/mmBtu,30d); NOx (0.08 #/mmBtu, 30d); CO (0.15 #/mmBtu, 3h); PM10 (0.018 #/mmBtu,3h); Fluorides (0.0004 #/mmBtu) | NOx-SCR, CO-cc, PM10-FF, SO2-DLS/SDA (with PRB coal), Pb-FF, VOC-cc, Fl (DLS-FF) | NOx-1164, SO2-1162, CO-1550, PM10-199, PM-222, VOC-36 |  | NDEQ | Clark Smith (402) 471-4204 | see http://www.nmppenergy.org/hastingsengineers.htm; project non-major for 112(g) so no limits established for HAPs
EPA Region 8
Colorado | Tri-State Generation and Transmission Association | Southeastern Colorado | 1200 MWe. | [14 empty] | see http://denver.bcentral.com/denver/stories/2001/03/12/story1.html, http://www.denverpost.com/Stories/0,1002,11%257E25323,00.html
Colorado | Colorado Springs Utilities | Colorado Springs (El Paso) | Addition of one 150 MW Circulating Fluidized Bed coal combustion boiler with fully integrated, multi-layered emission controls to produce what is predicted to be the cleanest coal plant in the world. Will demonstrate fuel flexibility for western & eastern coals, as well as waste coals. | 150 | Preapplication meeting only. | [12 empty] | http://www.netl.doe.gov/coalpower/ccpi/proposal-pdf/cosprabs.pdf
Colorado | Xcel Energy, Comanche Station | Pueblo (Pueblo) | Addition of Unit 3, an approximately 750 MW super critical pulverized coal boiler to the existing Comanche Station. | 750 | 9/10/2004 Revised 1/19/05 | 9/16/2004 Revised 1/24/05 | 2005-07-05 | PM/PM10, SO2, NOx, VOC, CO, Pb, SAM, Fluorides, HF, TRS, RSC, Hg |  |  |  | PM10 (filt) - 0.012 , PM (filt) - 0.013, PM10 (total) - 0.02, PM (total) - 0.022 (three test runs); CO - 0.13 (8-hr ave; Limit is 0.3 during Startup/shutdown); VOC - 0.0035 (three test runs); HF - 0.00049 (three test runs); SAM - 0.0042 (three test runs); "BACT Equivalent" Limits per Settlement Agreement (state did not determine as BACT): NOx - 0.08 (30 d.r.a.); SO2 - 0.1 (30 d.r.a.); [all limits in lb/MMBtu] | PM/PM10 - pulse jet baghouse; NOx - SCR; SO2 - dry FGD, CO/VOC - combustion control; HAPs - cobenefit control & sorbent injection for Hg. | PM (total)- 703, PM10 (total)- 638, SO2 - 3,250, NOx - 2600, CO - 4,876, VOC - 119, Lead - 0.07, SAM - 110, Flourides/HF - 15.9, TRS - 24.0, RSC - 24.0, HAPs - 42.5. Note that application proposes reductions in SO2 and NOx from Units 1 and 2 to offset Unit 3 increases. |  | Colorado Dept Public Health & Environ. | Jackie Joyce | The permit application nets out of PSD for NOx and SO2 by adding controls to existing units. BACT Limits Proposed (lb/MMBtu): PM Total (0.022, 3-hr), PM Filt (0.015, 3-hr), PM10 Total (0.020 3-hr), PM10 Filt (0.013, 3-hr) SO2 (0.1, 30-day; Not BACT - net out), NOx (0.08, 30-day, Not BACT - net out), CO (0.15 no ave), VOC (0.0037 no ave), SAM (0.0029 no ave), HF (0.0005, 3-test runs), Hg (20.0*10E06 lb/MWh). Ave. Coal Characteristics: 8,200 Btu/lb; 0.287 %wt S; 5.75% ash content.
Colorado | Lamar Utilities Board (Lamar Light & Power) | Lamar (Prowers) | Replacing an existing 25 MW natural-gas fired utility boiler with one 44 MW coal-fired CFB unit burning western subituminous or bituminous coal. Known as Lamar Repowering Project. | 44 | 2005-01-12 | 2005-08-15 | [6 empty] | PM/PM10 - baghouse; NOx - SNCR (netting out of PSD); SO2 - limestone injection, CO - combustion control; PSD not triggered for VOC, Pb, H2SO4, H2S, or TRS | PM (total)- 46, PM10 (total)- 46, SO2 - 226, NOx - 45 decrease, CO - 293, VOC - 10, Lead - 0.02, SAM - 3, Note that the application proposes reductions in NOx by replacing existing natural gas unit. |  | Colorado Dept Public Health & Environ. | Ram Seetharam | The permit application nets out of PSD for NOx by replacing the existing unit and controlling emissions from the new unit. PSD not triggered based on increases in VOC, lead, H2SO4, H2S, or TRS. BACT Limits Proposed (lb/MMBtu): PM/PM10 Total (0.035, compliance test), PM/PM10 Filt (0.015, compliance test), SO2 (0.103, Daily ave), CO (0.15, no ave, 0.3 during Startup/Shutdown). Ave. Coal Characteristics: 8,725 Btu/lb; 0.45 %wt S; 5.7% ash content.
Montana | Composite Energy, Bear Creak |  |  | 2000 | [13 empty] | see http://www.epsa.org/competition/index.cfm?section=competition
Montana | Bull Mountain Development Company, No.1, LLC. | Roundup (Musselshell) | The Power Plant will consist of two coal-fired generating units and auxiliary equipment. Each unit will have a pulverized coal-fired boiler and steam turbine-generator with a gross electrical output of 390 MW. Pollution controls: dry FGD, SCR, and pulse jet baghouse. | 780 | 2002-01-16 |  | 2003-07-21 | CO, NOx, PM, PM10, Pb, SOx, VOC, HAP |  |  |  | PM10 (filt) - 0.015 (source test - submit emissions for consideration of lowering to 0.012 after 18 mo); NOx - 0.07 (24-hr ave) & 0.1 (1-hr ave); SO2 - 0.15 (1-hr ave) & 0.12 (24-hr ave); CO - 0.15 (source test); VOC - 0.003 (no ave); SAM - 0.0064 (sour | PM/PM10 - pulse jet baghouse; NOx - SCR; SO2 - dry FGD; CO/VOC - combustion control. | PM/PM10 - 508, SO2 - 3939, NOx - 2329, CO - 4917, VOC - 99, Lead - 0.2, SAM - 113, HAPs - 91 | Dry FGD - $390/ton | Montana Dept Environ. Quality | David Klemp | Coal characteristics (ave): 9,232 Btu/lb; 1.0% wt S
Montana | Rocky Mountain Power, Inc. (Bison) | Hardin, Montana | Pulverized coal-fired boiler (1968 vintage) with a heat input of up to 1,304 MMBtu/hr to produce up to 900,000 pounds of steam pounds per hour. | 113 116 | 2002-01-31 |  | 6/11/2002 Revised 12/22/004 | CO, NOx, PM10, SOx, VOC, H2SO4, HCl, HF, and Hg |  | 2004 |  | PM/PM10 (filt) - 0.012 (source test); PM/PM10 (cond) - 0.024; NOx - 0.09 (30-day ave); SO2 - 0.14 (1-hr ave, increment) & 0.11 (30-day ave, BACT); CO - 0.15 (source test); VOC - 0.0034 (no ave) SAM - 0.0063 (1-hr); HCl - 0.00118; HF - 0.00051; All limits in lb/MMBtu. Hg - 5.8 lb/Tbtu (1 hr ave) | PM/PM10 - multiclone & wet venturi scrubber, baghouse; NOx - SCR; SO2 - wet venturi scrubber dry scrubber; CO/VOC - combustion control. | PM/PM10 - 69 (filt), 137 (cond), SO2 - 628, NOx - 514, CO - 857, VOC - 19 | SCR - $355/ton | Montana Dept Environ. Quality | David Klemp | Coal characteristics (ave): 9,993 Btu/lb; 0.94% wt S. 12/04 revision to permit to change PM/SO2 emission control equipment originally proposed to baghouse and dry scrubber. BACT limits were revisited for these pollutants only.
North Dakota | Great River Energy |  | Applied for some funding under ND's Lignite Vision 21 Project | 500 | [13 empty] | see http://www.epsa.org/competition/index.cfm?section=competition, http://www.greatriverenergy.com/HTML/press/pre_01_Vision21.htm Project not moving forward.
North Dakota | Montana-Dakota Utilities, Westmoreland Power Inc. | Gascoyne (Bowman) | New power plant consisting of one circulating fluidized bed boiler burning lignite from an adjacent mine with the following pollution controls: fabric filter baghouse, selective non-catalytic reduction (SNCR), dry lime scrubber with limestone injection. | 175 | 4-May-2004 & 3-Feb-2005 | 2005-04-04 | 2005-06-02 | PM/PM10, NOx, SO2, VOC, CO, SAM, H2SO4, HF, HCl |  |  |  | PM10 (filt) - 0.013 (3-hr avg); PM10(filt& cond) 0.0167 (3-hr avg); PM (filt) - 0.0167 (3-hr avg); NOx - 0.865 lb/MWe-hr gross (30 d.r.a.) ; SO2 - 0.038 (30- d.r.a.); CO - 0.154(3-hr avg); VOC - 0.005 (3-hr avg) ; Opacity 10% (6 min avg); H2SO4 0.0061 (3-hr avg); HF 0.00053 (3 hr avg); HCL 9.9 tpy (m.r.t.); [Lignite Characteristics (design): 5,680 Btu/lb; 1.067% wt S; 14.1% ash content] | PM/PM10 - baghouse (w/ Ryton bags); NOx - SNCR; SO2/H2SO4/HF/HCL - limestone injection & spray dryer; CO/VOC - combustion control. | PM10 - 139, NOx - 833, SO2 - 347, VOC - 25, CO - 1424, Lead - 0.015, HAPs - 19 | SNCR - $2926/ton; baghouse - $38/ton; | North Dakota Depart. of Health | Tom Bachman | BACT Limits Proposed (lb/MMBtu): PM10 (0.015 3-hr rolling ave), SO2 (0.038 30-day rolling ave), NOx (0.09 30-day rolling), CO (0.15 no ave), VOC (0.005 no ave), SAM (0.0029 no ave). [Lignite Characteristics (design): 5,680 Btu/lb; 1.067% wt S; 14.1% ash content]
North Dakota | Great Northern Power Development L.P./ South Heart Coal LLC, South Heart Power Project | South Heart (Stark) | New power plant and surface lignite mine (mine-mouth power plant). 500 MW baseload consisting of 2 atmoshperic circulating fluidized bed boilers fueled with lignite, obtained from the Mine and delvered to the Plant by truck. The following pollution controls have been proposed: SNCR, limestone injection and spray dry absorber flue gas desulfurization, fabric filter baghouse. | 500 | 2005-08-18 | [8 empty] | CO - 3843.1; NOx - 2278.0; PM10 - 778.0; SO2 - 971.2; VOC 62.9; PB 0.1.; H2SO4 - 103.6 | SNCR - $1690/ton; baghouse - $35/ton; CFB+ limestone injection+ spray dry absorber - $1210/ton | North Dakota Depart. of Health | Tom Bachman | BACT Limits Proposed (lb/MMBtu): PM10 (filt)(0.01 3), SO2 (0.039 ), NOx (0.09), CO (0.15 ), VOC (0.0025), H2SO4 (0.0042), [Lignite Characteristics (worst case): 5,5782 Btu/lb; 1.70% wt S; 10.79% ash]
South Dakota | Otter Tail Power Company | Milbank (Grant) | Adding one new 600 MW super-critical pulverized coal boiler to existing power plant that will be fired on PRB coal. | 600 | 2005-07-20 | 2005-08-10 | [6 empty] | PM/PM10 - baghouse; NOx - SCR (not subject to BACT); SO2 - wet scrubber (not subject to BACT; H2SO4 - wet scrubber and baghouse; CO/VOC - combustion control. | PM/PM10 (total)- 933, SO2 - 39, NOx - 39, CO - 4,262, VOC - 106, Lead - 0.5, H2SO4 - 131. Note that application proposes reductions in SO2 and NOx from Unit 1 to offset Unit 2 increases. |  | South Dakota Depart of Environ. & Nat Resources | Kyrik Rombough | BACT Limits Proposed (lb/MMBtu): PM/PM10 (total)(0.0 3, approx three-hrs for test runs), CO (0.16 , approx 3-hrs for test runs), VOC (0.0036, approx three-hrs for test runs), H2SO4 (0.005, approx three-hrs for test runs). [Coal Characteristics: Subbituminous PRB Coal - characteristics not given in application]
Utah | Intermountain Power Service Corp | Delta (Millard) | Add Unit 3 to existing power plant (pulverized coal fired) with fabric filter baghouse, low NOx burners and SCR, forced oxidation wet limestone FGD system, and combustion controls (CO & VOC). | 950 | 2002-12-09 | 2004-04-03 | 2004-10-15 | PM10, SO2, NOx, CO, VOC, lead, sulfuric acid mist, HF, TRS, RSC |  |  |  | PM (filt) - 0.013 (3 test runs); PM10 (filt) - 0.012 (3-test runs) ; PM10 (total) - 221 lb/hr (0.024 lb/MMBtu equiv - 24 hr block); NOx - 0.07 (30-day); SO2 - 0.10 (24-hr) & 0.09 (30-day); CO - 0.15 (30-day); VOC - 0.0027 (3 test runs); SAM - 0.0044 (24-hr block); Hg (bituminous) - 6.0 E-06 lb/MWhr (12-mo roll); Hg (subbituminous) - 20 E-06 lb/MWhr); Fluorides/HF - 0.0005 (3 test runs); Lead - 0.00002 ( 3 test runs) | PM/PM10 - Fabric filter baghouse; NOx - SCR; SO2 - wet FGD; CO/VOC - combustion control; HAPs - cobenefit controls | PM10 - 496.5, SO2 - 3,568, NOx - 2775, CO - 5,946, VOC - 107, Lead - 0.7, SAM - 174, HF - 20, TRS - 29, RSC - 29, HAPs - 198 |  | Utah Division of Air Quality | Milka Radulovic | BACT Limits Proposed (lb/MMBtu): PM10 (0.015 3-hr rolling ave), SO2 (0.10 30-day rolling ave), NOx (0.07 30-day rolling), CO (0.154 no ave), VOC (0.0027 no ave), lead (0.00002 no ave), HF (0.001 no ave), SAM (0.027 no ave). Coal Characteristics (design worst-case): 11,193 Btu/lb; 0.75% wt S (calendar year ave); 12.0% Ash
Utah | NEVCO Energy | Sevier (Sevier) | New power plant consisting of one circulating fluidized bed boiler with the following pollution controls: fabric filter baghouse, selective non-catalytic reduction (SNCR), dry lime scrubber with limestone injection, combustion controls (CO). | 270 | 2003-09-10 | 2004-03-05 | 2004-10-12 | PM10, SO2, NOx, CO |  |  |  | PM/PM10 (filt) - 0.0154 (24-hr); NOx - 0.1 (24-hr); SO2 - 0.05 (24-hr) & 0.022 (30-day); CO - 0.115 (1-hr); VOC - no limit; SAM - 0.0024 (24-hr); Hg - 4.0 E-07 (M29l); Fluorides - 0.00019 (M13A); HF - 0.005 (M26A); Lead - 0.0000113 (M12 or M29); HCl - 4.01 lb/hr (M26A) | PM/PM10 - Baghouse with bag leak detectors; NOx - SNCR; SO2 - dry lime scrubber; CO/VOC - combustion control; HAPs - cobenefit controls | PM/PM10 - 177.4, SO2 - 233.9, NOx - 1,067, CO - 1,279, VOC - 53, Lead - 0.12, SAM - 26, HF - 2, HAPs - 23 |  | Utah Division of Air Quality | John Jenks | BACT Limits Proposed (lb/MMBtu): PM10 (0.016 no ave), SO2 (0.022 annual ave based on 0.4% S in coal; 0.05 on short-term ave based on 0.9% S coal), NOx (0.10 no ave), CO (0.12 no ave), VOC (0.005 no ave). No VOC limit was established, although VOC emissions greater than significance levels. Ave Coal Characteristics: 11,390 Btu/lb; 0.4 wt% S; 8.3% Ash
Utah | PacifiCorp - Hunter | Castle Dale (Emery) | Add Unit 4 to existing power plant (pulverized coal fired) with fabric filter baghouse, low NOx burners and SCR, and forced oxidation wet lime scrubber system, and combustion controls (CO & VOC). | 575 | 2003-11-14 |  |  | PM, PM10, SO2, NOx, CO, VOC, lead, SAM, HF, TRS, RSC | [5 empty] | PM10 - 343, SO2 - 1348, NOx - 1645, CO - 3656, VOC - 61, Lead - 0.4, SAM - 4.3, HF - 8.4, TRS - 9.9, RSC - 9.9, HAPs - ~ 45 |  | Utah Division of Air Quality |  | BACT Limits Proposed (lb/MMBtu) (Note that there are no proposed BACT limits for SO2 and NOx, as the application nets out of PSD for these pollutants. There are also no BACT limits for lead or sulfur compounds.): PM10 (0.015), SO2 (0.10 30-day rolling ave)
Utah (Tribal Land) | Deseret Generation & Transmission - Bonanza | Bonanza (Uintah) | Add one circulating fluidized bed boiler (waste coal) to existing power plant with fabric filter baghouse, selective non-catalytic reduction (SNCR), limestone injection, dry scrubber, and combustion controls (CO and VOC). | 110 | 2004-04-14 |  |  | PM, PM10, SO2, NOx, CO, SAM, and HF. |  |  |  |  | PM/PM10 - Baghouse; NOx - SNCR; SO2 - limestone injection & dry lime scrubber; CO/VOC - combustion control; HAPs - cobenefit controls | PM/PM10 (total) - 326, SO2 - 352, NOx - 552, CO - 949, VOC - 32, Lead - 0.0177, SAM - 31, Be - 0.0008, HAPs - 246.2 |  | EPA Region 8 | None - Mike Owens (R8) | BACT Limits Proposed (lb/MMBtu): PM/PM10 (0.017/0.012, filterable no ave), PM10 total (0.052, no ave), SO2 (0.055, 30-day rolling), NOx (0.088 30-day rolling ave), CO (0.15 no ave), VOC (0.005 no ave), SAM (0.005 no ave).
Wyoming | Independent Energy Group of Black Hills Corporation @ Wygen Unit 1 | Gillette | Pulverized coal fired Electric Generating Plant | 80 | 1996-06-04 | 1996-06-04 | 1996-09-06 | SO2, NOx, CO, VOCs, |  |  |  | PM(filt): 0.02, SO2:0.20(2-hr rolling), 0.17 (30-day), NOx: 0.22(30-day rolling), 0.2(365-day rolling), CO: 0.15, 0.015 | PM-ESP, NOx-LNB/OFA, SO2-CDS, VOC/CO-Combustion control | PM-89, SO2-755, NOx-888, CO-666,VOCs-67 |  | WDEQ | Bernard J. Daley | see http://www.babcock.com/pgg/pr/wygen.html
Wyoming | Black Hills Power and Light (WYGEN 2) | Gillette | Pulverized Coal Fired Electric Generating Plant | 500 | 2002-04-26 | 2002-05-06 | 2002-09-26 | CO, NOx, PM,PM10, PB,SOx,VOC,HAP |  |  |  | PM/PM10 (filt): 0.012 (source test); SO2: 0.1 (30-day ave) 0.15 (3-hr block); NOx: 0.07 (30 day); CO: 0.15 (source test), VOC: 0.01 (source test). Limits in lb/MMBtu. | PM10 - multiclone & wet venturi scrubber; NOx - SCR; SO2 - Spray dryer/absorber; CO/VOC - combustion control. | PM/PM10 - 270, SO2 - 2254, NOx - 1578, CO - 3381, VOC - 225, SAM - 104, HAPs - 110 | Spray Dryer - $569/ton; SCR - $4100/ton | Wy Dept of Environ. Quality | Bernard J. Daley | PRB Coal Characteristics (design): 7,950 Btu/lb; 1.0% wt S
Wyoming | North Amercian Power Group | Wright |  | 274 | [13 empty] | see http://www.epsa.org/competition/index.cfm?section=competition
Wyoming | Ziegler Coal Holding | Wright |  | 240 | [13 empty] | see http://www.epsa.org/competition/index.cfm?section=competition
EPA Region 9
Arizona | Unisource Energy @ Tuscon Electric's Springerville Station | Tucson | 2 - 360 MW units, final committment to procede, July 2001, online 2004 and 2005 | 720 | [13 empty] | see http://www.tucsonelectric.com/News/NewsReleases/2001/UNS010201.htm
New Mexico (Navajo) | Sithe Global - Desert Rock Energy Facility | 25 miles SW of Farmington, NM | 2 x 750 MW greenfield, mine mouth plant | 1500 | 2004-02-25 | [6 empty] | NOx (0.06 lb/mmbtu, 24-hr), CO (0.10 lb/mmbtu, 24-hr), SO2 (0.06 lb/mmbtu, 24-hr), VOC (0.03 lb/mmbtu), PM10 (0.02 lb/mmbtu) | NOx - LNB and SCR, SO2 - limestone wet FGD, PM - baghouse | NOx - 3,315, CO - 5,526, PM10 - 1,105, SO2 - 3,315, VOC - 162, Lead - 0.59 |  | Region 9 |  | Located on Navajo reservation
New Mexico (Navajo) | BHP Billiton - Cottonwood Energy Center | Four Corners area, NM | One 550 MW coal-fired sub-critical boiler, 495 net. | 495 | 2004-03-23 | [6 empty] | NOx (0.06 lb/mmbtu), CO (0.14 lb/mmbtu), SO2 (0.06 lb/mmbtu), VOC (0.0072 lb/mmbtu), PM10 (0.02 lb/mmbtu) | NOx - LNB and SCR, SO2 - limestone wet FGD, PM - baghouse | NOx - 1,351, CO - 3,139, PM10 - 464, SO2 - 1,350, VOC - 162, Lead - 0.59 |  | Region 9 |  | Competitor of Desert Rock. Only one will be built. Application on hold.
California | None
Hawaii | None
Nevada | Duke Energy | (White Pine) | 2 - 650 MW coal-fired units |  | Conceptual
Nevada | LS Power | White Pine area near UT border | 1600 MW | 1600 | Conceptual | [7 empty] | dry scrubbing for SO2 |  |  | NDEP |  | Application not submitted yet.
Nevada | Sempra Energy - Granite Fox Power | Gerlach (Washoe) | 1450 MW greenfield plant | 1450 | [11 empty] | NDEP |  | Application withdrawn. Resubmittal expected in last quarter of 2005
Nevada | Newmont Mining, TS Power Plant | Eureka County | 200 MW pulverized coal-fired boiler (four oil-fired combustion turbines to be used for back-up power). | 200 | 2004-10-01 | 2004-11-09 | 2005-05-05 |  |  |  |  | NOx (0.067 lb/MMBTU, 24-hr rolling average); CO (0.15 lb/MMBTU, 24-rolling average); SO2 (0.09 lbs/MMBTU 24-hr rolling average & 95% control when sulfur content > 0.45%; 0.065 lbs/MMBTU 24-hr rolling average & 91% control when sulfur content < 0.45%); PM/PM10 0.012 lbs/MMBTU (24-hr rolling average) | Low-NOx burners and SCR; combustion controls; Low-sulfur coal and Dry Scrubber; fabric filters | PM10 - 87, SO2 - 194, CO - 316, Nox - 234, VOC - 12, Lead - 0.02, |  | NDEP |  | Appeal filed with EAB by ACE on 6/3/05
Nevada | Touquop Energy Project | Mesquite (Clark County) | 750 MW | 750 | [11 empty] | NDEP |  | Application not submitted yet.
American Samoa | None
Guam | None
EPA Region 10
Alaska | Arctic Slope Regional Corporation | Point Lay (North Slope Borough) | Greenfield coal-fired power plant at mine mouth. | [14 empty] | Applicant is developing meteorological monitoring network in preparation for PSD permit application.
Alaska | Golden Valley Electric Association | Healy (Denali Borough) | Retrofit existing Department of Energy Clean Coal Technology pulverized coal boiler to a conventional system. The boiler has been idle since 1999. | 50 | None submitted | [10 empty] | ADEC |  | On March 19, 2004, GVEA made an offer to purchase Healy Unit 2 from Alaska Industrial Development and Export Authority. On July 3, 2004, GVEA withdrew its offer after AIDEA announced it was rejecting the offer in a July 23 meeting. AIDEA is pursuing other partners for this project.
Idaho | Sempra Energy Resources | Jerome (Jerome County) | Idaho Valley Energy. Conventional coal-fired power plant. | 600 | None submitted | [10 empty] | IDEQ | Mike Simon (IDEQ) @ 208.373.0212 | http://www.mountainhomenews.com/story/1065754.html http://www.sempra.com/news_performance2005Q2_IdahoValley.htm
Idaho | Mountain Island Energy LLC | Soda Springs (Caribou County) | IGCC | 600 | None submitted | [10 empty] | IDEQ | Mike Simon (IDEQ) @ 208.373.0212 | http://www.journalnet.com/articles/2005/05/04/news/local/news04.txt
Idaho | Undetermined | Idaho Falls (Bonneville County) | Coal-fired power plant retrofit of shutdown boiler at the Idaho National Laboratory. | 50 | None submitted | [10 empty] | IDEQ | Mike Simon (IDEQ) @ 208.373.0212 | Regional Development Alliance is hoping to secure the rights to a Department of Energy coal-fired power plant at the Idaho National Laboratory. The plant has been shutdown since 1999. The organization would lease the boiler from the DOE, and a subcontractor would operate the plant.
Idaho | Undetermined | Shoshone-Bannock Reservation outside Pocatello (Bannock) | Coal-fired power plant using PRB coal | 550 | None submitted | [10 empty] | EPA |  | Governor of Idaho has formed a task force (Idaho Optimum Initiative) to evaluate the development of the old FMC (elemental phosphorus) industrial site. Plans to construct both a coal-fired power plant and an ethanol plant are being discussed. http://www2.state.id.us/gov/mediacenter/press/pr02/prdec02/Pr_132.htm
Idaho | Southeast Idaho Energy LLC | Power County and Fort Hall Indian Reservation outside Pocatello | IGCC | 520 | None submitted |  |  |  | 2007-01-01 |  | 2010-01-01 |  |  |  |  | IDEQ / EPA | Mike Simon (IDEQ) @ 208.373.0212 and Dan Meyer (EPA) @ 206.553.4150 | FutureGen Research Project Proposal. IDEQ responsible for permitting of IGCC on state land, and EPA responsible for permitting of coal handling on Fort Hall Indian Reservation. Governor of Idaho has formed a task force (Idaho Optimum Initiative) to evaluate the development of the old FMC (elemental phosphorus) industrial site. Plans to construct both a coal-fired power plant and an ethanol plant are being discussed. http://www2.state.id.us/gov/mediacenter/press/pr02/prdec02/Pr_132.htm http://www.journalnet.com/articles/2005/03/13/news/local/news01.prt http://www.journalnet.com/articles/2005/03/13/news/local/news02.prt http://www.ioi-online.org/
Oregon | Portland General Electric | Boardman (Morrow) | Additional coal-fired power generation at existing coal-fired power plant. | [14 empty] | New project is speculation at the moment.
Oregon | PacifiCorp | ? | ? | 500 | None submitted | [10 empty] | ODEQ |  | http://www.netl.doe.gov/coalpower/oces/pubs/ncp.pdf
Washington | Composite Power | Richland (Benton County) | Develop former Washington Public Power Supply System sites 1&4. | 2500 | None submitted | [10 empty] | EPA & WA EFSEC |  | Permitting authority has not been contacted by the developer. http://www.compositepower.com/index.html
Washington | US Electric Power | Blaine (Whatcom County) | Earliest on-line projection is April 2004. | [14 empty] | http://archives.seattletimes.nwsource.com/cgi-bin/texis/web/vortex/display?slug=coal23m&date=20010323&query=us+electric+power, http://www.globaltexinc.com, http://www.uselectricpower.com, US Electric Power plans to partially offset CO2 emissions with in-state reforestation project, Size of project likely to increase to 349 MW as State of Washington Energy Facility Site Evaluation Council raises applicability threshold from 250 MW to 350 MW.
Washington | Energy Northwest | Western WA | IGCC | 600 | None submitted | [10 empty] | EPA & WA EFSEC | Dan Meyer (EPA) @ 206.553.4150 and Irina Makarow (EFSEC) @ 360.956.2047 | http://www.tri-cityherald.com/tch/local/story/6754756p-6642957c.html
Total |  |  |  | 54301
STRIKE THROUGH
means project no longer being evaluated
at this time