FOAM – IT’S ALL ABOUT WATER

ESSENTIALS FOR ORGANIZING A MUTUAL AID FOAM PROGRAM

REFERENCES

NFPA 11   STANDARD FOR LOW-, MEDIUM-, AND HIGH-EXPANSION FOAM 2005 EDITION

NFPA 16   STANDARD FOR THE INSTALLATION OF DELUGE FOAM – WATER SPRINKLER AND FOAM -- WATER SPRAY SYSTEMS—2003 EDITION

NFPA 30   FLAMMABLE AND COMBUSTIBLE LIQUIDS CODE- 2000  EDITION

UNDERWRITERS LABORATORIES INC.  DIRECTORY – FIRE                   PROTECTION EQUIPMENT 2007– LISTINGS AND                                CLASSIFICATIONS—2007

AFFF RESPONSE AND COMMUNITY MUTUAL AID AGREEMENTS

30th ANNUAL AIRPORT CONFERENCE

FEDERAL AVIATION ADMINISTRATION

MARCH 6 – MARCH 8th, 2007

HERSHEY, PA

WILLIAM C. TAMBURRO, Sr. CFPS – PRESIDENT

THE TAMBURRO GROUP INC

WEST CHESTER, PA

ORGANIZING A MUTUAL AID FOAM PROGRAM BEGINS WITH RECOGNIZING AND RECORDING DETAILS OF VARIOUS FLAMMABLE / COMBUSTIBLE HAZARDS THAT ARE LOCATED WITHIN THE JURISDICTIONAL AREA. THE AREA IS TO BE TREATED AS ONE HUGE POTENTIAL HAZARDOUS SITE. DEVELOP FOAM REQUIREMENTS BASED UPON THE SINGLE WORSE HAZARD IN THE AREA.

FOLLOWING ARE SOME TYPICAL HAZARDOUS SITES. THE LIST IS FAR FROM            COMPLETE:

- BULK STORAGE TANK FARMS—PETROLEUM / CHEMICAL

- TANK TRUCK LOADING / UNLOADING RACKS

- TANK TRUCK OVER THE ROAD TRAFFIC

- WAREHOUSES STORING VARIOUS SIZE CONTAINERS OF

PETROLEUM / CHEMICAL AND PHARMACEUTICAL 
			           PRODUCTS

- RAILROAD TANK CAR / LOADING / UNLOADING RACKS

- MARINE DOCKS

- BUILDING HEATING FUEL OIL TANKS—ABOVE / BELOW

GROUND

- BUILDING HEATING FUEL OIL TANKS / TANK TRUCK

UNLOADING SITE

- INDUSTRIAL RUG CLEANING AND RECLAIMATION PLANTS

- MUNICIPAL WASTE DISPOSAL PLANTS

- TIRE DUMP SITES

- SPILL AREAS / DIKED / NON-DIKED

- AIRCRAFT HANGARS / MAINTENANCE AREAS / SHOPS

THE ABOVE REFERENCE MATERIAL WILL ASSIST THE ORGANIZERS.

WHEN RESPONDING TO A CLASS “A” TYPE FIRE, AN EVALUATION IS MADE TO DETERMINE THE ESSENTIALS REQUIRED TO GAIN TOTAL EXTINGUISHMENT. THE PROCEDURE IS UNCHANGED WHEN CONFRONTED WITH A PETROLEUM / CHEMICAL SITUATION USING FOAM.

THE REFERENCED FAA PAPER’S OPENING STATEMENT, PROVIDES AN UNDERSTANDING AS TO WHY PLAIN WATER IS UNSATISFACTORY FOR THE CURRENT PURPOSE.  HOWEVER, THE ADDITION OF A FOAM CONCENTRATE TO THE WATER, CONVERTS IT TO A USEFUL PURPOSE. EACH GENERATED FOAM BUBBLE CONTAINS MORE THAN 90% WATER, IN THE FORM OF FOAM SOLUTION. THE FOAM BUBBLE IS TRANSPORTING FOAM SOLUTION (WATER-FOAM  CONCENTRATE MIXTURE) TO THE HAZARD. THE WATER CONTENT BEGINS ITS COOLING / EXTINGUISHING PROCESS.

FOAM EXTINGUISHMENT REQUIRES THREE ESSENTIALS, I.E;

CONTROL, EXTINGUISHMENT AND NO-REIGNITION.

THIS IS ACCOMPLISHED WHEN A MINIMUM FOAM SOLUTION GPM PER SQUARE FOOT, IS APPLIED OVER THE ENTIRE FUEL SURFACE. THE PROCESS IS KNOWN AS THE “FOAM SOLUTION APPLICATION RATE”.

WHEN SURVEYING HAZARDOUS SITES, RECORD LOCATIONS FOR WATER SOURCES. DETERMINE THE QUANTITY PUMPERS REQUIRED TO FLOW THE WATER TO THE FOAM OPERATION SITE. NURSE TRAILERS, TOTE TANKS, DRUMS AND PAILS ARE SOURCES FOR FOAM CONCENTRATE SUPPLY. DETERMINE THE DESPOSAL SITE FOR EMPTY CONAINERS.

NOTES: POLAR SOLVENTS (WATER SOLUBLE) ARE MORE DISTRUCTIVE TO FOAM BLANKETS THAN HYDROCARBONS. FOAM SOLUTION APPLICATION RATES ARE ESTABLISHED BY APPROVAL AGENCIES, UL, USCG AND FEDERAL GOVERNMENT. THE FACTORS  AFFECTING THESE RATES INCLUDE: FOAM CONCENTRATE TYPE, POLAR SOLVENT OR HYDROCARBON FUELS AND  METHOD OF FOAM APPLICATION. CONSULT APPROPRIATE APPROVAL AGENCY AND/OR FOAM CONCENTRATE MANUFACTURER FOR RATES.

TEST CASE: SPILL AREA INVOLVING GASOLINE. ESTIMATED AREA 5,000 SQ FT.  FOAM CONCENTRATE 3% AFFF, PORTABLE APPLICATION, CONSERVATIVE FOAM SOLUTION APPLICATION RATE - 0.2 GPM / SQ. FT. X 5,000 SQ. FT. = 1,000 GPM FOAM SOLUTION X 3% = 30 GPM FOAM CONCENTRATE X  15 MINUTES MINIMUM OPERATING TIME = 450 GALLONS FOAM CONCENTRATE REQUIRED.

EVALUATION OF FIXED FOAM SYSTEMS

- MUST COMPLY WITH APPLICABLE NFPA STANDARDS #11, #16 OR #30.

- NFPA #11, CHAPTERS #10 & #11, (READ BOTH CHAPTERS) RECOMMEND AN ANNUAL INSPECTION, TEST AND MAINTENANCE BY A QUALIFIED EXPERIENCED PERSON. THE INSTALLATION IS A FOAM SYSTEM AND TESTED AS SUCH. RECEIVE A COPY OF THE REPORT. CORRECT PROBLEM AREAS.

- OPERATING INSTRUCTIONS SHOULD BE WALL MOUNTED NEAR THE SYSTEM SITE WITH A SECOND COPY ON FILE. THIS IS IMPORTANT FOR NUMEROUS OBVIOUS REASONS.

- OBTAIN THE MANUFACTURER’S OPERATING AND MAINTENANCE MANUAL.

- ANNUALLY FOAM CONCENTRATE SHALL BE CHEMICALLY ANALYZED BY A QUALIFIED AND RECOGNIZED LABORATORY. STORED FOAM CONCENTRATE SHALL MEET DESIGN REQUIREMENTS.

- LOCAL FIRE CODES SHOULD MANDATE NOTIFICATION OF NEW CONSTRUCTION AND/OR MODIFICATIONS TO EXISTING FOAM SYSTEMS. CONE ROOF TANKS USUALLY CONTAIN HYDROCARBON COMBUSTIBLE PRODUCTS.

- CONVERSION OF THE TANK TO AN INTERNAL FLOATING ROOF, INDICATES A STORED PRODUCT CHANGE. WILL THE EXISTING FOAM SYSTEM SUPPORT THE MODIFICATION? NOTE GASOLINE BLENDED WITH A POLAR SOLVENT REQUIRES SPECIAL CONSIDERATION REGARDING A RECOMMENDED FOAM CONCENTRATE. ITS BLENDING PROCESS PERFORMED AT TRUCK RACK RECEIVING THE POLAR SOLVENT FROM A DEDICATED STORAGE T

- IF A STORAGE TANK AND DIKE, SIMULTANEOUSLY ON FIRE, EXTINGUISH THE DIKE FIRE FIRST TO MINIMIZE DIKE’S HARDWARE DAMAGE AND REDUCE RELEASE OF PRODUCT. PROCEED WITH TANK EXTINGUISHMENT.

- COOLING WATER APPLIED TO AN UNIGNITED TANK, IN THE HOT ZONE, SHOULD BE APPROACHED WITH CAUTION. DETERMINE THE TANK’S INTERNAL PRODUCT HEIGHT, AS COMPARED TO THE ACCUMMULATED WATER HEIGHT IN ITS DIKE. IF THE PRODUCT HEIGHT IS LESS THAN THE DIKE’S WATER HEIGHT, THE TANK MAY SEPARATE FROM ITS FOUNDATION.

WILLIAM C. TAMBURRO, Sr. CFPS

THE TAMBURRO GROUP INC

WEST CHESTER, PA