Spallation Neutron Source

Interface Control Document

1.5.6.1 Ring High Level RF System

and

1.9.5 Ring Controls

105060100-IC0001-R0A

February 2002

Approvals

1.5.6.1 High Level RF System	1.9.5 Ring Control System

Group Leaders:	____________________________  	_________________________________

Alexander Zaltsman			John Smith

Spallation Neutron Source

Interface Control Document

Ring High Level RF System

and

Integrated Control System.

Prepared by

Johnny Tang (Editor)

Brookhaven National Laboratory

SNS Project

UT-Battelle, LLC

managing

Spallation Neutron Source activities at

| Argonne National Laboratory | Brookhaven National Laboratory |
| --- | --- |
| Thomas Jefferson National Accelerator Facility | Lawrence Berkeley National Laboratory |
| Los Alamos National Laboratory | Oak Ridge National Laboratory |

under contract DE-AC05-00OR22725

for the

U.S. Department of Energy

CONTENTS

1. Scope	5

2. Overview	5

3. VME Interface Options	5

3.1. Blue Hose Interface	5

3.2. Ethernet Interface	5

3.3 ControlLogix gateway	6

4. Performance Requirement	6

Appendix A. Bit Definitions	11

Appendix B. Schedule	14

References	15

# Scope

This document provides the interface requirements between the Ring high level RF (HLRF) system and the Integrated Control System (ICS).

This document is intended to be a guideline for the design of SNS Ring high level RF control system.

This document may be modified as a change request to the control system. Proposed changes require Ring HLRF System and ICS review and approval.

# Overview

The Spallation Neutron Source (SNS) consists of a front-end system, a linear accelerator, an accumulator ring, and mercury target. The front-end system produces a beam of H – ions and injects it at 2.5 MeV into a following linear accelerator for further acceleration to 1 GeV. The accumulator ring has circumference of 248 meters that is designed to accumulate 2x 10 14 , 1 GeV protons in 1 ms, via charge exchange injection of H –   beam. After the accumulation, the beam is extracted using a fast kicker magnet and sent to the mercury target. The purpose of the accumulator ring RF system is to maintain a 250ns gap for the 200ns rise time of the extraction kicker while maintaining low peak beam current and large momentum spread.

The design of SNS Ring RF system is a dual harmonic system running with h=1 and h=2 which imply RF frequencies of f1 = 1.05 MHz and f2 = 2.11 MHz. Three cavities will be used for h=1 system, with two gaps per cavity and 10kV per gap. There will be one power amplifier per cavity to compensate the heavy beam loading at h=1. The h=2 RF system will consist of one cavity with two gaps at 10kV per gap, driven by a single power amplifier.

An Allen-Bradley PLC-5 will be used for SNS Ring High Level RF controls. Two dedicated RIO ports on the PLC will be used for two RIO buses, each bus to control two cavity systems via RIO and Flex I/O interface. Several REDI Panels will be installed on each of the RIO buses. Another dedicated DH+ port on the PLC will be used for a local PC running RS View or PLC programming.  See figure 1, a proposed architecture for SNS ring high-level RF system.

# VME Interface Options

There are three options that could be used to interface between SNS global ICS and Ring high level RF system, Blue Hose interface, Ethernet interface and ControlLogix gateway.

## Blue Hose Interface

The Allen-Bradley VMEbus remote I/O scanner modules (6008-SVnR) allow a VME master processor (IOC) direct access to I/O adapter devices on the Allen-Bradley Universal Remote I/O link. The VMEbus I/O scanner modules provide up to 230.4k bit/s communication and continuous block-transfers.  1771-DCM PLC direct communication module provides a remote I/O adapter port for a local PLC processor (Ring High Level RF PLC) to communicate with a remote I/O scanner port of a supervisory processor (IOC) across a remote I/O link. Figure 2 shows the Blue Hose interface between IOC and PLC-5.

## Ethernet Interface

The Allen-Bradley 1785-ENET Ethernet Interface Module provides an Ethernet port for a 1771-platform PLC-5 processor, so that it can communicate with IOC via Ethernet link. Figure 3 shows this interface option.

## 3.3 ControlLogix gateway

A ControlLogix 5550 can be used as a gateway between DH+ Network and Ethernet. See figure 4.

# Performance Requirement

There are about 500 bits per cavity system or total of 2k bits data will be transferred from PLC to VME IOC. As a minimum requirement, the update rate on operator screens shall be at least once every 5 seconds.

The detailed bits definition information along with their names, units, alarm ranges, and the descriptions of the bits is in Appendix A.

Figure 1. Ring High Level RF Control Architecture

Figure 2. Blue Hose Interface Between IOC and RF PLC

## Figure 3. Ethernet Interface Between IOC and RF PLC

Figure 4. Logix 5550 Gateway Configuration

# Appendix A. Bit Definitions

| Type | Source | Name |
| --- | --- | --- |
|  | Anode First Input Module |
| Sink Inp | 303 #1 | HV On Status |
| Sink Inp | 303 #1 | HV Inh Status |
| Sink Inp | 303 #1 | Loc/Rem Status |
| Sink Inp | 303 #1 | Over-Voltage Status |
| Sink Inp | 303 #1 | Interlock Status |
| Sink Inp | 303 #1 | Overload Status |
| Sink Inp | 303 #1 | Arc Status |
| Sink Inp | 303 #1 | Power Fault Status |
| Sink Inp | 303 #1 | Coolant Fault Status |
| Sink Inp |  | WATER LEAK |
| Sink Inp |  | WATER MAT FAULT |
|  | Anode Second Input Module |
| Sink Inp | 303 #2 | HV On Status |
| Sink Inp | 303 #2 | HV Inh Status |
| Sink Inp | 303 #2 | Loc/Rem Status |
| Sink Inp | 303 #2 | Over-Voltage Status |
| Sink Inp | 303 #2 | Interlock Status |
| Sink Inp | 303 #2 | Overload Status |
| Sink Inp | 303 #2 | Arc Status |
| Sink Inp | 303 #2 | Power Fault Status |
| Sink Inp | 303 #2 | Coolant Fault Status |
|  | Anode Third Input Module |
| Sink Inp | 402 | HV On Status |
| Sink Inp | 402 | HV Inh Status |
| Sink Inp | 402 | Loc/Rem Status |
| Sink Inp | 402 | Over-Voltage Status |
| Sink Inp | 402 | Interlock Status |
| Sink Inp | 402 | Overload Status |
| Sink Inp | Flow-1 | 303 #1 Water Flow |
| Sink Inp | Flow-2 | 303 #2 Water Flow |
| Sink Inp | Fan | Control Box TC Fault |
| Sink Inp | Door | Cabinet Access Door Inerlock |
| Sink Inp | Extnl | Remote Interlock Link |
| Sink Inp | PLC | PLC I/L Trip readback |
|  | Cap Bank Module |  |
| Sink Inp |  | Crowbar circuit interlock |
| Sink Inp |  | Crowbar fuse interlock |
| Sink Inp |  | Overcurrent |
| Sink Inp |  | Airflow fault |
| Sink Inp |  | Door interlock |
| Sink Inp |  | PS shorting bar |
| Sink Inp |  | Crowbar OT |
| Sink Inp |  | Load fault |
| Sink Inp |  | Cubical OT |
| Sink Inp |  | Heat Lamp interlock |
| Sink Inp |  | CR6 NO C1 Dump Res |
| Sink Inp |  | CR6 NC C1 Dump Res |
| Sink Inp |  | CR7 NO C2 Dump Res |
| Sink Inp |  | CR7 NO C2 Dump Res |
|  | PA / Cavity Interlocks & Statuses |
| Sink Inp | Local Switch |  |
| Sink Inp | Remote Switch |  |
| Sink Inp | Attenuator Water Flow |  |
| Sink Inp | Tube Water Flow |  |
| Sink Inp | Cavity Water Left Flow |  |
| Sink Inp | Tube Over-Temp |  |
| Sink Inp | Cavity Over-Temp Left |  |
| Sink Inp | Cavity Water Flow Right |  |
| Sink Inp | Cavity Over-Temp Right |  |
| Sink Inp | Cables |  |
| Sink Inp | Grid Under-Voltage |  |
| Sink Inp | Filament Under-Voltage |  |
| Sink Inp | Flushing Air Flow |  |
| Sink Inp | Tube Air Flow |  |
| Sink Inp | Screen Over-Load |  |
| Sink Inp | Ross Relay Readback |  |
| Sink Inp | Filament Contactor Readback |
|  | Variac Interlocks |  |
| Sink Inp | Blower Contactor Readback |
| Sink Inp | Blower Motor Over-Load |  |
| Sink Inp | Crash |  |
| Sink Inp | Filament Safety |  |
| Sink Inp | Blower Under-Voltage |  |
| Sink Inp | Variac Door Readback |  |
| Sink Inp | Variac Low Limit |  |
| Sink Inp | Variac High Limit |  |
| Sink Inp | Vacuum |  |
| Sink Inp | HV Safety |  |
| Sink Inp | Bldg Crash |  |
| Sink Inp | HV READY |  |
| Sink Inp | Ross Relay Control Relay |  |
|  | Tuning PS Interlocks |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |
| Sink Inp |  |  |

# Appendix B. Schedule

| Dates | Activities |
| --- | --- |
| 03/31/02 | Preliminary Ring High Level ICD. |
| ? | Final Ring High Level ICD |
| 04/01/04 – 09/30/04 | Ring High Level RF system commission |
| 10/01/04 – 09/30/05 | Ring RF system integration |

# References

- Spallation Neutron source Design Manual June 1998

- Allen-Bradley & Rockwell Software, Inc Product Catalogs

# Text boxes

1

7

7

1

D

C

M

P

L

C

-

5

Flex I/O

Flex I/O

Flex I/O

Flex I/O

6

0

0

8

-

S

V

1

R

Ring HL RF IOC

MVME 2

1

0

0

Cavity-2

Cavity-1

Cavity-4

Cavity-3

RIO

DH+

PC

Ethernet

EPICS OPI

Linux

R

I

O

PS