## list
source
cond
emiss
feed
process

## source
Source Description
Phase II ID No. | 1005
EPA ID No. | TXD008076846
Facility Name | Huntsman Corp. (formerly Texaco)
Facility Location
City | Port Neches
State | TX
Unit ID Name/No. | Boiler # 1 (6-BB-1) At C4 Facility
Other Sister Facilities | Boiler # 2 (6-BB-2)
Number of Sister Facilities | 1
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid injection
Combustor Characteristics | Steam Boilers - Babcock & Wilcox units, built in 1943; Rated @ 594 MMBtu/hr with 495,000 lb/hr steam @ 500 psig and 563 F
Capacity (MMBtu/hr) | 549
Soot Blowing | Yes
APCS Detailed Acronym | None
APCS General Class | None
APCS Characteristics | None
Hazardous Wastes | Liq
Haz Waste Description | "Polyblend"
Supplemental Fuel | Process gas, oil
Sponge oil
Stack Characteristics
Diameter (ft) | 12.8
Height (ft) | 84.9779
Gas Velocity (ft/sec) | 32
Gas Temperature (°F) | 265
Permitting Status
HWC Burn Status (Date if Terminated)

## cond
Cond Description
1005C1
Report Name/Date | Test Report on Re-Certification of Compliance of Boiler No. 1 & Annual Performance Test on 2 CEMS installed on Blrs 1 & 2; 10/95
Report Preparer | Cubix Corp.
Testing Firm | Cubix Corp.
Testing Dates | 1995-10-04
Cond Dates | 1995-10-01
Cond Description | CoC; max feedrates
Content | PM, HCl/Cl2, CO emissions; metals, ash, chlorides in feeds
1005C2
Report Name/Date | Test Report on Re-Certification of Compliance of Boiler No. 1 & Annual Performance Test on 2 CEMS installed on Blrs 1 & 2; 10/95
Report Preparer | Cubix Corp.
Testing Firm | Cubix Corp.
Testing Dates | 1995-10-05
Cond Dates | 1995-10-01
Cond Description | CoC; min combustion temperature
Content | CO emissions

## emiss
Stack Gas Emissions
| Cond ID | Comments | Units | 7% O2
soot blow
1 | 1005C1 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Sampling Train | (PM) | E1
| Stack Gas Flowrate |  | dscfm |  |  | 150000 |  | 138700 |  | 143200 |  | 143966.6667
| O2 |  | % |  |  | 11.31 |  | 11.27 |  | 11.25 |  | 11.28
| Moisture |  | % |  |  | 9.46 |  | 10.06 |  | 11.25 |  | 10.2567
| Temperature |  | °F |  |  | 260 |  | 263 |  | 269 |  | 264
| PM (total) | E1 | gr/dscf | y |  | 0.0141 |  | 0.0131 |  | 0.015 |  | 0.014067
| PM | E1 | gr/dscf | y |  | 0.0075 |  | 0.0067 |  | 0.0062 |  | 0.0068
| CO (RA) | E1 | ppmv | y |  | 1.6 |  | 0.7 |  | 0.7 |  | 1
| HCl | E1 | ppmv | y | nd | 0.08 | nd | 0.03 | nd | 0.02 | 100 | 0.043333
| Cl2 | E1 | ppmv | y | nd | 0.01 | nd | 0.01 | nd | 0.01 | 100 | 0.01
| Total Chlorine | E1 | ppmv | y | 100 | 0.1 | 100 | 0.05 | 100 | 0.04 | 100 | 0.063333
2 | 1005C2 |  |  |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| CO (RA) | E1 | ppmv | y |  | 0.6 |  | 0.6 |  | 0.4 |  | 0.7

## feed
Feedstreams
Units
* | 1005C1 |  | Cond Avg | Cond Avg | Cond Avg
| Feedstream Number |  | F1 | F2 | F3
| Feed Class |  | Liq HW | Misc Fuel | Misc Fuel
| Feedstream Description |  | Polyblend flow | Fuel gas flow | Sponge oil flow
| Feed Rate | BPD | 328
| Feed Rate | mcfh |  | 382 | 8.3
* | 1005C2
| Feedstream Number |  | F1 | F2 | F3
| Feed Class |  | Liq HW | Misc Fuel | Misc Fuel
| Feedstream Description |  | Polyblend flow | Fuel gas flow | Sponge oil flow
| Feed Rate | BPD | 340
| Feed Rate | mcfh |  | 340 | 9.4

## process
Process Information
Cond ID No. | Units | Run | Run | Run | Avg
|  | 1 | 2 | 3
1005C1
"Gas in Temperature" | °F | 540 | 535 | 535 | 537
Steam Production Rate | Mlb/hr | 240 | 240 | 240 | 240
1005C2
"Gas in Temperature" | °F | 518 | 515 | 521 | 518
Steam Production Rate | Mlb/hr | 213 | 209 | 230 | 217