COMMUNICATIONS SITE MANAGEMENT PLAN

GREEN MOUNTAIN

UNCOMPAHGRE FIELD OFFICE

Prepared by the United States Bureau of Land Management

Uncompahgre Field Office

Montrose, Colorado

Approved by: __Barbara Sharrow__________________________    ___9/28/2006 ____

Field Manager						Date

___Karen Tucker____________________________    ___9/28/2006_____

Gunnison Gorge NCA Manager				Date

GREEN MOUNTAIN COMMUNICATIONS SITE MANAGEMENT PLAN

I.	INTRODUCTION	3

A.	Terms and Definitions	3

B.	Purpose	4

C.	Site Description	5

D.	Area Served	5

E.	Access	5

F.	Site History and Development	5

G.	Goals and Objectives of Site Management Plan	5

II.	AUTHORITY AND DIRECTION	6

A.	Authority	6

B.	Relationship to Communications Site Leases/ROW Grants	7

III.	GENERAL RESPONSIBILITIES	7

A.	The Bureau of Land Management	7

B.	Facility Owners and Facility Managers	7

C.	FCC and NTIA/IRAC	9

IV.	AUTHORIZED USES AND USERS WITHIN A FACILITY	9

Use by Multiple Users	9

V.	FEES	9

VI.	General Operation and Maintenance Direction	10

A.	Unique Resource Considerations at this Communication Site	10

B.	Wiring and Grounding	11

C.	Communications Equipment	11

D.	Cables and Transmission Line (Wave Guides)	14

E.	Radiation	15

F.	Utilities-Availability of and Requirements for:	15

G.	Sanitary Facilities	16

H.	Security and Law Enforcement	16

I.	Site Maintenance	17

J.	Inspections	17

K.	Fire Prevention and Hazard Reduction Requirements	18

L.	Access Maintenance and Restrictions	19

VII.	CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION	19

A.	New Facility Owner Responsibilities	19

B.	Construction Methods and Resource Protection	20

C.	Construction Inspection	21

D.	New or Remodeled/Expanded Buildings	22

E.	New or Remodeled/Expanded Towers	23

VIII.	SITE ASSOCIATION/ADVISORY GROUP	23

IX.	APPENDICIES	23

A.	Communication Site Plat	23

B.	Authorized Facilities	23

C.	Inspection Checklist	23

D.	Site Photographs	23

INTRODUCTION

## Terms and Definitions

The terms used in this communications site management plan conform to the definitions listed in the April 22, 2005, Federal Register notice “Rights-of-Way, Principles and Procedures: Rights-of-Way Under the Federal Land Policy and Management Act and the Mineral Leasing Act” (available at: http://a257.g.akamaitech.net/7/257/2422/01jan20051800/edocket.access.gpo.gov/2005/pdf/05-7501.pdf)

and clarifications provided in Bureau of Land Management (BLM) Handbook 2860-1 and the United States Code of Federal Regulations (CFR) 43 CFR 2800.  In the event of a conflict, between the plan and these sources, the Federal Register notice and the BLM Handbook will govern.

The words “lease” and “lessee” as used in this plan refer to the relationship between the BLM and the communications use lease lessee, or right-of-way (ROW) holder.  The words “customer” and “tenant” refer to the relationship between the lessee or holder and the occupants in the lessee’s facilities.

LEASE OR ROW – A use authorization issued to a communication Facility Owner or Facility Manager allowing for the use of public land to construct and or operate a communications facility and, unless specifically prohibited, to sublease to occupants in that facility.

LESSEE, OR LEASE OR ROW HOLDER – Facility Owner or Facility Manager

CUSTOMER – Entities that pay a facility owner, facility manager or tenant for communications services and are not re-selling or broadcasting communications services to others

TENANT – A communications user who rents space in a communications facility and operates communication equipment for the purpose of re-selling or broadcasting communications services to others for profit.

COMMUNICATIONS SITE – An area of BLM-managed public land designated through the land and resource management planning process as being used or is suitable for communications uses.  A communications site may be limited to a single communications facility, but most often encompasses more than one.  Each site is identified by name; usually a local prominent landmark, such as Green Mountain Communications Site.

FACILITY MANAGER – The holder of a BLM communications use authorization who leases space for other communication users.  A facility manager does not directly provide communications services to third parties.

FACILITY OWNER – Individuals, commercial entities, organizations, or agencies, that own a communications facility on Federal land; own and operate their own communications equipment; and hold a communications use authorization.

NON-BROADCAST – This category includes Commercial Mobile Radio Service (CMRS), Facility Managers, Cellular Telephone, Private Mobile Radio Service (PMRS), Microwave, Local Exchange Network, and Passive Reflector.

BROADCAST – This category includes Television Broadcast, AM and FM Radio Broadcast, Cable Television, Broadcast Translator, Low Power Television, and Low Power FM Radio.

RIGHT-OF-WAY (ROW) – The public land authorized to be used or occupied pursuant to a ROW grant.

RIGHT-OF-WAY GRANT – A use authorization issued pursuant to Title V of the Federal Land Policy and Management Act of October 21, 1976 (U.S.C. 1701 et seq.) or issued on or before October 21, 1976, pursuant to then existing statutory authority, authorizing the use of a ROW over, upon, under or through public land for construction, operation, maintenance and termination of a project.

HOLDER – Any applicant who has received a ROW grant, lease or temporary use permit.

USERS – All ROW and lease holders, lessees, customers, and tenants that own or operate a facility or communication equipment at the communication site.

## Purpose

This plan will be used by BLM officials administering communications uses at Green Mountain, existing lessees, holders, and applicants desiring a lease, grant, or an amendment to an existing lease or ROW grant.  The plan will be kept updated by amending pages or sections of the plan rather than issuing a revised edition of the plan.  When a revision is necessary, a letter from the Uncompahgre Field Office enclosing a copy of revised pages or sections will amend the plan.  The amendments will be consecutively numbered.

Overall management direction for the administration of communications sites is outlined in the CFR and the BLM Handbook and applicable BLM Instructional Memoranda.  Specific direction for site management planning on designated communications sites is contained in BLM Handbook 2860-1.  Primary regulations and policy pertaining to issuance of ROW and lease authorizations by the BLM are found in Title 43 CFR 2800 and BLM Handbook 2860-1.

The site is identified in the Gunnison Gorge National Conservation Area (NCA) Resource Management Plan (RMP) approved in November 2004.  The site is designated in the RMP for low power communication uses.

Prior communications site management plans have not been developed for Green Mountain.  This Site Management Plan provides applicable guidance and adds current policy and technical standards for better management of the Green Mountain Communications Site.  This plan governs development and management of Green Mountain and will be modified in the future as needs and conditions warrant.  Any future such uses must be designed, installed, operated, and maintained to be compatible and not interfere with the senior uses as defined in Appendix B, Lessee Facility Table. This site-specific plan is administrative in nature and is Categorically Excluded from further review under the National Environmental Policy Act (NEPA) (516.DM2, Appendix 1,1.7).  Any additional development of the site will be addressed in a site-specific NEPA document.

## Site Description

The site is located on Green Mountain, which is located north of the Gunnison River Gorge and southwest of Crawford, Colorado. The area is managed by the Uncompahgre Field Office.  The site is specifically located in S½SE¼, Section 5, T. 50 N., R. 8 W., New Mexico Principle Meridian at approximately 38º 37’ 13” North Latitude and 107º 46’ 56” West Longitude (NAD 83).  The elevation at the Green Mountain Communications Site is approximately 8,442 feet above mean sea level.   A Communication Site Plat is provided as Appendix A.

## Area Served

This site does not serve a Ranally Metro Area (RMA).  The population zone served is less than 25,000 (Zone 9).  These zones may be adjusted in the future as population change.  This information will be used for rental fee determination.

## Access

Access to Green Mountain is from SH 92 just south of the Crawford Reservoir and then west on County Route C77.  The final access road is a two-track route from C77 south and then east to the rim and the communications site.

The portion of the road on public land from C77 to the site is authorized under ROW grant COC 59910.

## Site History and Development

In 1996, the first communications facility ROW on Green Mountain was granted to the Black Canyon - Curecanti National Park Service for UHF and VHF radio repeaters and links. Other government entities in this facility include Delta County EMS, Montrose County Sheriff's Posse, and Crawford Fire Department.

A list of all facilities, including tenants and customers, as of the date of this plan can be found in Appendix B.

Access is extremely limited and the power is limited to solar panel arrays. Space appears to be available in the existing building and tower to serve this area for the current demand.   Any modifications to existing facilities or proposals for new facilities must be approved by the Uncompahgre Field Office according to the appropriate NEPA process and guidance described in this document.

## Goals and Objectives of Site Management Plan

1.	Manage the Green Mountain Site for non-broadcast uses within the Operation and Maintenance guidelines within this plan.  All uses must be designed, operated and maintained so as not to materially or electronically interfere with the existing uses.

2.	Manage communication equipment on the Green Mountain Site to maintain the radio frequency (RF) hazard to be within the Public and Occupational Standards as defined by the Federal Communications Commission (FCC).

3.	Systematically develop the site to maximize the number of compatible uses while ensuring safety and protection of resources.  Development of new towers or buildings within each of the authorized owner’s facilities will be authorized only after their respective tower or building space area is filled to near capacity.

4.	Present a program for future growth, development and operation within the site which is consistent with the Gunnison Gorge NCA RMP.   See section VI General Operation and Maintenance Direction; A. Unique Resource Considerations at this Communications Site.

5.	Help fulfill the public need for adequate communications sites.

6.	Protect the interests of holders, lessees, tenants and customers, by preserving a safe and electronically “clean” environment.

7.	Encourage the efficient development and use of space and facilities within the designated site, subject to the BLM’s goal to provide the best possible public service at reasonable cost.

8.	Achieve visual quality objectives by requiring design standards that are unobtrusive and utilizing earth tone colors and non-reflective surface material and stringent site maintenance requirements.

9.	Describe the BLM’s policy for road maintenance.

10. Develop new facilities only after the appropriate site-specific NEPA analysis and coordination with current lease or ROW holders and users.  This future development must be consistent with the NCA RMP.

11. Amend this Communications Site Plan as necessary to be consistent with future RMPs.

AUTHORITY AND DIRECTION

## Authority

BLM’s authority to authorize communications uses on public land (administered by the BLM) is granted by the Federal Land Policy and Management Act of 1976, 90 Stat. 2776 (43 U.S. C. 1761-1771) and is reflected in Title 43, Code of Federal Regulations (CFR), 2800 and BLM Washington Office Information Bulletin 98-23.

BLM authority for communications site management planning is contained in BLM Handbook 2801-1, Plan of Development and H-2860-1, Communication Site Rights-of-way.  Direction on, and policy for communication use authorizations is contained in BLM Manual Section 2860.

Authority for the issuance of authorizations and/or licenses for the transmission and reception of electronic radiation for communication purposes is granted by Congress and administered by the FCC and/or the National Telecommunication and Information Administration – Interagency Radio Advisory Committee (NTIA/IRAC).

## Relationship to Communications Site Leases/ROW Grants

This site plan will be incorporated into all leases and ROW grants issued (now and/or in the future) for this communications site and must be used in conjunction with the granting authorization. PROVISIONS OF THE SITE PLAN ARE ENFORCED THROUGH THE GRANTING AUTHORIZATION.  Each lessee or holder is expected to include the requirements of the authorization and the site plan into any documents, which describe the business relationship between the lessee or holder’s and their tenants and customers. The lessee or holder is responsible for enforcing those provisions.

GENERAL RESPONSIBILITIES

## The Bureau of Land Management retains the responsibility for:

- Issuing and amending authorizing instruments to Facility Owners and Facility Managers, only for the areas actually occupied by the authorized improvements.  Granting occupancy and use of public land rests exclusively with the BLM. The issuance of a FCC license (authorization), or frequency assignment, does not authorize occupancy of public land.

- Approving any new facility(ies) at the site.

- Approving amendments to existing facilities (i.e. additions to tower, antenna, equipment or building), and approving assignments of leases and ROW grants to qualified buyers of facilities on the site.

- Approving any modifications to existing facilities including the tower, antenna, equipment or building.  Also, approving any changes to the existing FCC licenses, prior to the submission of an application to the FCC.

- Frequency Management.  The BLM is not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the FCC and NTIA/IRAC authorizations.

- Notifying existing users at the site of any proposed new uses and provide for a 30-day comment period.  If the new use(s) is opposed based on proven technical merits and the technical issues cannot be resolved, the BLM will deny the proposed new use(s).

## B.	Facility Owners and Facility Managers (or their designated representatives) are responsible for:

- Complying with their use authorization and all provisions of this site plan.

- Ensuring that all new facilities, expansions, or improvements are consistent with the  Gunnison Gorge NCA and Uncompahgre Field Office Planning Documents; any environmental document(s)/decisions for the site; and, this site plan.

- Ensuring facilities/equipment not complying with Federal/State/local laws/regulations/ ordinances will be removed or modified.  Any modification needs pre-approval by the BLM.

- Keeping all facilities within the established limits of their authorized area.

- Providing the BLM with the name, address and phone number for a local contact person.  The Facility Owner and Facility Manager and the contact person may be the same individual.  The contact person will be available for emergencies and will have the authority to make decisions about construction issues, facility maintenance and all equipment within the facility.

- Adhering to the Facility Owner/Facility Manager Lease/ROW as follows:

  - Facility Owners and Facility Managers with Communications Use Leases and ROW grants are authorized to rent building/tower space to tenants and/or customers without prior written approval from the BLM.

  - Tenants and/or customers may not construct their own equipment shelter (building, shelter or cabinet) or antenna support structure (tower or mast).  The facility owner must own all communication shelters and towers under their lease or grant. [If that is not possible, a separate SF-299 application, cost-recovery deposit, analysis, and authorization are required.  This will also result in the use being a tenant/customer of the original lease/ROW in addition to being a separate facility for billing purposes.]

  - Tenants and/or customers using a facility covered by a Facility lease/ROW will not have separate BLM leases/ROWs to authorize the use except in situations where regulations or policy require them.

  - Facility Owners and Facility Managers are responsible for complying with the terms and conditions of the facility lease/ROW.  Facility Owners/Facility Managers are also responsible for ensuring that their tenants and customers are in compliance with the terms and conditions of the lease/ROW and applicable FCC or NTIA/IRAC license terms and conditions.

  - The Facility Owner and Facility Manager may not place any unreasonable restrictions nor any restriction restraining competition or trade practices on tenants and/or customers, or potential tenants and/or customers.

- Ensuring that all communications equipment is properly installed, operated, and maintained.

- Ensuring that all communication equipment meets ANSI, FCC and BLM regulations, guidelines and standards concerning radiation limitations by:

  - Monitoring radiation levels at their facility and;

  - Immediately correcting any radiation levels that are, or could be a hazard to human health. (FCC 47CFR sections 1.1307(b), 1.1310 and 2.1093) and FCC OET Bulletin 54, August 1999.

- Providing a certified copy of all uses and the correct category of uses within the facility, along with the current phone numbers and addresses of all tenants and customers as of September 30th each year.  This report is due by October 15th each year.

- Keeping the premises around their buildings free of trash and debris.

- Placing the BLM lease/ROW serial number on the door of their communications site building.

- Correcting all interference problems.  The users are normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the FCC and NTIA/IRAC authorizations.

## C.	FCC and NTIA/IRAC are responsible for:

Frequency Management.  The FCC and NTIA/IRAC are not normally responsible for the resolution of conflicts when the licensees or agencies are operating within the limits of the authorizations.

AUTHORIZED USES AND USERS WITHIN A FACILITY

## Use by Multiple Users

Use of all facilities and improvements by more than one user will be required except where the facility owner is a government agency.  Site applicants will take the lead in this area and design their proposals to accommodate multiple uses of facilities and improvements.  This includes multiple uses of buildings, towers, back-up generators, grounding systems, fuel containers, access ways and parking areas.

Due to the availability of building and tower space at the site, new facilities, or major modifications to existing facilities will generally not be approved until the empty space is utilized even if other users are, or could be, competitors.

Facility Owners and Facility Managers are not required to lease facility space to others if they can prove to the authorized BLM officer that:

- Space is not available;

- The use is incompatible with the existing facilities;

- Additional space is needed by the facility owner/manager;

- Additional users would violate system security needs; or,

- Potential interference is not resolvable.

FEES

The BLM will charge Facility Owners and Facility Managers annual rental fees based on the Fee Schedule for Communications Uses on Public Lands, as adjusted annually.  These fees will be fair market value for the use of public land.  The population Zone 9 will be used for these calculations unless something else is specifically agreed to in writing by the authorizing officer or until populations change.

Fees that Facility Owners and Facility Managers may charge their tenants and “customers” are to be:

Reasonable (consistent with, and not in excess of, other fees for similar facilities) and commensurate with the uses and occupancy of the facilities and services provided to tenants and “customers”.

General Operation and Maintenance Direction

## Unique Resource Considerations at this Communication Site

This site is adjacent to the Gunnison Gorge NCA.  Specific direction which is applicable to this site will include visual impact analysis and considerations as seen from view points within the NCA and the Black Canyon of the Gunnison National Park (NP).

This site is within the Gunnison Gorge NCA planning area.  Specific direction which is applicable to this site is as follows:

  - LAND-C-8 Approximately 5 acres of public lands on Green Mountain … will be designated as low-power communication site.  A detailed site and landscape plan will be developed before authorizing any additional uses…. and visual impacts of existing uses will be mitigated where possible.  Fencing will be required at all sites for security.  Construction, materials, or structures on the site will not create strong visual contrasts as seen from the Black Canyon of the Gunnison National Park, NCA, or Wilderness area .Future applicants will collaborate with the BLM and Park Service to develop the proposed action during the application process and to mitigate the visual impacts.  Each future additional application for use will be accompanied by a simulation visual analysis and visual impact determination as seen from to-be-selected critical viewing points, in order to assess the actual visual impacts for the proposal and the alternatives.

All future uses at the Green Mountain … Communication Site will not interfere with the uses currently authorized at the time new applications are received.  (This plan meets this intent.)

The RMP states that Green Mountain will be designated as a low-power communication site.  Without defining high power and low power, implementation of this plan would be difficult.

The intent of this plan was to reduce the overall effective radiated power (ERP) at this site.  Therefore, in keeping with the objectives of the NCA RMP, this plan will limit new uses at this site to non-broadcast uses only.  No new broadcasting uses would be allowed at this site.

Any changes in the existing FCC licensed uses (i.e. frequency, ERP, height above average terrain (HAAT)) requires review and approval by the BLM prior to submission of an application to the FCC.  Any changes to the tower, antenna, equipment, or building requires review and approval by the BLM.

If any additional coordination measures are identified in the future through the NEPA and or RMP process, the appropriate standards will be amended to this plan.

## Wiring and Grounding

1.	All equipment is to be installed within existing buildings and on equipment racks that are grounded and shielded.  Grounding is to be installed in accordance with accepted standards.

2.	All electrical wiring and grounding must meet the “National Electrical Code” and applicable State/local codes.  All permanent wiring shall be installed in metallic conduit.  Surge protection shall be installed on all power distribution panels.

3.	Lightning protection shall be in accordance with NEC part 810-20 Antenna Discharge Units and part 810-21 Grounding Conductors.  Periodic bonding of the down conductor to the tower (Galvanized) steel shall be made with proper bonding connectors that are tin plated or made of brass.

4.	Each building is to have its own separate grounding system for all users in that structure.  Wherever practical, interconnection of individual grids and/or the simultaneous placement of a large sized copper ground wire with any new grounding systems that are buried on the site will be required.

5.	Site or facility grounding must be constructed of copper, with #2 AWG or larger wire or 2” or larger solid copper strap, connected to an adequate site/facility ground electrode system.  The site/facility ground electrode system shall be bonded to the power service entrance grounding electrode conductor.  Guy wires should also be grounded using manufacturers approved methods to preclude bi-metallic junction and corrosion.  All equipment on the site (buildings, towers, power units, transmitters, receivers, antennas, combiners, telephone systems, power cabinets, HVAC units, etc) must be connected to the site/facility ground by direct connection.  Electrical system ground wiring is required for electrical ground fault protection and circuit breaker coordination.  High power operations should use copper strap bonding in accordance with manufacturers specifications.  The grounding systems shall comply with applicable laws, codes and in accordance with standard engineering practice.  Below ground connections must use either an exothermic welding process (i.e. Cadweld, Thermoweld, etc.), copper wedge pressure devices (i.e. Ampact, Wrench-lock, etc.), or brazed copper connections in conjunction with a mechanical UL listed connector (to be used as a physical strength enhancement component).  Brazing by itself is not an acceptable method of bonding below earth grade (buried).

## Communications Equipment

Equipment Ownership

All equipment shall be labeled with:

- The owner’s name;

- Transmitter frequency(ies);

- A valid FCC, or IRAF, authorization;

- Transmitting power output(s); and

- A current 24-hour phone contact number.

Transmitting Equipment

The BLM manual, H-2860-1, Communication Site Right-of-Way Handbook (Rel. 2-268, dated 3/29/90) states that “mixed low power (less than 1000 watts ERP) and high power (1000 watts ERP and greater) use of a site often creates severe interference problems for low power users, and generally is advisable to separate the two types of uses”. Future and existing uses at Green Mountain will be limited to less than 1000 watts ERP in order to attempt to maintain site integrity for existing users

All transmitters will have protective devices (shields, filters, isolation components), designed into or externally installed, to prevent interference to other users.  All transmitters shall be FCC type accepted or meet type acceptance criteria.

Re-radiation of intercepted signals from any unprotected transmitter and its associated antenna system will be prevented by the use of appropriate filters (wide band and narrow band broadcast transmitters).

Direct radiation of out-of-bound emissions, (i.e. transmitter wide band noise, spurious emissions, harmonics, etc.) shall be reduced to a level such that they may not be identified as a source of interference as defined in the FCC Rules and Regulations (e.g. Part 90.209(e)) by using bandpass, lowpass, and/or harmonic filtering.  Where duplexing is used, use of a notch type device should be avoided.  In situations where a notch type or a hybrid device is used, a bandpass filter must be used with the transmitter.  If site noise (electromagnetic noise) becomes an issue, noise threshold limits will be established, and amended into the site plan.

Band-reject filtering may be required in certain applications.

Re-radiation of signals from a transmitter and its associated antenna system shall be prevented by installing appropriate devices (i.e. ferrite isolators), with minimum return loss of 25 db.

All transmitters not in immediate use and not specifically designated as standby equipment shall be removed.  Loads connected to circulators are to be capable of dissipating the total power output of the transmitter.

Receiving Equipment

All receivers shall comply with all applicable parts of the FCC rules, including Parts 2 and 15.

All receivers shall have sufficient “front end” pre-selection to prevent receiver spurious response. The use of bandpass, band-reject cavity or crystal filters to prevent receiver-produced intermodulation or adjacent-channel interference is recommended at the input of all receiving devices.  Use of a notch type device is not permitted.

Tower

- Generally only one tower is authorized for each facility owner.  Facility Owners and Facility Managers may obtain permission to construct a second tower only after submitting evidence that demonstrates that their existing tower is completely filled and full use has been made of combining systems.

- All towers will be left unpainted, if they are dull, galvanized steel.  If paint is required, the BLM will approve only non-reflective colors from the Munsell Soil Color Chart, Standard Environmental Colors.

- Maximum tower height for this site is 50 feet.  Towers must be designed to meet on site wind and icing conditions estimated to be 70 mph with 1 inch ice and otherwise meet   the EIA/TIA-222 standards.

- Anti-climb devices, removable steps, or other means to discourage unauthorized climbing, are highly recommended to reduce or avoid liability claims.

- All new towers will be self supporting.  No new guy lines are permitted.

- To avoid possible impacts to birds or bats, follow the most current version of the U.S. Fish & Wildlife Service’s Interim Guidelines on the Siting, Construction, Operation and Decommissioning of Communication Towers (available at http://migratorybirds.fws.gov/issues/towers/comtow.html).

Antennas

            - Microwave (dish) antennas (other than ground mounted satellite dishes) will be limited to a maximum of six (6) feet in diameter.  The smallest diameter dish that is technically feasible  is preferred. No microwave dish may be mounted above the 20' height on the tower to avoid visual impacts to the NCA and the National Park.

            - All antennas must meet all OSHA safety standards.  If an antenna exceeds FCC public or occupations standards (see FCC OET Bulletin 57), it will be remedied within 24 hours after measures are taken or isolated (e.g., fencing, signing, relocation, lowering power levels are all possible remedies).  Ground measurements of radio frequency radiation (RFR) levels will be taken before mitigation measures are implemented.

            - Color(s) for dish antennas, or covers, must be pre-approved by the BLM.  White dish antennas and/or covers will not be approved.  Typically, only dark grey antennas and/or covers will be approved.

            - Antennas will be treated for low to non-reflectance.

Interference

The responsibility for correcting interference problems is a matter for resolution between the lease/ROW holder of the facility(ies), the user causing the interference, and the affected party(ies).  First users on a site have seniority with respect to the resolution of interference complaints.  All site uses have an obligation to maintain their equipment to industry standards, to operate their systems in accordance with the terms of the FCC license and NTIA/IRAC frequency authorization, and to comply with the BLM regulations.

New users on a site must correct, at their expense, interference problems that they create.   They may be required to furnish an intermodulation study, electromagnetic noise study, or other interference-related data and agree to accept financial responsibility for elimination or prevention of any interference caused by the facility before their application can be evaluated. They must cease operation of the suspect equipment until the problem is corrected.  If interference problems cannot be resolved or corrected within a reasonable time, the new use that is causing the interference may be terminated and the equipment removed.

All users shall cooperate with the Site Users Association, to be formed, and the BLM in identification and correction of any interference.  The BLM does not have authority for correcting interference problems, but can act as a mediator to help all affected parties.  Interference problems must be coordinated with the FCC or NTIA/IRAC, whichever is appropriate.

Interference with law enforcement and/or emergency communications must be corrected immediately.  The operation of equipment covered by this site plan shall not interfere with United States Government radio or electronic operations already in existence.  The user causing this interference, shall, at its own expense, take all action necessary to prevent or eliminate such interferences.  If it does not eliminate such interference within ten (10) days after receipt of notice from the BLM to do so, this use will be terminated.

If electromagnetic noise becomes an issue, noise thresholds will be established and this site plan will be amended accordingly.

## Cables and Transmission Line (Wave Guides)

All new cabling will be jacketed and shielded and shall either be flexible or semi-rigid type.  Existing substandard cables will be upgraded as repairs or replacement become necessary.

Cables will be properly installed and will be strapped and fastened down.  Use of ports at building entrance points will be kept to a minimum by use of combiners.

When attaching cables onto a tower, conduits should be used and cable runs should be equally divided among all tower legs.

All transmission lines (wave guides) are to be supported in accordance with manufacturer’s specifications.

Double shielded braided, or solid shielded cable will be used.  No RG-8 type cable is permitted.  No connector-type adapters will be used on transmission lines.  Only correct connectors that will mate to connected devices are to be used.

Conduits will be shared when they service common areas and will be buried where possible.

## Radiation

All communications uses must meet ANSI, FCC and BLM regulations, guidelines and standards concerning radiation limitations.

Monitoring radiation levels at the site is the responsibility of all site users and will occur at intervals to comply with FCC regulations and guidelines.  A copy of these monitoring reports will be provided to the BLM upon request. The FCC is responsible for enforcement of the monitoring and standardization for compliance.  The FCC could revoke the license and/or issue a fine for failure to comply.  Additionally the BLM could terminate or suspend the use authorization for failure to comply.

Onsite RFR measurements will be taken using appropriate equipment that can adequately measure both on-tower and on the ground levels before mitigation measures related to RFR are implemented pursuant to FCC standards and requirements.

Security fences with RFR notice signs are required around areas that exceed public use levels.  Raising higher power transmitting antenna on the tower or modifying the antenna type to half wavelength may be necessary to eliminate RFR hazards.  Reducing power may also be required if other alternatives are not feasible. All fencing location and design or new tower construction must be pre-approved by the BLM.

Warning signs will comply with ANSI C95.2 color, symbol, and content conventions.  Contact information including name and telephone number will also be included on warning signs.

Lowering power levels for on-tower access during maintenance will be coordinated between affected users.

Any identified RFR radiation problems that are, or could be, a human health hazard must be corrected within 24 hours after measurement tests have been completed or be removed from the site by the site user(s).  If the proposed corrective action involves any new ground disturbance, it must be pre-approved by the BLM.  RF Safety Plan(s) will be developed for the site as determined necessary by the FCC or the BLM.

## Utilities-Availability of and Requirements for:

Commercial Electrical Power

No commercial power is provided to the site.  The site is powered by solar array panels.

Telephone Service

No commercial telephone lines are provided to the site.

If additional service is ever deemed necessary, site users will pay for the cost of:

- The necessary resource surveys and reports for service connections; and

- The cost of constructing service connections.

For visual reasons, new overhead utility poles may not be authorized.  Underground powerlines would be preferred at this site.

Fuel Tanks

All facility owners and facility managers are responsible for providing fuel storage (propane and diesel) and emergency power for their tenants and customers.  No tenants or customers will be authorized to have separate fuel tanks and/or generators. Each facility owner will preferably consolidate fuel storage into a tank large enough in size to accommodate all tenants and customers.  At a minimum, tanks will be grouped together in a consolidated area adjacent to their facilities.  All fuel, storage tanks (e.g. LPG, propane and diesel) must meet current fire department, Federal, State and County safety and hazardous materials requirements. Propane is the preferred fuel for future generators.

- All tanks will be:

a.	Signed in red letters, “SMOKING OR OPEN FLAME PROHIBITED WITHIN 20 FEET”;

b.	In conformance with National Fire Protection Association (NFPA) requirements; and,

c.	Painted an approved color, or screened by an enclosure to blend in with the natural environment.  If an enclosure is used, it must be pre-approved and painted an approved color from the Munsell Soil Color Chart, Standard Environmental Colors.

2.	Diesel tanks will also be:

a.	Enclosed in BLM and fire department approved secondary containment vaults that are painted a BLM approved color from the Munsell Soil Color Chart, Standard Environmental Colors.

b.	Constructed with underground fuel lines.  Fuel line must be constructed of black, treated pipe and fittings, and must be posted.

c.	A containment basin must be maintained below all diesel tanks which are not designed and approved to be self contained.

## Sanitary Facilities

1.	Plans for any sanitary facilities must be pre-approved by the BLM.  If it is determined by the BLM that the users need such facilities, they will be provided by the lease/ROW holder in a manner and location satisfactory to the BLM and within the requirements of the Montrose County Health Department.

## Security and Law Enforcement

The Montrose County Sheriff’s Department is the key law enforcement agency for the area.  They are responsible for most civil and criminal matters.  The BLM will be responsible for enforcing matters related to uses of BLM lands (e.g. resource protection issues).

Patrolling and policing for security purposes is the user’s responsibility.

Fence gates and key access must be approved in advance by the BLM and must be adequate for BLM and Montrose County Fire Department access needs.

## Site Maintenance

The objective of maintenance activities is to present a clean, neat, and orderly appearance at the site and have all of the authorized improvements safe for workers and the public.  All users will keep up the overall appearance of the site.

Miscellaneous debris remaining after any construction and/or equipment installation, removal or modification, is not only a hazard, but can cause interference or intermodulation problems.  In particular, all loose wire or metal objects are to be removed from the site.

The users of the site will remove all graffiti within 10 working days of finding it.

Users will not be permitted to leave or dispose of trash, garbage or cut brush on public lands.  No outside trash or litter containers will be provided.  Site users will remove litter from the site as it is produced.

Policing of litter in common areas (i.e. areas between buildings and developed sites) is the shared responsibility of those holders bordering these areas.

During construction and/or maintenance, excess materials (e.g. cement, wire, metal, building materials) will be removed from public land.

Peeling paint on buildings and/or towers will be re-painted within thirty (30) days of discovery by the facility owner or facility manager and within 10 days of notification of the holder by the BLM.

## Inspections

Enforcement authority is vested in the BLM as the Communications Site Administrator for Green Mountain via 43 CFR 2800.  The BLM may conduct an annual inspection of each user’s facility.  This inspection will verify:

  - Compliance with technical standards.

  - Structural integrity.

  - As-built plan accuracy.

  - Electromagnetic compatibility.

  - General site health, safety, and cleanliness.

The BLM shall provide written notice of the scheduled inspection date at least 30 days in advance.  Each user shall arrange to have personnel available at the site at the time of the inspection.

Any non-compliance found by a user shall be reported to the BLM.  The BLM will conduct an inspection and a written copy of the inspection report shall be forwarded to the violating user within 30 working days following the inspection.  The report shall include:

  - A description of the violation.

  - Corrective action required.

  - Name, address, and organization of the responsible party.

  - Time allowed for completion of corrective measures.

  - Anticipated action in the event of noncompliance with remedial instructions.

## Fire Prevention and Hazard Reduction Requirements

Facility owners and facility managers will be required to maintain vegetation within the currently cleared area around their facilities.  Brush must be pruned to ground level within the site boundary. Gravel or mineral soil (i.e. bare ground) must be maintained to a minimum of (10) feet clearance around buildings and a minimum of (10) feet clearance around any propane tanks. Identified threatened, endangered, or sensitive plant species must remain within the minimum clearance areas.

Smoking is prohibited in flammable vegetation areas.

Roof structure shall be kept reasonably clear of debris at all times.

No explosives will be stored at this site.  Flammable materials shall be stored in conformance with the requirements of local fire regulations.  Flammables will be placed in closed containers and stored away from sources of ignition and combustible materials.  If flammables are stored within a building, the building will be locked, properly signed and well ventilated.

Approved spark arresters will be required and maintained on all internal combustion engines.

At least one (1) U.L. rated 40 B:C dry chemical fire extinguisher is required inside each building.  Prior to each June, fire extinguisher(s) shall be inspected by holders and refilled, if necessary.

Any fire will be immediately reported to “911”, the nearest BLM office and/or Montrose County Sheriff.

BLM Officers will make periodic fire prevention inspections.  They will call to the holder’s attention any lack of compliance with the above regulations, plus any other existing hazards.  Compliance with these inspections is required within the time limits specified in the inspection report.

The Facility Owners and Facility Managers shall maintain batteries in accordance with manufactures specifications to prevent corrosion, leaks, spills, and other case damage immediately around each battery and from spilling on the floor.  Material Safety Data Sheets (MSDS) shall be posted in a visible location inside the storage facility.  All MSDS recommendations shall be followed by the  Facility Owners and Facility Managers to eliminate possibility of leaks, spills, and unnecessary personnel exposures. All batteries and contents shall be treated as hazardous waste and proper disposal methods shall be followed for recycling and disposal.

## Access Maintenance and Restrictions

Roads

The primary access road is a County Road maintained by Montrose County, the final two track road must remain in a primitive condition with no blading.  Vegetation may be pruned as necessary to maintain a minimum width.

Users who damage or disturb the access road, or any associated structures, such as ditches, culverts, roadside vegetation, signs and/or underground utilities or facilities, will be required to repair the road or associated structures, to conditions equal to or superior to those prior to any damage or disturbance.  This work must be done according to applicable road maintenance standards and may require the appropriate NEPA analysis.

Interior Site Driveways/ Parking Areas

Interior site driveways within the communications site will be maintained by the site users.  Interior roads will be planned and approved during establishment of new facilities.  Interior roads will be maintained in a manner to allow only one entrance to the site.  Off-road vehicle use by a user in and around the communication site will be avoided.

CONDITIONS FOR CONSTRUCTION, MODIFICATIONS OR EXPANSION

## New Facility Owner Responsibilities

## In addition to the responsibilities listed in Section III, New Facility Owners and Facility Managers are responsible for:

1.	Submitting a complete application (SF-299) to the Uncompahgre Field Office (ATTN: “Realty Specialist”) prior to any new construction, or modifications to existing improvements.  The application must include:

- The appropriate cost recovery processing fees as determined by BLM.

b.	A copy of the approved Communication Site Plat showing all of the proposed (new) facilities including structures, towers, and auxiliary equipment;

c.	Completed drawings/plans prepared by a registered engineer and Plan of Development approved by the BLM;

d.	Identification of any microwave beam paths, a plot of their azimuth(s), and their proposed elevation(s) on the tower;

e.	Documentation that shows that proposed facilities will not be obstructing, or interfering with, any existing fixed point to point antennas, omni directional broadcast antennas, or microwave beam paths in the directions of primary population targets.  Proposed beam path needs must be shown on Communication Site Plat; and,

f.	Any needed recommendations, changes or modifications to their original proposal, based on any required resource surveys and/or reports.

g.	Communication Site Technical Data Reports for all new proposals.

2.	Demonstrating that their proposals will not cause undue interference with any existing uses before the BLM can approve new facilities.  In addition, it is the applicant’s responsibility to show that any new facilities will make the most efficient use of the limited amount of space at the site.

3.	Showing their proposals will provide for future users without additional construction.

4.	Providing engineering and geotechnical investigations for development of specific foundation designs and grading plans.

5.	Provide for erosion control as part of the Plan of Development prior to construction activities.  At a minimum, erosion control must include: sediment control, stipulations that cut/fill slopes will be graded and contoured to prevent erosion and/or excessive runoff, and recommendations for temporary erosion control measures, (e.g. netting, silt fences, swales, and/or sediment collection areas).

6.	Coordinating with other Federal (e.g., FCC and FAA), State and County agencies and obtain all required approvals and/or permits.

7.	Providing 30-day notice to all facility owners/facility managers at the site, as well as the BLM, of all new frequencies proposed for the site.  A completed BLM Communication Site Technical Data Report or equivalent must be sent with the 30-day notice to allow for comment of potential interference.  This would be for new frequencies for themselves and their tenants and customers.

8.	Insuring that all written approvals have been obtained from the BLM prior to construction.  In addition:

a. Directional broadcast antennas (e.g. translators) will only be protected within the arch between their licensed 3 dB points.

b.  New and/or modified facilities will not obstruct existing fixed point-to-point antennas or omni-directional broadcast antennas in directions of primary population targets.

## Construction Methods and Resource Protection

Plans submitted by an applicant for any new construction or modifications shall specify provisions for soil rehabilitation measures including, but not limited to, soil replacement and stabilization and for proper handling of runoff from buildings, parking area, access roads, and undeveloped common areas.

The following methods and resource protection measures will be required to minimize impacts during construction:

1.	Avoid and protect sensitive resource areas, as identified by the BLM.

2.	Compliance with the Plan of Development and the Erosion Control Plan.

3.	During construction and/or maintenance, no paint or paint thinners will be disposed of on site.

4.	Minimize ground disturbance and vegetation removal as much as possible during construction activities.  All ground-disturbing activities require BLM pre-approval.

5.	Disturbed areas will be re-vegetated with native vegetation species pre-approved by BLM as soon as possible after construction.  If necessary, reseeding will be required until vegetation is successfully established as determined by the BLM.

6.	 No grading material will be cast off during construction/reconstruction activities. Excess soil can be used for fill material on road and/or building/tower pads.

7.	Temporary, on-site storage of construction materials will require pre-approval by the BLM.

8.	Construction materials and supplies, except for hazardous materials (see number 10. below) may be left unattended at the construction site at the end of each workday, but at the owner’s risk.

9.	Hazardous materials, including, but not limited to all fuels, oils, and lubricants are not to be left unattended at the site at any time.  During construction, these materials are to be removed from the site at the end of each workday, or temporarily stored inside a locked and signed building until the following workday.

10.	All surplus construction materials and/or waste debris must be removed from the site no later than thirty (30) days after construction has been completed.

11.	Any earth moving or heavy equipment (e.g. dozers, graders, cranes, backhoes, etc.) leaving the designated roadway and/or approved parking area(s) to perform authorized activities at the site, will be washed off prior to being brought onto public lands to prevent the introduction and spread of noxious weeds into the area.

## Construction Inspection

1.	All new construction, reconstruction, or major modification shall conform to the established technical standards and accepted engineering practices (i.e., the Uniform Building Code).

2.	Any construction inspections required by other applicable agencies are the responsibility of the lessee/holder.  Copies of completed inspections are to be provided to the Uncompahgre Field Office, Authorized Officer, either as they occur or as part of the final as-built plan.  Inspection information shall become a permanent part of the holder’s lease/ROW case file.

3.	The Lessee/Holder agrees that corrective work detailed in BLM, or other agency required compliance inspections, would be completed by the scheduled completion date.  If the Lessee/Holder disagrees or has questions about specific items, the Lessee/Holder must contact the BLM in order that the disagreement or item may be resolved.

4.	A final set of as-built plans will be submitted to the Uncompahgre Field Office, Authorized Officer, within 90 days of acceptance of structure (if contracted) or of completion date.

## New or Remodeled/Expanded Buildings

- All new construction, reconstruction, and modifications to building will be pre-approved by the BLM prior to implementation.

- Any new buildings must be designed to accommodate multiple users along with fitting into the physical environment as defined in a site-specific environmental analysis developed at the time of the proposal.  New buildings shall be constructed to meet Uniform Building Codes (UBC) and be fire resistant.

- Buildings are required to be one-story.  The roof must be metal, covered with metal, concrete, or other fire resistant material.  Roofs can be equipped with antenna support structures, such as poles and railings that can extend up to 25-feet above ground level.

- Facility Owners and Facility Managers are encouraged to construct the interior of their buildings in a modular fashion, so that they can:

a.	Sublease sections to others;

b.	Provide tenants and customers with internal separation and security;

c.	Reduce physical interference; and

d.	Increase management effectiveness.

- The following materials are approved for construction of new facilities (i.e. buildings).  The use of other construction materials not listed would require review and approval by the BLM on a case-by-case basis.

#### a.	Floors – Concrete slab with drainage is preferred.

b.	Walls – Concrete block, metal or pre-fabricated concrete.

c.	Roof – Metal, or concrete, painted to eliminate shiny surfaces, or other fireproof material as approved by the BLM.

d.	Partitions – If partitions are necessary in buildings, ensure they are constructed with fire resistant material (e.g., concrete block, reinforced concrete, sheetrock, or properly grounded fencing).

e.	Color – Proposed color for use on all exterior building surfaces must be pre-approved by the BLM. The goal of the color selection for the facilities is to make the building as inconspicuous as possible and make buildings located on the skyline look inconspicuous when viewed from a distance.  The intent is to reduce or eliminate glare from reflective and/or illuminated surfaces such as windowpanes, sheeting and reflective paints.  Non-reflective, BLM approved colors will be used on equipment buildings.

f.	Prefabricated building may be authorized with prior approval by the BLM.

- Building entry lights must:

a.	Only light the immediate area in the vicinity of the door;

b.	Be motion activated and have a limited time duration (e.g., 3-5 minutes); and

c.	Have a shielded beam that is pointed at the building door.

Requests for all-night (i.e. “dusk-to-dawn”) lighting, or entry lighting that would be visible from outside of the site will not be approved. FAA required lighting would be the only exception.

## New or Remodeled/Expanded Towers

- All new construction, reconstruction, and modifications to towers will be pre-approved by the BLM prior to implementation.

- It is the applicant/holder’s responsibility to assure that a new, or modified, structure will not unduly interfere electronically or physically with any existing equipment at the site.  Towers must be spaced, so as to prevent ground level radiation and/or interference problems.  This must be clearly demonstrated in writing to the BLM prior to issuance of a new lease/ROW or amendment.

- All new towers will comply with current structural and safety specifications and design standards, including safety-climbing devices.  Towers should be as narrow and “open” as safety and structural integrity allow.  Towers must be designed to meet on site wind and icing conditions estimated to be 70 mph with 1 inch ice and otherwise meet the EIA/TIA-222 standards.

SITE ASSOCIATION/ADVISORY GROUP

A Site Users’ Association at this site is not necessary due to the existence of only one facility and the limitations for future development.  However, if the users want to form an association, they can, subject to BLM approval.  If future development at the site were to reach three (3) facilities, a Site User’s Association shall be formed.

APPENDICIES

## Communication Site Plat

## B.	Authorized Facilities

## C.	Inspection Checklist

## D.	Site Photographs

## APPENDIX A

COMMUNICATION SITE PLAT

(See associated AutoCAD Map - in development)

APPENDIX B

LESEE/HOLDER FACILITY TABLE

(See associated User’s Table on the Website)

|  | Auth # | Use | Building | Tower | Access/Parking | Other |
| --- | --- | --- | --- | --- | --- | --- |
| Facility # 1 NPS | COC 59910 | PMRS | 8'x 10' metal siding | 48' guyed | Access and parking | Solar Panels |
| Delta County | COC 60533 | PMRS |  |  |  |  |
| Montrose County | COC 63197 | PMRS |  |  |  |  |

PMRS – Private Mobile Radio Service

Appendix C

“Green Mountain Annual Technical Inspection”

Date Inspected: _____________________________   	Time Inspection: ________________________________

Permit Holder: ______________________________  	Authorization # _________________________________

Site Technician : ____________________________   	 Phone # _______________________________________

Number of Transmitters ______________________   	 License Posted _________________________________

Please mark the following Items as Acceptable (A) or Unacceptable (U).

Electrical Wiring ------------------- (A)     (U)        	Grounding --------------------- (A)     (U)

Equipment Installation ------------ (A)     (U)	Housekeeping ----------------- (A)     (U)

Building Repair -------------------- (A)     (U)	Tower Repair ------------------ (A)     (U)

Please mark the following Items as Yes (Y) or NO (N) or (NA)

Isolators ---------------------------- (Y)     (N)     (NA)	Circulators --------------------- (Y)     (N)     (NA)

Cavities ----------------------------- (Y)     (N)     (NA)	Terminators -------------------- (Y)     (N)     (NA)

Filters ------------------------------- (Y)     (N)     (NA)	Lightning Protection ---------- (Y)     (N)     (NA)

Comments: __________________________________________________________________________________

____________________________________________________________________________________________

Recommended Corrective Action:  ________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Required Corrective Action To Be Taken:  __________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

_____________________________________________________________________________________________

Committee Representatives:  _____________________________________________________________________

Bureau of Land Management Representatives: _______________________________________________________

Please make the required corrective action within the next 120 days.

Please make a written report of corrective action taken and submit to the BLM in Montrose.  If you should have any questions, please call the BLM office.

APPENDIX D

SITE PHOTOGRAPHS

(See associated Facility Photos on the Website)