## Beam
CHAPTER 17. ESTIMATING FIRE RESISTANCE TIME OF STEEL BEAMS
PROTECTED BY FIRE PROTECTION INSULATION (QUASI-STEADY-STATE APPROACH)
Version 1805.0
The following calculations estimate the fire resistance time for structural steel beams protected by spray-applied fire protection
insulating material.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Beam and Insulation Selected.
All subsequent output values are calculated by the spreadsheet, and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [5 empty] | 12.336 | lb/ft2
| Thickness of Spray-Applied Protection on Steel Beam (h) |  |  |  | h ≥ 1/16 in |  | 0.5 | in |  | 0.041667 | ft
| Density of Spray-Applied Material (ri) | [5 empty] | 19 | lb/ft3
| Thermal Conductivity of Spray-Applied Material (ki) | [5 empty] | 0.06936 | Btu/ft-hr-°F |  | 1.9267e-05 | Btu/ft-sec-°F
| Specific Heat of Spray-Applied Material (ci) | [5 empty] | 0.2868 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [5 empty] | 77 | °F
| Specific Heat of Steel (cs) | [5 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL BEAMS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 29.6162
| 36x280 | 27.756
| 36x260 | 25.8943
| 36x245 | 24.4816
| 36x230 | 23.0596
| 36x210 | 23.2773
| 36x194 | 21.5965
| 36x182 | 20.3286
| 36x170 | 19.053
| 36x160 | 17.991
| 36x150 | 16.9213
| 36x135 | 15.3191
| 33x241 | 25.3063
| 33x221 | 23.3194
| 33x201 | 21.314
| 33x152 | 18.1664
| 33x141 | 16.9208
| 33x130 | 15.6705
| 33x118 | 14.2944
| 30x211 | 23.9671
| 30x191 | 21.8161
| 30x173 | 19.8613
| 30x132 | 17.4018
| 30x124 | 16.403
| 30x116 | 15.4025
| 30x108 | 14.4008
| 30x99 | 13.2574
| 27x178 | 22.1519
| 27x161 | 20.1418
| 27x146 | 18.3561
| 27x114 | 16.3539
| 27x102 | 14.7124
| 27x94 | 13.6183
| 27x84 | 12.236
| 24x162 | 22.2286
| 24x146 | 20.1657
| 24x131 | 18.2124
| 24x117 | 16.3598
| 24x104 | 14.6187
| 24x94 | 15.0832
| 24x84 | 13.563
| 24x76 | 12.336
| 24x68 | 11.0983
| 24x62 | 10.9832
| 24x55 | 9.7974
| 21x147 | 21.9923
| 21x132 | 19.8795
| 21x122 | 18.4546
| 21x111 | 16.8736
| 21x101 | 15.4218
| 21x93 | 16.5726
| 21x83 | 14.889
| 21x73 | 13.1819
| 21x68 | 12.3244
| 21x62 | 11.2898
| 21x57 | 11.2205
| 21x50 | 9.919
| 21x44 | 8.7824
| 18x119 | 20.2769
| 18x106 | 18.2026
| 18x97 | 16.7374
| 18x86 | 14.937
| 18x76 | 13.2799
| 18x71 | 14.4763
| 18x65 | 13.3174
| 18x60 | 12.3499
| 18x55 | 11.3734
| 18x50 | 10.3887
| 18x46 | 10.3024
| 18x40 | 9.02
| 18x35 | 7.9545
| 16x100 | 18.7368
| 16x89 | 16.807
| 16x77 | 14.6632
| 16x67 | 12.8486
| 16x57 | 12.8186
| 16x50 | 11.3272
| 16x45 | 10.2515
| 16x40 | 9.1612
| 16x36 | 8.2941
| 16x31 | 7.7849
| 16x26 | 6.5851
| 14x730 | 94.836
| 14x665 | 88.1086
| 14x605 | 81.6694
| 14x550 | 75.5841
| 14x500 | 69.8893
| 14x455 | 64.6039
| 14x426 | 61.0935
| 14x398 | 57.6742
| 14x370 | 54.1761
| 14x342 | 50.7293
| 14x311 | 46.5859
| 14x283 | 42.8626
| 14x257 | 39.3392
| 14x233 | 36.0263
| 14x211 | 32.9344
| 14x193 | 30.3499
| 14x176 | 27.8886
| 14x159 | 25.2923
| 14x145 | 23.2932
| 14x132 | 21.9375
| 14x120 | 20.0585
| 14x109 | 18.318
| 14x99 | 16.7218
| 14x90 | 15.2715
| 14x82 | 16.9684
| 14x74 | 15.4033
| 14x68 | 14.2272
| 14x61 | 12.8387
| 14x53 | 12.4025
| 14x48 | 11.2963
| 14x43 | 10.1785
| 14x38 | 9.5218
| 14x34 | 8.5669
| 14x30 | 7.6062
| 14x26 | 7.3611
| 14x22 | 6.2827
| 12x336 | 57.3991
| 12x305 | 52.9705
| 12x279 | 49.1919
| 12x252 | 45.104
| 12x230 | 41.6824
| 12x210 | 38.5144
| 12x190 | 35.2668
| 12x170 | 31.9499
| 12x152 | 28.8973
| 12x136 | 26.1371
| 12x120 | 23.3085
| 12x106 | 20.7775
| 12x96 | 18.9474
| 12x87 | 17.2833
| 12x79 | 15.7842
| 12x72 | 14.4578
| 12x65 | 13.1181
| 12x58 | 12.9633
| 12x53 | 11.9068
| 12x50 | 12.5313
| 12x45 | 11.3481
| 12x40 | 10.1469
| 12x35 | 9.5281
| 12x30 | 8.2342
| 12x26 | 7.1807
| 12x22 | 7.2948
| 12x19 | 6.3572
| 12x16 | 5.4069
| 12x14 | 4.7552
| 10x112 | 25.622
| 10x100 | 23.1392
| 10x88 | 20.5988
| 10x77 | 18.2213
| 10x68 | 16.2388
| 10x60 | 14.4462
| 10x54 | 13.083
| 10x49 | 11.9318
| 10x45 | 12.3967
| 10x39 | 10.8421
| 10x33 | 9.261
| 10x30 | 9.5314
| 10x26 | 8.3311
| 10x22 | 7.114
| 10x19 | 7.1161
| 10x17 | 6.4212
| 10x15 | 5.7107
| 10x12 | 4.6095
| 8x67 | 19.2806
| 8x58 | 16.9178
| 8x48 | 14.2117
| 8x40 | 12.003
| 8x35 | 10.5823
| 8x31 | 9.438
| 8x28 | 9.5577
| 8x24 | 8.2628
| 8x21 | 7.9071
| 8x18 | 6.8419
| 8x15 | 6.4806
| 8x13 | 5.6686
| 8x10 | 4.4021
| 6x25 | 9.8814
| 6x20 | 8.016
| 6x15 | 6.1038
| 6x16 | 7.9569
| 6x12 | 6.1017
| 6x9 | 4.6392
| 5x19 | 9.1751
| 5x16 | 7.824
| 4x13 | 7.82
| User Specified Value | Enter Value
Select Beam
Scroll to desired beam size then Click on selection
THERMAL PROPERTIES OF SPRAY-APPLIED INSULATION MATERIALS
Insulation Material |  | Density | Thermal | Specific Heat | Select Insulation Type
Spray-Applied |  | ρi | Conductivity ki | ci
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F) | Scroll to desired material then Click on selection
Sprayed mineral fiber |  | 19 | 0.06936 | 0.2868
Perlite or vermiculite |  | 22 | 0.06936 | 0.2868
High density perlite or vermiculite |  | 35 | 0.06936 | 0.2868
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 179.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of FireProtection Engineering, 3rd Edition, 2002, Page 4-209.
cs W/D > 2 ci ri h
| Where | cs = specific heat of steel (Btu/lb-°F)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (BTU/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
| 1.6284 | > | 0.0016577
Temperature Rise in Steel Beam
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
| Where | DTs = temperature rise in steel (°F)
ki = thermal conductivity of spray-applied material (Btu/ft-sec-°F)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
Dt = 15.9 W/D
| Dt = | 196.1423 | sec
| Dt = | 3.269 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
| Tf = C1 LOG (0.133 t + 1) + Ta |  |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
| Where | Tf = fire exposure temperature (°F) |  |  | carbon steel structural members begin to fail. Predicted
|  | C1 = constant = 620 |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where | t1 = Dt/2
Ts0 = initial steel temperature (°F)
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
| Where | t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Time | Time | DTs | Ts |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°F) |  | (min) | (sec) | (°F) | (°F)
3.269 | 196.1423 | 39.6256 | 116.6256 |  | 173.259 | 10395.5417 | 102.6253 | 4782.5465 | failure of beam | Failure of Beam
6.5381 | 392.2846 | 53.1655 | 169.791 |  | 176.5281 | 10591.684 | 102.8929 | 4885.4394 | failure of beam | Failure of Beam
9.8071 | 588.4269 | 59.9222 | 229.7132 |  | 179.7971 | 10787.8263 | 103.1555 | 4988.5949 | failure of beam | Failure of Beam
13.0762 | 784.5692 | 64.5272 | 294.2404 |  | 183.0661 | 10983.9686 | 103.4134 | 5092.0083 | failure of beam | Failure of Beam
16.3452 | 980.7115 | 68.0036 | 362.244 |  | 186.3352 | 11180.1109 | 103.6667 | 5195.6749 | failure of beam | Failure of Beam
19.6142 | 1176.8538 | 70.7965 | 433.0405 |  | 189.6042 | 11376.2532 | 103.9155 | 5299.5904 | failure of beam | Failure of Beam
22.8833 | 1372.9961 | 73.1303 | 506.1709 |  | 192.8733 | 11572.3955 | 104.16 | 5403.7504 | failure of beam | Failure of Beam
26.1523 | 1569.1384 | 75.1348 | 581.3056 |  | 196.1423 | 11768.5378 | 104.4005 | 5508.1509 | failure of beam | Failure of Beam
29.4213 | 1765.2807 | 76.8913 | 658.1969 |  | 199.4113 | 11964.6801 | 104.6369 | 5612.7878 | failure of beam | Failure of Beam
32.6904 | 1961.423 | 78.4544 | 736.6513 |  | 202.6804 | 12160.8224 | 104.8694 | 5717.6572 | failure of beam | Failure of Beam
35.9594 | 2157.5653 | 79.8626 | 816.514 |  | 205.9494 | 12356.9647 | 105.0982 | 5822.7554 | failure of beam | Failure of Beam
39.2285 | 2353.7076 | 81.1438 | 897.6578 |  | 209.2184 | 12553.107 | 105.3234 | 5928.0788 | failure of beam | Failure of Beam
42.4975 | 2549.8499 | 82.319 | 979.9767 |  | 212.4875 | 12749.2493 | 105.545 | 6033.6238 | failure of beam | Failure of Beam
45.7665 | 2745.9922 | 83.4043 | 1063.3811 | Failure of Beam | 215.7565 | 12945.3916 | 105.7633 | 6139.3871 | failure of beam | Failure of Beam
49.0356 | 2942.1345 | 84.4127 | 1147.7937 | Failure of Beam | 219.0256 | 13141.5339 | 105.9782 | 6245.3653 | failure of beam | Failure of Beam
52.3046 | 3138.2767 | 85.3541 | 1233.1479 | Failure of Beam | 222.2946 | 13337.6762 | 106.19 | 6351.5553 | failure of beam | Failure of Beam
55.5737 | 3334.419 | 86.2371 | 1319.385 | Failure of Beam | 225.5636 | 13533.8185 | 106.3986 | 6457.9539 | failure of beam | Failure of Beam
58.8427 | 3530.5613 | 87.0684 | 1406.4533 | Failure of Beam | 228.8327 | 13729.9608 | 106.6042 | 6564.5582 | failure of beam | Failure of Beam
62.1117 | 3726.7036 | 87.8537 | 1494.3071 | Failure of Beam | 232.1017 | 13926.1031 | 106.8069 | 6671.3651 | failure of beam | Failure of Beam
65.3808 | 3922.8459 | 88.5979 | 1582.905 | Failure of Beam | 235.3708 | 14122.2454 | 107.0068 | 6778.3719 | failure of beam | Failure of Beam
68.6498 | 4118.9882 | 89.3051 | 1672.21 | Failure of Beam | 238.6398 | 14318.3877 | 107.2038 | 6885.5757 | failure of beam | Failure of Beam
71.9188 | 4315.1305 | 89.9787 | 1762.1887 | Failure of Beam | 241.9088 | 14514.53 | 107.3982 | 6992.9738 | failure of beam | Failure of Beam
75.1879 | 4511.2728 | 90.6218 | 1852.8105 | Failure of Beam | 245.1779 | 14710.6723 | 107.5899 | 7100.5638 | failure of beam | Failure of Beam
78.4569 | 4707.4151 | 91.237 | 1944.0475 | Failure of Beam | 248.4469 | 14906.8146 | 107.7791 | 7208.3429 | failure of beam | Failure of Beam
81.726 | 4903.5574 | 91.8268 | 2035.8743 | Failure of Beam | 251.7159 | 15102.9569 | 107.9658 | 7316.3087 | failure of beam | Failure of Beam
84.995 | 5099.6997 | 92.393 | 2128.2673 | Failure of Beam | 254.985 | 15299.0992 | 108.1501 | 7424.4588 | failure of beam | Failure of Beam
88.264 | 5295.842 | 92.9375 | 2221.2047 | Failure of Beam | 258.254 | 15495.2414 | 108.332 | 7532.7908 | failure of beam | Failure of Beam
91.5331 | 5491.9843 | 93.4619 | 2314.6666 | Failure of Beam | 261.5231 | 15691.3837 | 108.5116 | 7641.3024 | failure of beam | Failure of Beam
94.8021 | 5688.1266 | 93.9676 | 2408.6342 | Failure of Beam | 264.7921 | 15887.526 | 108.689 | 7749.9914 | failure of beam | Failure of Beam
98.0711 | 5884.2689 | 94.456 | 2503.0902 | Failure of Beam | 268.0611 | 16083.6683 | 108.8642 | 7858.8556 | failure of beam | Failure of Beam
101.3402 | 6080.4112 | 94.9281 | 2598.0183 | Failure of Beam | 271.3302 | 16279.8106 | 109.0372 | 7967.8928 | failure of beam | Failure of Beam
104.6092 | 6276.5535 | 95.385 | 2693.4034 | Failure of Beam | 274.5992 | 16475.9529 | 109.2082 | 8077.101 | failure of beam | Failure of Beam
107.8783 | 6472.6958 | 95.8277 | 2789.2311 | Failure of Beam | 277.8683 | 16672.0952 | 109.3772 | 8186.4782 | failure of beam | Failure of Beam
111.1473 | 6668.8381 | 96.2571 | 2885.4881 | Failure of Beam | 281.1373 | 16868.2375 | 109.5441 | 8296.0223 | failure of beam | Failure of Beam
114.4163 | 6864.9804 | 96.6738 | 2982.1619 | Failure of Beam | 284.4063 | 17064.3798 | 109.7091 | 8405.7314 | failure of beam | Failure of Beam
117.6854 | 7061.1227 | 97.0786 | 3079.2405 | Failure of Beam | 287.6754 | 17260.5221 | 109.8722 | 8515.6036 | failure of beam | Failure of Beam
120.9544 | 7257.265 | 97.4723 | 3176.7128 | Failure of Beam | 290.9444 | 17456.6644 | 110.0335 | 8625.6371 | failure of beam | Failure of Beam
124.2235 | 7453.4073 | 97.8553 | 3274.5681 | Failure of Beam | 294.2134 | 17652.8067 | 110.193 | 8735.8301 | failure of beam | Failure of Beam
127.4925 | 7649.5496 | 98.2282 | 3372.7963 | Failure of Beam | 297.4825 | 17848.949 | 110.3507 | 8846.1808 | failure of beam | Failure of Beam
130.7615 | 7845.6919 | 98.5916 | 3471.3879 | Failure of Beam | 300.7515 | 18045.0913 | 110.5066 | 8956.6874 | failure of beam | Failure of Beam
134.0306 | 8041.8342 | 98.946 | 3570.3339 | Failure of Beam | 304.0206 | 18241.2336 | 110.6609 | 9067.3482 | failure of beam | Failure of Beam
137.2996 | 8237.9765 | 99.2917 | 3669.6257 | Failure of Beam | 307.2896 | 18437.3759 | 110.8135 | 9178.1617 | failure of beam | Failure of Beam
140.5686 | 8434.1188 | 99.6293 | 3769.2549 | Failure of Beam | 310.5586 | 18633.5182 | 110.9645 | 9289.1262 | failure of beam | Failure of Beam
143.8377 | 8630.2611 | 99.9589 | 3869.2139 | Failure of Beam | 313.8277 | 18829.6605 | 111.1139 | 9400.24 | failure of beam | Failure of Beam
147.1067 | 8826.4034 | 100.2811 | 3969.495 | Failure of Beam | 317.0967 | 19025.8028 | 111.2617 | 9511.5017 | failure of beam | Failure of Beam
150.3758 | 9022.5457 | 100.5962 | 4070.0912 | Failure of Beam | 320.3658 | 19221.9451 | 111.408 | 9622.9097 | failure of beam | Failure of Beam
153.6448 | 9218.688 | 100.9044 | 4170.9956 | Failure of Beam | 323.6348 | 19418.0874 | 111.5528 | 9734.4626 | failure of beam | Failure of Beam
156.9138 | 9414.8302 | 101.2061 | 4272.2017 | Failure of Beam | 326.9038 | 19614.2297 | 111.6962 | 9846.1588 | failure of beam | Failure of Beam
160.1829 | 9610.9725 | 101.5015 | 4373.7032 | Failure of Beam | 330.1729 | 19810.372 | 111.8381 | 9957.9969 | failure of beam | Failure of Beam
163.4519 | 9807.1148 | 101.7909 | 4475.4941 | Failure of Beam | 333.4419 | 20006.5143 | 111.9787 | 10069.9756 | failure of beam | Failure of Beam
166.721 | 10003.2571 | 102.0745 | 4577.5686 | Failure of Beam | 336.7109 | 20202.6566 | 112.1178 | 10182.0934 | failure of beam | Failure of Beam
169.99 | 10199.3994 | 102.3526 | 4679.9212 | Failure of Beam | 339.98 | 20398.7989 | 112.2556 | 10294.3491 | failure of beam | Failure of Beam
The Failure Temperature for Steel Beams is Assumed at 1000 °F (538 °C)
The above calculations are based on principles developed in the Society of Fire Protection
Engineers (SFPE) Handbook of Fire Protection Engineering, 3rd Edition 2002.
Calculations are based on certain assumptions and have inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a given
situation, and should only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | January 2005
Note on I19: This default value (0.132) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Column
CHAPTER 17. ESTIMATING FIRE RESISTANCE TIME OF STEEL COLUMNS
PROTECTED BY FIRE PROTECTION INSULATION (QUASI-STEADY-STATE APPROACH)
Version 1805.0
The following calculations estimate the fire resistance time for structural steel columns protected by spray-applied fire protection
insulating material.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Column and Insulation Selected.
All subsequent output values are calculated by the spreadsheet, and based on values specified in the input
parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s).
The chapter in the NUREG should be read before an analysis is made.
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [5 empty] | 10.9986 | lb/ft2
| Thickness of Spray-Applied Protection on Steel Column (h) |  |  |  | h ≥ 1/16 in |  | 0.5 | in |  | 0.041667 | ft
| Density of Spray-Applied Material (ri) | [5 empty] | 19 | lb/ft3
| Thermal Conductivity of Spray-Applied Material (ki) | [5 empty] | 0.06936 | Btu/ft-hr-°F |  | 1.9267e-05 | Btu/lb-sec-°F
| Specific Heat of Spray-Applied Material (ci) | [5 empty] | 0.2868 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [5 empty] | 77 | °F
| Specific Heat of Steel (cs) | [5 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL COLUMNS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 26.0473
| 36x280 | 24.4097
| 36x260 | 22.7671
| 36x245 | 21.5227
| 36x230 | 20.2703
| 36x210 | 20.9233
| 36x194 | 19.4146
| 36x182 | 18.2746
| 36x170 | 17.1285
| 36x160 | 16.1725
| 36x150 | 15.2091
| 36x135 | 13.7638
| 33x241 | 22.2222
| 33x221 | 20.474
| 33x201 | 18.7107
| 33x152 | 16.2901
| 33x141 | 15.1708
| 33x130 | 14.0465
| 33x118 | 12.8098
| 30x211 | 20.9689
| 30x191 | 19.0841
| 30x173 | 17.3709
| 30x132 | 15.5952
| 30x124 | 14.6992
| 30x116 | 13.7999
| 30x108 | 12.8994
| 30x99 | 11.8729
| 27x178 | 19.3286
| 27x161 | 17.5732
| 27x146 | 16.0132
| 27x114 | 14.5967
| 27x102 | 13.1316
| 27x94 | 12.1526
| 27x84 | 10.9162
| 24x162 | 19.3606
| 24x146 | 17.5586
| 24x131 | 15.8516
| 24x117 | 14.2365
| 24x104 | 12.7191
| 24x94 | 13.4526
| 24x84 | 12.095
| 24x76 | 10.9986
| 24x68 | 9.8921
| 24x62 | 9.9492
| 24x55 | 8.8745
| 21x147 | 19.025
| 21x132 | 17.195
| 21x122 | 15.9616
| 21x111 | 14.5925
| 21x101 | 13.3363
| 21x93 | 14.7307
| 21x83 | 13.2359
| 21x73 | 11.7191
| 21x68 | 10.956
| 21x62 | 10.0351
| 21x57 | 10.1318
| 21x50 | 8.9526
| 21x44 | 7.9255
| 18x119 | 17.4807
| 18x106 | 15.6882
| 18x97 | 14.4256
| 18x86 | 12.871
| 18x76 | 11.4415
| 18x71 | 12.814
| 18x65 | 11.7896
| 18x60 | 10.9339
| 18x55 | 10.0671
| 18x50 | 9.1954
| 18x46 | 9.2555
| 18x40 | 8.104
| 18x35 | 7.1429
| 16x100 | 16.1139
| 16x89 | 14.45
| 16x77 | 12.604
| 16x67 | 11.0424
| 16x57 | 11.3095
| 16x50 | 9.9933
| 16x45 | 9.0437
| 16x40 | 8.0822
| 16x36 | 7.3134
| 16x31 | 6.9781
| 16x26 | 5.9002
| 14x730 | 79.4486
| 14x665 | 73.7387
| 14x605 | 68.2908
| 14x550 | 63.1458
| 14x500 | 58.3317
| 14x455 | 53.8727
| 14x426 | 50.9316
| 14x398 | 48.0483
| 14x370 | 45.1082
| 14x342 | 42.1962
| 14x311 | 38.7378
| 14x283 | 35.6199
| 14x257 | 32.673
| 14x233 | 29.9037
| 14x211 | 27.3198
| 14x193 | 25.1684
| 14x176 | 23.1123
| 14x159 | 20.9454
| 14x145 | 19.2905
| 14x132 | 18.2216
| 14x120 | 16.6551
| 14x109 | 15.2075
| 14x99 | 13.8769
| 14x90 | 12.6701
| 14x82 | 14.4451
| 14x74 | 13.1128
| 14x68 | 12.1086
| 14x61 | 10.9237
| 14x53 | 10.7179
| 14x48 | 9.7594
| 14x43 | 8.792
| 14x38 | 8.3425
| 14x34 | 7.5041
| 14x30 | 6.6593
| 14x26 | 6.5809
| 14x22 | 5.6146
| 12x336 | 48.2124
| 12x305 | 44.4552
| 12x279 | 41.2315
| 12x252 | 37.7764
| 12x230 | 34.8881
| 12x210 | 32.2168
| 12x190 | 29.4878
| 12x170 | 26.6946
| 12x152 | 24.127
| 12x136 | 21.8065
| 12x120 | 19.4332
| 12x106 | 17.3203
| 12x96 | 15.7895
| 12x87 | 14.394
| 12x79 | 13.1411
| 12x72 | 12.0334
| 12x65 | 10.9152
| 12x58 | 10.9262
| 12x53 | 10.03
| 12x50 | 10.7219
| 12x45 | 9.707
| 12x40 | 8.6784
| 12x35 | 8.2938
| 12x30 | 7.1656
| 12x26 | 6.2475
| 12x22 | 6.5639
| 12x19 | 5.7186
| 12x16 | 4.8608
| 12x14 | 4.2748
| 10x112 | 21.3774
| 10x100 | 19.2926
| 10x88 | 17.1624
| 10x77 | 15.1724
| 10x68 | 13.5144
| 10x60 | 12.016
| 10x54 | 10.8798
| 10x49 | 9.919
| 10x45 | 10.4692
| 10x39 | 9.1496
| 10x33 | 7.8076
| 10x30 | 8.2607
| 10x26 | 7.2189
| 10x22 | 6.1596
| 10x19 | 6.3228
| 10x17 | 5.7015
| 10x15 | 5.0676
| 10x12 | 4.0909
| 8x67 | 16.0864
| 8x58 | 14.1005
| 8x48 | 11.8421
| 8x40 | 9.9875
| 8x35 | 8.8028
| 8x31 | 7.8464
| 8x28 | 8.0595
| 8x24 | 6.9649
| 8x21 | 6.7851
| 8x18 | 5.8664
| 8x15 | 5.6622
| 8x13 | 4.9492
| 8x10 | 3.8462
| 6x25 | 8.2327
| 6x20 | 6.6741
| 6x15 | 5.0733
| 6x16 | 6.8182
| 6x12 | 5.2174
| 6x9 | 3.9677
| 5x19 | 7.6305
| 5x16 | 6.4997
| 4x13 | 6.5
| User Specified Value | Enter Value
Select Column
Scroll to desired column size then Click on selection
THERMAL PROPERTIES OF SPRAY-APPLIED INSULATION MATERIALS
Insulation Material |  | Density | Thermal | Specific Heat | Select Insulation Type
Spray-Applied |  | ρi | Conductivity ki | ci
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F) | Scroll to desired material then Click on selection
Sprayed mineral fiber |  | 19 | 0.06936 | 0.2868
Perlite or vermiculite |  | 22 | 0.06936 | 0.2868
High density perlite or vermiculite |  | 35 | 0.06936 | 0.2868
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 182.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of FireProtection Engineering, 3rd Edition, 2002, Page 4-209.
cs W/D > 2 ci ri h
| Where | cs = specific heat of steel (Btu/lb-°F)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (ci)
h = thickness of spray-applied protection on steel column (in)
| 1.4518 | > | 0.0016577
Temperature Rise in Steel Column
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
| Where | DTs = temperature rise in steel (°F)
ki = thermal conductivity of spray-applied material (Btu/ft-sec-°F)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
Dt = 15.9 W/D
| Dt = | 174.877 | sec
| Dt = | 2.9146 | minutes
| For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression |  |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
| Tf = C1 LOG (0.133 t + 1) + T0 |  |  |  | carbon steel structural members begin to fail. Predicted
| Where | Tf = fire exposure temperature (°F) |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
C1 = constant = 620
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where | t1 = Dt/2
Ts0 = initial steel temperature (°F)
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
| Where | t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Time | Time | DTs | Ts |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°F) |  | (min) | (sec) | (°F) | (°F)
2.9146 | 174.877 | 38.0338 | 115.0338 |  | 177.7916 | 10667.4964 | 103.0077 | 5513.6454 | failure of column | Failure of Column
5.8292 | 349.754 | 51.5784 | 166.6122 |  | 180.7062 | 10842.3734 | 103.2402 | 5616.8856 | failure of column | Failure of Column
8.7438 | 524.631 | 58.317 | 224.9292 |  | 183.6208 | 11017.2504 | 103.469 | 5720.3546 | failure of column | Failure of Column
11.6585 | 699.508 | 62.9153 | 287.8445 |  | 186.5355 | 11192.1274 | 103.6942 | 5824.0488 | failure of column | Failure of Column
14.5731 | 874.3849 | 66.3877 | 354.2323 |  | 189.4501 | 11367.0043 | 103.9158 | 5927.9646 | failure of column | Failure of Column
17.4877 | 1049.2619 | 69.178 | 423.4103 |  | 192.3647 | 11541.8813 | 104.134 | 6032.0986 | failure of column | Failure of Column
20.4023 | 1224.1389 | 71.5101 | 494.9204 |  | 195.2793 | 11716.7583 | 104.349 | 6136.4476 | failure of column | Failure of Column
23.3169 | 1399.0159 | 73.5132 | 568.4336 |  | 198.1939 | 11891.6353 | 104.5607 | 6241.0083 | failure of column | Failure of Column
26.2315 | 1573.8929 | 75.2687 | 643.7023 |  | 201.1085 | 12066.5123 | 104.7693 | 6345.7776 | failure of column | Failure of Column
29.1462 | 1748.7699 | 76.8311 | 720.5334 |  | 204.0232 | 12241.3893 | 104.9749 | 6450.7525 | failure of column | Failure of Column
32.0608 | 1923.6469 | 78.2386 | 798.772 |  | 206.9378 | 12416.2663 | 105.1776 | 6555.9301 | failure of column | Failure of Column
34.9754 | 2098.5239 | 79.5192 | 878.2912 |  | 209.8524 | 12591.1433 | 105.3774 | 6661.3075 | failure of column | Failure of Column
37.89 | 2273.4009 | 80.694 | 958.9852 |  | 212.767 | 12766.0203 | 105.5745 | 6766.882 | failure of column | Failure of Column
40.8046 | 2448.2779 | 81.7789 | 1040.7641 | Failure of Column | 215.6816 | 12940.8973 | 105.7688 | 6872.6508 | failure of column | Failure of Column
43.7192 | 2623.1548 | 82.7869 | 1123.5511 | Failure of Column | 218.5962 | 13115.7742 | 105.9605 | 6978.6113 | failure of column | Failure of Column
46.6339 | 2798.0318 | 83.7281 | 1207.2792 | Failure of Column | 221.5109 | 13290.6512 | 106.1497 | 7084.761 | failure of column | Failure of Column
49.5485 | 2972.9088 | 84.6108 | 1291.89 | Failure of Column | 224.4255 | 13465.5282 | 106.3364 | 7191.0974 | failure of column | Failure of Column
52.4631 | 3147.7858 | 85.4419 | 1377.3319 | Failure of Column | 227.3401 | 13640.4052 | 106.5207 | 7297.6181 | failure of column | Failure of Column
55.3777 | 3322.6628 | 86.227 | 1463.5589 | Failure of Column | 230.2547 | 13815.2822 | 106.7026 | 7404.3207 | failure of column | Failure of Column
58.2923 | 3497.5398 | 86.971 | 1550.5299 | Failure of Column | 233.1693 | 13990.1592 | 106.8822 | 7511.2029 | failure of column | Failure of Column
61.2069 | 3672.4168 | 87.678 | 1638.2079 | Failure of Column | 236.0839 | 14165.0362 | 107.0596 | 7618.2624 | failure of column | Failure of Column
64.1216 | 3847.2938 | 88.3515 | 1726.5594 | Failure of Column | 238.9986 | 14339.9132 | 107.2347 | 7725.4972 | failure of column | Failure of Column
67.0362 | 4022.1708 | 88.9944 | 1815.5538 | Failure of Column | 241.9132 | 14514.7902 | 107.4078 | 7832.9049 | failure of column | Failure of Column
69.9508 | 4197.0478 | 89.6096 | 1905.1634 | Failure of Column | 244.8278 | 14689.6671 | 107.5787 | 7940.4837 | failure of column | Failure of Column
72.8654 | 4371.9247 | 90.1992 | 1995.3626 | Failure of Column | 247.7424 | 14864.5441 | 107.7477 | 8048.2314 | failure of column | Failure of Column
75.78 | 4546.8017 | 90.7653 | 2086.1279 | Failure of Column | 250.657 | 15039.4211 | 107.9146 | 8156.146 | failure of column | Failure of Column
78.6946 | 4721.6787 | 91.3097 | 2177.4376 | Failure of Column | 253.5716 | 15214.2981 | 108.0796 | 8264.2256 | failure of column | Failure of Column
81.6093 | 4896.5557 | 91.834 | 2269.2716 | Failure of Column | 256.4863 | 15389.1751 | 108.2427 | 8372.4683 | failure of column | Failure of Column
84.5239 | 5071.4327 | 92.3397 | 2361.6113 | Failure of Column | 259.4009 | 15564.0521 | 108.404 | 8480.8723 | failure of column | Failure of Column
87.4385 | 5246.3097 | 92.8279 | 2454.4392 | Failure of Column | 262.3155 | 15738.9291 | 108.5634 | 8589.4357 | failure of column | Failure of Column
90.3531 | 5421.1867 | 93.3 | 2547.7392 | Failure of Column | 265.2301 | 15913.8061 | 108.7211 | 8698.1568 | failure of column | Failure of Column
93.2677 | 5596.0637 | 93.7569 | 2641.4961 | Failure of Column | 268.1447 | 16088.6831 | 108.8771 | 8807.0339 | failure of column | Failure of Column
96.1823 | 5770.9407 | 94.1995 | 2735.6956 | Failure of Column | 271.0593 | 16263.5601 | 109.0313 | 8916.0652 | failure of column | Failure of Column
99.097 | 5945.8177 | 94.6288 | 2830.3244 | Failure of Column | 273.974 | 16438.437 | 109.1839 | 9025.2491 | failure of column | Failure of Column
102.0116 | 6120.6946 | 95.0454 | 2925.3698 | Failure of Column | 276.8886 | 16613.314 | 109.3349 | 9134.584 | failure of column | Failure of Column
104.9262 | 6295.5716 | 95.4502 | 3020.82 | Failure of Column | 279.8032 | 16788.191 | 109.4843 | 9244.0683 | failure of column | Failure of Column
107.8408 | 6470.4486 | 95.8438 | 3116.6638 | Failure of Column | 282.7178 | 16963.068 | 109.6321 | 9353.7004 | failure of column | Failure of Column
110.7554 | 6645.3256 | 96.2268 | 3212.8906 | Failure of Column | 285.6324 | 17137.945 | 109.7784 | 9463.4789 | failure of column | Failure of Column
113.67 | 6820.2026 | 96.5997 | 3309.4902 | Failure of Column | 288.547 | 17312.822 | 109.9232 | 9573.4021 | failure of column | Failure of Column
116.5847 | 6995.0796 | 96.9631 | 3406.4533 | Failure of Column | 291.4616 | 17487.699 | 110.0666 | 9683.4687 | failure of column | Failure of Column
119.4993 | 7169.9566 | 97.3174 | 3503.7707 | Failure of Column | 294.3763 | 17662.576 | 110.2085 | 9793.6773 | failure of column | Failure of Column
122.4139 | 7344.8336 | 97.6631 | 3601.4337 | Failure of Column | 297.2909 | 17837.453 | 110.3491 | 9904.0263 | failure of column | Failure of Column
125.3285 | 7519.7106 | 98.0005 | 3699.4343 | Failure of Column | 300.2055 | 18012.33 | 110.4882 | 10014.5145 | failure of column | Failure of Column
128.2431 | 7694.5876 | 98.3302 | 3797.7644 | Failure of Column | 303.1201 | 18187.2069 | 110.626 | 10125.1405 | failure of column | Failure of Column
131.1577 | 7869.4645 | 98.6524 | 3896.4168 | Failure of Column | 306.0347 | 18362.0839 | 110.7625 | 10235.903 | failure of column | Failure of Column
134.0724 | 8044.3415 | 98.9674 | 3995.3842 | Failure of Column | 308.9493 | 18536.9609 | 110.8976 | 10346.8006 | failure of column | Failure of Column
136.987 | 8219.2185 | 99.2756 | 4094.6598 | Failure of Column | 311.864 | 18711.8379 | 111.0315 | 10457.8322 | failure of column | Failure of Column
139.9016 | 8394.0955 | 99.5772 | 4194.237 | Failure of Column | 314.7786 | 18886.7149 | 111.1642 | 10568.9964 | failure of column | Failure of Column
142.8162 | 8568.9725 | 99.8726 | 4294.1096 | Failure of Column | 317.6932 | 19061.5919 | 111.2956 | 10680.292 | failure of column | Failure of Column
145.7308 | 8743.8495 | 100.162 | 4394.2716 | Failure of Column | 320.6078 | 19236.4689 | 111.4258 | 10791.7178 | failure of column | Failure of Column
148.6454 | 8918.7265 | 100.4456 | 4494.7171 | Failure of Column | 323.5224 | 19411.3459 | 111.5549 | 10903.2727 | failure of column | Failure of Column
151.5601 | 9093.6035 | 100.7236 | 4595.4407 | Failure of Column | 326.437 | 19586.2229 | 111.6827 | 11014.9554 | failure of column | Failure of Column
154.4747 | 9268.4805 | 100.9963 | 4696.437 | Failure of Column | 329.3517 | 19761.0999 | 111.8095 | 11126.7649 |  | Failure of Column
157.3893 | 9443.3575 | 101.2638 | 4797.7008 | Failure of Column | 332.2663 | 19935.9768 | 111.9351 | 11238.7 |  | Failure of Column
160.3039 | 9618.2344 | 101.5265 | 4899.2273 | Failure of Column | 335.1809 | 20110.8538 | 112.0596 | 11350.7596 |  | Failure of Column
163.2185 | 9793.1114 | 101.7843 | 5001.0116 | Failure of Column | 338.0955 | 20285.7308 | 112.183 | 11462.9426 |  | Failure of Column
166.1331 | 9967.9884 | 102.0376 | 5103.0491 | Failure of Column | 341.0101 | 20460.6078 | 112.3054 | 11575.248 |  | Failure of Column
169.0478 | 10142.8654 | 102.2864 | 5205.3355 | Failure of Column | 343.9247 | 20635.4848 | 112.4267 | 11687.6747 |  | Failure of Column
171.9624 | 10317.7424 | 102.5309 | 5307.8664 | Failure of Column | 346.8394 | 20810.3618 | 112.547 | 11800.2217 |  | Failure of Column
174.877 | 10492.6194 | 102.7713 | 5410.6377 | Failure of Column | 349.754 | 20985.2388 | 112.6663 | 11912.888 |  | Failure of Column
The Failure Temperature for Steel Columns is Assumed at 1000 °F (538 °C)
The above calculations are based on principles developed in the Society of Fire Protection
Engineers (SFPE) Handbook of Fire Protection Engineering, 3rd Edition 2002.
Calculations are based on certain assumptions and have inherent limitations. The results
of such calculations may or may not have reasonable predictive capabilities for a given
situation, and should only be interpreted by an informed user.
Although each calculation in the spreadsheet has been verified with the results of hand calculation,
there is no absolute guarantee of the accuracy of these calculations.
Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet,
please send an email to nxi@nrc.gov or mxs3@nrc.gov.
Prepared by: |  | Date |  | Organization
Checked by: |  | Date |  | Organization
Additional Information
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | January 2005
Note on I19: This default value (0.132) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Data
SECTIONAL FACTORS FOR STEEL MEMBERS
| BEAMS |  | COLUMNS
| Structural Shape | W/D Ratio | Structural Shape | W/D Ratio
| W Shapes | (lb/ft2) | W Shapes | (lb/ft2)
| 36x300 | 29.6162 | 36x300 | 26.0473
| 36x280 | 27.756 | 36x280 | 24.4097
| 36x260 | 25.8943 | 36x260 | 22.7671
| 36x245 | 24.4816 | 36x245 | 21.5227
| 36x230 | 23.0596 | 36x230 | 20.2703
| 36x210 | 23.2773 | 36x210 | 20.9233
| 36x194 | 21.5965 | 36x194 | 19.4146
| 36x182 | 20.3286 | 36x182 | 18.2746
| 36x170 | 19.053 | 36x170 | 17.1285
| 36x160 | 17.991 | 36x160 | 16.1725
| 36x150 | 16.9213 | 36x150 | 15.2091
| 36x135 | 15.3191 | 36x135 | 13.7638
| 33x241 | 25.3063 | 33x241 | 22.2222
| 33x221 | 23.3194 | 33x221 | 20.474
| 33x201 | 21.314 | 33x201 | 18.7107
| 33x152 | 18.1664 | 33x152 | 16.2901
| 33x141 | 16.9208 | 33x141 | 15.1708
| 33x130 | 15.6705 | 33x130 | 14.0465
| 33x118 | 14.2944 | 33x118 | 12.8098
| 30x211 | 23.9671 | 30x211 | 20.9689
| 30x191 | 21.8161 | 30x191 | 19.0841
| 30x173 | 19.8613 | 30x173 | 17.3709
| 30x132 | 17.4018 | 30x132 | 15.5952
| 30x124 | 16.403 | 30x124 | 14.6992
| 30x116 | 15.4025 | 30x116 | 13.7999
| 30x108 | 14.4008 | 30x108 | 12.8994
| 30x99 | 13.2574 | 30x99 | 11.8729
| 27x178 | 22.1519 | 27x178 | 19.3286
| 27x161 | 20.1418 | 27x161 | 17.5732
| 27x146 | 18.3561 | 27x146 | 16.0132
| 27x114 | 16.3539 | 27x114 | 14.5967
| 27x102 | 14.7124 | 27x102 | 13.1316
| 27x94 | 13.6183 | 27x94 | 12.1526
| 27x84 | 12.236 | 27x84 | 10.9162
| 24x162 | 22.2286 | 24x162 | 19.3606
| 24x146 | 20.1657 | 24x146 | 17.5586
| 24x131 | 18.2124 | 24x131 | 15.8516
| 24x117 | 16.3598 | 24x117 | 14.2365
| 24x104 | 14.6187 | 24x104 | 12.7191
| 24x94 | 15.0832 | 24x94 | 13.4526
| 24x84 | 13.563 | 24x84 | 12.095
| 24x76 | 12.336 | 24x76 | 10.9986
| 24x68 | 11.0983 | 24x68 | 9.8921
| 24x62 | 10.9832 | 24x62 | 9.9492
| 24x55 | 9.7974 | 24x55 | 8.8745
| 21x147 | 21.9923 | 21x147 | 19.025
| 21x132 | 19.8795 | 21x132 | 17.195
| 21x122 | 18.4546 | 21x122 | 15.9616
| 21x111 | 16.8736 | 21x111 | 14.5925
| 21x101 | 15.4218 | 21x101 | 13.3363
| 21x93 | 16.5726 | 21x93 | 14.7307
| 21x83 | 14.889 | 21x83 | 13.2359
| 21x73 | 13.1819 | 21x73 | 11.7191
| 21x68 | 12.3244 | 21x68 | 10.956
| 21x62 | 11.2898 | 21x62 | 10.0351
| 21x57 | 11.2205 | 21x57 | 10.1318
| 21x50 | 9.919 | 21x50 | 8.9526
| 21x44 | 8.7824 | 21x44 | 7.9255
| 18x119 | 20.2769 | 18x119 | 17.4807
| 18x106 | 18.2026 | 18x106 | 15.6882
| 18x97 | 16.7374 | 18x97 | 14.4256
| 18x86 | 14.937 | 18x86 | 12.871
| 18x76 | 13.2799 | 18x76 | 11.4415
| 18x71 | 14.4763 | 18x71 | 12.814
| 18x65 | 13.3174 | 18x65 | 11.7896
| 18x60 | 12.3499 | 18x60 | 10.9339
| 18x55 | 11.3734 | 18x55 | 10.0671
| 18x50 | 10.3887 | 18x50 | 9.1954
| 18x46 | 10.3024 | 18x46 | 9.2555
| 18x40 | 9.02 | 18x40 | 8.104
| 18x35 | 7.9545 | 18x35 | 7.1429
| 16x100 | 18.7368 | 16x100 | 16.1139
| 16x89 | 16.807 | 16x89 | 14.45
| 16x77 | 14.6632 | 16x77 | 12.604
| 16x67 | 12.8486 | 16x67 | 11.0424
| 16x57 | 12.8186 | 16x57 | 11.3095
| 16x50 | 11.3272 | 16x50 | 9.9933
| 16x45 | 10.2515 | 16x45 | 9.0437
| 16x40 | 9.1612 | 16x40 | 8.0822
| 16x36 | 8.2941 | 16x36 | 7.3134
| 16x31 | 7.7849 | 16x31 | 6.9781
| 16x26 | 6.5851 | 16x26 | 5.9002
| 14x730 | 94.836 | 14x730 | 79.4486
| 14x665 | 88.1086 | 14x665 | 73.7387
| 14x605 | 81.6694 | 14x605 | 68.2908
| 14x550 | 75.5841 | 14x550 | 63.1458
| 14x500 | 69.8893 | 14x500 | 58.3317
| 14x455 | 64.6039 | 14x455 | 53.8727
| 14x426 | 61.0935 | 14x426 | 50.9316
| 14x398 | 57.6742 | 14x398 | 48.0483
| 14x370 | 54.1761 | 14x370 | 45.1082
| 14x342 | 50.7293 | 14x342 | 42.1962
| 14x311 | 46.5859 | 14x311 | 38.7378
| 14x283 | 42.8626 | 14x283 | 35.6199
| 14x257 | 39.3392 | 14x257 | 32.673
| 14x233 | 36.0263 | 14x233 | 29.9037
| 14x211 | 32.9344 | 14x211 | 27.3198
| 14x193 | 30.3499 | 14x193 | 25.1684
| 14x176 | 27.8886 | 14x176 | 23.1123
| 14x159 | 25.2923 | 14x159 | 20.9454
| 14x145 | 23.2932 | 14x145 | 19.2905
| 14x132 | 21.9375 | 14x132 | 18.2216
| 14x120 | 20.0585 | 14x120 | 16.6551
| 14x109 | 18.318 | 14x109 | 15.2075
| 14x99 | 16.7218 | 14x99 | 13.8769
| 14x90 | 15.2715 | 14x90 | 12.6701
| 14x82 | 16.9684 | 14x82 | 14.4451
| 14x74 | 15.4033 | 14x74 | 13.1128
| 14x68 | 14.2272 | 14x68 | 12.1086
| 14x61 | 12.8387 | 14x61 | 10.9237
| 14x53 | 12.4025 | 14x53 | 10.7179
| 14x48 | 11.2963 | 14x48 | 9.7594
| 14x43 | 10.1785 | 14x43 | 8.792
| 14x38 | 9.5218 | 14x38 | 8.3425
| 14x34 | 8.5669 | 14x34 | 7.5041
| 14x30 | 7.6062 | 14x30 | 6.6593
| 14x26 | 7.3611 | 14x26 | 6.5809
| 14x22 | 6.2827 | 14x22 | 5.6146
| 12x336 | 57.3991 | 12x336 | 48.2124
| 12x305 | 52.9705 | 12x305 | 44.4552
| 12x279 | 49.1919 | 12x279 | 41.2315
| 12x252 | 45.104 | 12x252 | 37.7764
| 12x230 | 41.6824 | 12x230 | 34.8881
| 12x210 | 38.5144 | 12x210 | 32.2168
| 12x190 | 35.2668 | 12x190 | 29.4878
| 12x170 | 31.9499 | 12x170 | 26.6946
| 12x152 | 28.8973 | 12x152 | 24.127
| 12x136 | 26.1371 | 12x136 | 21.8065
| 12x120 | 23.3085 | 12x120 | 19.4332
| 12x106 | 20.7775 | 12x106 | 17.3203
| 12x96 | 18.9474 | 12x96 | 15.7895
| 12x87 | 17.2833 | 12x87 | 14.394
| 12x79 | 15.7842 | 12x79 | 13.1411
| 12x72 | 14.4578 | 12x72 | 12.0334
| 12x65 | 13.1181 | 12x65 | 10.9152
| 12x58 | 12.9633 | 12x58 | 10.9262
| 12x53 | 11.9068 | 12x53 | 10.03
| 12x50 | 12.5313 | 12x50 | 10.7219
| 12x45 | 11.3481 | 12x45 | 9.707
| 12x40 | 10.1469 | 12x40 | 8.6784
| 12x35 | 9.5281 | 12x35 | 8.2938
| 12x30 | 8.2342 | 12x30 | 7.1656
| 12x26 | 7.1807 | 12x26 | 6.2475
| 12x22 | 7.2948 | 12x22 | 6.5639
| 12x19 | 6.3572 | 12x19 | 5.7186
| 12x16 | 5.4069 | 12x16 | 4.8608
| 12x14 | 4.7552 | 12x14 | 4.2748
| 10x112 | 25.622 | 10x112 | 21.3774
| 10x100 | 23.1392 | 10x100 | 19.2926
| 10x88 | 20.5988 | 10x88 | 17.1624
| 10x77 | 18.2213 | 10x77 | 15.1724
| 10x68 | 16.2388 | 10x68 | 13.5144
| 10x60 | 14.4462 | 10x60 | 12.016
| 10x54 | 13.083 | 10x54 | 10.8798
| 10x49 | 11.9318 | 10x49 | 9.919
| 10x45 | 12.3967 | 10x45 | 10.4692
| 10x39 | 10.8421 | 10x39 | 9.1496
| 10x33 | 9.261 | 10x33 | 7.8076
| 10x30 | 9.5314 | 10x30 | 8.2607
| 10x26 | 8.3311 | 10x26 | 7.2189
| 10x22 | 7.114 | 10x22 | 6.1596
| 10x19 | 7.1161 | 10x19 | 6.3228
| 10x17 | 6.4212 | 10x17 | 5.7015
| 10x15 | 5.7107 | 10x15 | 5.0676
| 10x12 | 4.6095 | 10x12 | 4.0909
| 8x67 | 19.2806 | 8x67 | 16.0864
| 8x58 | 16.9178 | 8x58 | 14.1005
| 8x48 | 14.2117 | 8x48 | 11.8421
| 8x40 | 12.003 | 8x40 | 9.9875
| 8x35 | 10.5823 | 8x35 | 8.8028
| 8x31 | 9.438 | 8x31 | 7.8464
| 8x28 | 9.5577 | 8x28 | 8.0595
| 8x24 | 8.2628 | 8x24 | 6.9649
| 8x21 | 7.9071 | 8x21 | 6.7851
| 8x18 | 6.8419 | 8x18 | 5.8664
| 8x15 | 6.4806 | 8x15 | 5.6622
| 8x13 | 5.6686 | 8x13 | 4.9492
| 8x10 | 4.4021 | 8x10 | 3.8462
| 6x25 | 9.8814 | 6x25 | 8.2327
| 6x20 | 8.016 | 6x20 | 6.6741
| 6x15 | 6.1038 | 6x15 | 5.0733
| 6x16 | 7.9569 | 6x16 | 6.8182
| 6x12 | 6.1017 | 6x12 | 5.2174
| 6x9 | 4.6392 | 6x9 | 3.9677
| 5x19 | 9.1751 | 5x19 | 7.6305
| 5x16 | 7.824 | 5x16 | 6.4997
| 4x13 | 7.82 | 4x13 | 6.5
| User Specified Value | Enter Value | User Specified Value | Enter Value