Hazard Analysis For working in computer ROOMS

(2/2005) (CD-doc-627, version 3)

Description of Work: Installation, operation, testing, and repair of computing related equipment. (Note: This JHA is not meant to be job specific. It is meant to cover common safety elements of working in computer rooms. A specific job may require an additional HA, verbal or written. When in doubt, consult your supervisor.)

| Step/Phase of Job | Safety Hazard | Precautions/Safety Procedures |
| --- | --- | --- |
| Lifting equipment | Potential for back injury | Use proper lifting techniques. Seek assistance from others, use carts or equipment lifts provided in room. |
| Moving loads across floor | Possibility of load falling due to rolling over warped or unseated floor tiles or into floor tile cutouts. This could result in injury. | Check stability of load and condition of floor in the path of the move, reseating tiles where necessary. Make sure equipment is secure. Move load slowly. For loads exceeding 300 lbs, it is mandatory that you contact Building Management for assistance. |
| Inserting or removing computers from racks | Possibility that cabinet may become unstable and tip or fall causing serious injury | Check that the cabinet is steady and that stabilizing feet, if any, are snug to the floor. Do not pull out equipment so as to cause cabinet to tip. Be especially careful pulling out equipment in the higher bay areas of the cabinet. Do not pull out more than one unit at a time. |
| Working on equipment that is in racks | Rails holding equipment into rack may become partially disengaged when trying to fully extend them and gain access to parts in the very back of the equipment. The equipment could then fall out of the rack causing serious injury. | If the equipment design makes it necessary to extend the equipment fully in order to replace parts in it, either remove the equipment from the rack or use an equipment lift to support the equipment in the rack while you attempt to access it. |
| Removing/replacing floor tiles | Unmarked open floor areas could result in a person falling into open floor causing injuries. Lifting floor tiles could cause back injury. Handling floor tiles could cause pinch or cut to hands. | Encircle open floor tile area with yellow safety cones available at entrance doors. Place safety cones on loose tiles to prevent tripping over them. When floor tiles are replaced, ensure that they are fully seated and do not have any edges rising above adjacent tiles. If this is not possible, place safety cones around tile and contact Building Management. Use floor tile pullers provided at entrance doors. Use standup floor tile pullers whenever possible. For vented floor tiles, use special hook puller and wear gloves when handling these tiles. |
| Working underneath floor | Electrical cables could cause electric shock if shielding is broken. | Exercise care so as not to pull on cables which could break shielding |
| Using plug-in electrically powered tools | Electric shock potential | Use GFCI cord available from Building Management. |
| Working in aisles | Potential for trip hazard or aisle blockage for emergency exiting | Ensure cables, carts, etc. do not restrict pathways to less than 28”. Cables should not be strung across aisles. |
| Working on robotic equipment or mechanical equipment with moving parts | Injury to hands or other body parts | Follow specific lockout/tagout procedure when applicable. Individuals using lockout/tagout must be trained. Follow vendor safety procedures if it is necessary to troubleshoot equipment that is live. |
| Combustibles: packing materials and flammables | Potential for fire | Cardboard and packing materials are not allowed in computer rooms. If necessary, contact Building Management. Flammables, such as alcohol, are not permitted except for duration of use. |

Hazard Analysis For working in CD computer ROOMS

(12/2004) (CD-doc-627, version 2)

I understand the hazards and required precautionary actions.  I will follow the requirements of this hazard analysis or notify my supervisor if I am unable to do so.

Name (print)		ID		Signature			Date

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________

_________________	_________	_____________________	_______________