July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15833

CLEAN ROOM RECIRCULATION AIR-HANDLING UNITS

Page

PART 1 - GENERAL

1.01 Description.	2

1.02Related Work..	2

1.03Quality Assurance..	2

1.04References..	5

1.05Submittals	6

1.06 Delivery, Storage, and Handling..	8

PART 2 - PRODUCTS

2.01Acceptable Manufacturers..	9

2.02 Materials....	9

2.03 Equipment..	9

2.04 Fabrication....	10

2.05 Motors...	20

PART 3 - EXECUTION

3.01 Installation/Application/Erection...	22

3.02 Field Quality Control..	22

3.03 Commissioning..	22

SPECIAL SPECIFICATION

SECTION 15833

CLEAN ROOM RECIRCULATION AIR-HANDLING UNITS

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section specifies custom-built air-handling units and accessories, as indicated in the Drawings.

B.  	The units specified under this section are designated by the following equipment numbers: 104 through 113.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 13943

C.  	Section 15010

D.  	Section 15050

E.  	Section 15051

F.  	Section 15023

G.  	Section 15200

H.  	Section 15401

I.  	Section 15995

1.03	QUALITY ASSURANCE

A.  	The materials and methods of construction for these air-handling units and accessories hereinafter specified shall comply with the current editions (unless specifically indicated otherwise) of the practices, methods, or standards prepared by the applicable technical societies and associations.

B.  	The manufacturer of the custom air-handling units shall have at least 10 years of continuous, uninterrupted custom fabrication immediately prior to bid date.  Units of similar design and application shall be in operation as of bid date and manufacturer shall have demonstrated the capability to factory test units as described below.  Field assembled units from pre-fabricated panels are not considered equal to a factory fabricated machine.

C.  	Qualifications and Tests

1.  	Welder Qualifications

a. 		Perform structural and mechanical welding, brazing, and soldering with certified welders or welding operators having

1)  		Training and experience in accepted welding procedures.

2)  		Welding certification in accordance with American Society of Mechanical Engineers (ASME) Section 9.

2.  	Factory Tests

a. 		Test one type of unit serving each cleanroom as follows:

Room #                    Responsible AHU(s)

1401                      AHU - 5, 6, 7, 8, 9

1403                      AHU - 10, 11

1208                      AHU - 11, 12

1303                      AHU - 14

The owner reserves the right to randomly select which units are tested.

b. 		Submit detailed unit test plan for approval prior to conducting factory tests.

c. 		Perform tests in presence of Sandia National Laboratory (SNL) representative in order that results might be witnessed and certified.

d. 		Test each unit as a complete assembly for a minimum of two hours (hr.) and ensure that all components perform in accordance with the procedures outlined below:

1)  		A performance test shall be run on each tested unit.  For each test, the return air and supply air openings shall remain in the open positions.  All pre-filters shall be in place, along with all components of the unit.  A minimum of 8 feet (ft.) of rectangular discharge duct shall be installed on the unit's supply air opening.  The duct shall be throttled at its outlet plane as a means of varying the system resistance to obtain different performance determinations.  A pitot tube traverse test shall be conducted in the discharge duct based on the guidelines set forth in Air Movement and Control Association (AMCA), Standard (Std.) 203, "Field Performance Measurements".  Fan power shall be determined by means of a calibrated wattmeter in conjunction with the motor manufacturer's actual tested motor efficiencies.  Three performance determinations shall be made.  One determination shall be made at or near the rated flow and pressure.  The other two determinations shall be made at a higher and lower flow so as to define a short range of the unit's performance curve.  All test data shall be conducted in accordance with AMCA Std. 203.

2) 		Sound pressure levels shall be measured at the return-air, and supply openings with the unit's rated performance point established by throttling at the supply-air, discharge duct.  These readings should be unaffected by the throttling noise at the opposite end of the cabinet.  If it is determined there is some interference, a noise deflection/absorption barrier shall be erected near the discharge throttling area.  The discharge duct shall be removed and the supply-air dampers fully opened.  The sound pressure levels at the supply-air discharge plane shall be measured.  Again, the sound barrier shall be erected at the unit's inlet throttling planes if significant interference exists.  The unit must conform to the following sound criteria:

OCTAVE BAND - db

1    2   3    4    5   6    7   8

UNIT

OUTLET  96   102 102  97   95  90   85  80

UNIT

INLET   94   100 100  94   91  84   73  80

3)  		Pressure tests on and all piping systems.

4)  		Air-pressure test with the fan operating to ensure tight housing construction and integrity.  After completion of the unit, a pressure test at design static pressure is required on unit.  Air leakage to be measured with a calibrated orifice plate or flow tube.  Air leakage not to exceed 1/2 of 1 percent of total air-flow.

5)  		Unit operation and vibration analysis with unit fans operating at the unit design revolutions-per-minute (rpm).  Balance fan and motor so that vibration of assembly is 0.5 millimeters peak-to-peak or better.

6)  		Test of electrical devices, energized as components, to ensure operational integrity.

7)  		The thermal performance of each tested unit shall be measured.  For each test all penetrations of the tested unit shall be sealed.  The tested unit shall be placed in a location which prevents air currents.  A heat source shall be added to the tested unit interior, after 2 hours the exterior skin temperature shall be measured.  The difference between the tested unit outer skin temperature and the air temperature at the same location shall be used to determine the heat loss coefficient.  The heat loss coefficient shall be 0.07 British-thermal-units-per-hour (Btu/hr.)/ft2/degrees (deg.) Fahrenheit (F).

e.		Correct defects found during unit testing prior to shipment.

f. 		Submit test data for approval prior to unit shipment.

1.04	REFERENCES

A.  	Air Movement and Control Association (AMCA) Std. 203

B.  	American Society of Mechanical Engineers (ASME), ASME Boiler and Pressure Vessel Code Section IX

C.  American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) Standard 52-76

D.  	American National Standards Institute (ANSI) MC96.1

E.  	Air-Conditioning and Refrigeration Institute (ARI) 410-91

F.  	American Society for Testing and Materials (ASTM) E84

G.  	ASTM A386

H.  	ASTM A525

I.  	ASTM B209

J.  	ASTM B200

K.  	ASTM B221

L.  	ASTM B251

M.  	Electrical Standards Institute (ESI)

N.  	Federal Specification TT-S-001543A

O.  	Federal Specification TT-S-001657

P.  	Insulated Cable Engineers Association (ICEA) S-66-524

Q.  	ICEA S-82-552

R.  	Illuminating Engineering Society of North America (IES)

S.  	Institute of Electrical and Electronic Engineers (IEEE) No. 112, Method B

T.  	MIL-A-46106A

U.  	MIL-STD-282

V.  	National Electrical Manufacturer's Association (NEMA) MG1-12.53a

W.  	National Electrical Code (NEC)

X.  	National Fire Protection Association (NFPA) 79

Y.  	Sheet Metal and Air Conditioning Contractor's Association (SMACNA), "Heating, Ventilating, and Air-Conditioning (HVAC) Duct Construction Standards - Metal and Flexible"

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010, and Section 01300.

B.  	Submit manufacturer's literature and certified prints.

C.  	Submit Shop Drawings on sheets no larger than 30 inches (in.) by 42 in. to include the following:

1.  	Location and sizes of:

a. 		Piping connections

b. 		Electrical connections

c. 		Control tubing and wiring connections

d. 		Support points

e. 		Access areas required for maintenance

2.  	Operating weight and support locations of unit when bolted together in one assembly.

3.  	Shipping weight of each module or sub-section broken down for shipment.

4.  	Dimensions of unit when bolted together.

5.  	Dimensions of module or sub-section broken down for shipment.

6.  	Complete description of construction materials of unit including structural members, housing materials, finishes, access doors, hardware, lights, electrical components and controls.

7.  	Complete electrical data for unit including power and control wiring diagrams indicating all factory and field wiring requirements.  Use standard symbols, nomenclature, and markings as set forth by ESI in preparing diagrams.

8.  	Complete control diagrams of the items furnished for unit.

9.  	Complete performance data of unit including maximum cooling capacity, maximum kilo-Watts (kW) consumption, maximum air-quantities, leakage rate data, etc.

10. 	Static pressure of each internal component of the air-handling unit.

11. 	Vibration isolator data showing

a. 	The equipment identification mark.

b. 		The isolator type.

c. 		The actual load.

d. 			The static deflection expected under the actual load.

e. 		Specified minimum static deflection.

f. 		The remaining additional deflection to solid after the actual load is applied.

g. 		The ratio of spring height under actual load to spring diameter.

12. 	Verification that floor deflection beneath the fan shall not exceed 0.25 in..

D.  	The manufacturer is also requested to submit

1.  	At time of delivery all manufacturer's recommended spare parts lists and prices for unit and accessories to include:

a. 		Description of part.

b. 		Catalog number of part.

2.  	At time of delivery wiring diagram, installation, operation, and maintenance instructions for unit and accessories, sufficiently detailed so that the average mechanic, skilled in the trade, can install, operate, and perform maintenance operations.

3.  	Certification of unit housing panel thermal/acoustical/leakage performance and structural integrity under design conditions.

1.06	DELIVERY, STORAGE, AND HANDLING

A.  	See Section 15010.

B.  	All rigging and equipment required to get unit to installation location shall be provided by the Mechanical contractor.

C.  	All units shall be cleaned after final assembly and/or testing in accordance with these specifications.  After the unit is alcohol-cleaned, wrap in a protective double-layer plastic bag and seal all joints so that the unit can be transported, stored and installed without concern for contamination of the cleaned unit.

D.  	Each cleaned and bagged unit shall then be secured to allow shipment and handling, without damage to the cabinet.  Shipping base shall be suitable for handling and moving.  The cleanroom contractor shall review and approve the method of packaging and shipment prior to the first shipment.

E.  	The Mechanical contractor shall receive, unload, inspect, store, uncrate and install the units at the job site.

F.  	Any units arriving at the job site that have not been adequately protected, per the approved methods mentioned in Paragraph 1.06D or have endured damage during shipping, shall be rejected by the cleanroom contractor/Sandia National Laboratory (SNL) and must be returned to the manufacturer for rework or replacement.

G.  	The outside of the package or crate shall be adequately marked or tagged to indicate its contents by equipment number and weight.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Webco.

B.  	Environmental Air Systems.

C.  	Miller Picking.

2.02	MATERIALS

A.  	Galvanized steel in accordance with ASTM A386 or ASTM A525, G-90 coating, or finished with baked-on enamel; thickness in accordance with USS gauges (ga.).

B.  	Aluminum sheet and plate in accordance with 3003-H14 alloy, conforming to ASTM B209.

C.  	Aluminum extrusions in accordance with 6061-T6 or 6063-T52 alloy, conforming to ASTM B221.

D.  	All interior and exterior surfaces are to be cleaned, primed and painted with Fuller O'Brien "Wet White" dry polyester paint.  The base and structural components shall be painted with color match enamel.

2.03	EQUIPMENT

A.  	Performance Requirements

1.  	As indicated on the Drawings.

2.  	Design pressures shall include all losses internal and external to unit.

B.  Identification

1.  	Identify air-handling unit on exterior with minimum 6 in. painted, stenciled identification numbers corresponding to designation numbers on attached Drawings; locate numbers so they shall be clearly visible after installation of equipment.

2.  	Apply designation numbers on manufacturer's standard permanent nameplate or on stainless steel tag permanently attached to contain the following information:

a. 	Equipment name.

b. 	Equipment number as indicated on the attached Drawings.

c. 	Manufacturer's name, address, and phone number.

d. 	Manufacturer's model, serial number, year manufactured.

e. 	Design criteria (capacity in standard-cubic-feet-per-minute and static pressure drop).

f. 	Electrical Characteristics: motor horsepower (hp), rpm, Volts (V), phase (ph.) and amperage (A) for main power tie-in.

g. 	Purchase order number.

2.04	FABRICATION

A.  	Design and Assembly

1.  	Design and assemble units to ensure that each enclosure is engineered to withstand all operating pressures at design conditions and pressures of project requirements.

2.  	Design structural components of unit equal to or exceeding the following external loads with a maximum deflection of 1/8 in. over maximum 4-ft. span.

a. 	Roof - 75 pounds-per-square-foot (psf)

b. 	Walls and Ends - 65 psf

c. 	Floor - Equipment weight plus 50 psf

3.  	Design and assemble unit for indoor installation.

4.  	Design and assemble unit to require only the external connecting of electrical power, lighting, chilled water, drain piping, control tubing, control wiring, and ductwork to provide complete and operable systems.

5.  	Fabricate units in sub-sections or modules having the following features:

a. 		Fabricate so that power wiring can be properly reconnected on terminal strips located in junction boxes in adjacent sub-sections or modules.

b. 		Fabricate so that control wiring can be reconnected by reconnecting male and female connectors.

c. 		Fabricate so that piping can be reconnected by couplings, unions, or flanged joints and tubing by re-connection of tube fittings.

d. 		Fabricate so that panel frames and panels can be easily joined together in the field by bolting through companion angles or flanges.

e. 		Provide adequate lifting lugs, gaskets, flashing materials, attachment devices, and sealants to facilitate a complete, airtight, watertight, and operable installation.

f. 		Independent structural base.

6.  	Furnish  similar  equipment, such as motors, coils, filters,  and dampers, from the same manufacturer.

7.  	Factory install all internal components, conduits, electrical conductors, junction boxes, tubing, and piping.

8.  	Where holes are provided in floor or wall panels, for ductwork, piping, or conduits, exposed edges of insulation and panel facings shall be protected by structural steel members or steel sleeves continuously welded in place.  Holes shall be sealed airtight.

9.  	Removable panels shall be installed and located to facilitate fan removal.

10. 	Conduits shall be sealed with Nelson's Flame Seal or approved equal.

11. 	All internal piping and insulation shall be according to Sections 15051, 15250, and 15401.

12. 	Fabricate the unit with all field connections exterior to the unit.

B.  	Unit Casing and Base

1.  	Unit casing is to be fabricated from brake-formed panels of 16-gauge galvanized steel.  Panels shall be joined together by welding.  Roll-formed clamping strips and screws or bolts are not acceptable to assemble casing walls.  Entire outside casing is prepared for painting by acidizing.  All joints shall be caulked with rubber caulking that air dries to form a permanently flexible seal for total air-tight construction.  Casing base metal is to be zinc coated with a minimum of .60/.80 ounce per square foot, and shall have an average coating thickness on both sides of .0006 inch.  Following the coating, the sheets shall be annealed to produce a zinc-iron alloy to meet ASTM A527.  Bending and forming operations do not remove the alloy bond.

2.  	Welded wall and roof sections shall be completely covered with an acoustical and thermal efficient 2", 3 pound unfaced fiberglass insulation which complies with all requirements of NFPA Bulletin No. 90-A.  The insulation will not mold, rot, or sustain vermin, and will not corrode metals or disintegrate under vibrations.  The material is to be odorless, will not absorb odors, and shall resist water moisture permanently without chemical breakdown.  A double-wall casing shall incorporate a perforated interior liner of 22-gauge galvanized steel.  Media is to be lined with a 4-millimeter (4mm) mylar.

3.  	All compartments shall be fully accessible through insulated, double-wall access doors.  Doors shall be mounted on stainless steel butt hinges and retained by at least two chrome-plated hardware latches operable from interior or exterior of unit.  The hardware can be operated from either side of the door.  Double-wall door shall have a mechanically fastened bulb seal around entire perimeter of door frame.  All doors shall open against static pressure and close flush with the exterior cabinet surface.  Each door shall incorporate dual pane wire reinforced window.

4.  	Internal compartment, where needed, shall be individually drained to the exterior of the unit for field connection by others.  Any necessary traps are external to the unit and provided by others.

5.  	Floor rigidity is to be maintained by the addition of steel channel or angle members which act not only as a rigid foundation to which all component isolators are secured but also as a floor stiffener.

6.  	An integral structural steel weldment base frame shall support the unit's casing all internal components.  Base frame is to be a structural member engineered for roof curb mounting such that the base overhangs and curb. Formed metal base construction techniques are not acceptable.  The base frame shall include four (4) or more listing lugs bolted in place so located as to minimize lifting stress and designed for use with clevises.  Base frame is to be constructed to minimize oilcanning and deflection due to component loading.  All internal components shall be supported by structural steel members and supported by the periphery of the base frame.  The floor is to be 10-gauge black hot rolled sheet steel, with all seams continuously welded.  Entire floor Area is to be coated with Overshield emulsion applied at the factory.  The coating shall have a flame spread of 25 or less, smoke generation of 50 or less, and fuel contribution of 0.  Entire floor underside is to be insulated with 2", 3 pound fiberglass.  Insulation is to be retained with a 20 gauge solid galvanized steel liner.  During component installation, no holes or bolts are allowed to penetrate the floor pan.

7.  	Sound Transmission Loss Values:  The following casing transmission loss values are required as a minimum and shall be obtained by a independent sound lab that is accredited by the U.S. Department of Commerce, National Institute of Standards and Technology under the National Voluntary Laboratory Accreditation Program for this test procedure.  All tests shall be performed in explicit conformance with ASTM E90-90 and E413-87

FREQ             125  250  500 1000  2000  4000  STC

PERF LINER        21   26   31   42    50    58   37

SOLID LINER       23   41   47   50    56    63   47

8.  	The unit shall incorporate appropriate sections with components to achieve the scheduled performances in the arrangement shown in the attached sketches.

9. 	Structural integrity of the completed enclosure shall provide for maximum panel deflections of 1/200th of span when enclosure is subjected to an air-pressure test of 10-in. water gage (w.g.), both positive and negative.

10. 	Panel to panel joints shall be flange and gasket type having factory installed insulation that fully fills joint when assembled.

C.  	Electrical

1.  	Lighting

a. 		Provide for a separate power feed for the lighting.

b. 		Provide 100 watt, watertight, incandescent fixtures to provide lighting levels recommended by IES.

c. 		Install wall mounted switches for each section as required.

d. 		Provide outlet boxes, conduits, and conductors to complete an operable installation.

e. 		Terminate conductors in factory mounted control panel on a terminal  strip so that only one connection is required for lighting system and receptacle (weather proof GFI).  The control panel shall be mounted external to the unit casing.

2.  	Power

a. 		Provide for a 480 second power feed for all other equipment.

b. 		Install conduits, conductors, junction  boxes, etc., as required for complete and operable system.

c. 		Provide the following electrical components:

1)  		Install control panel on exterior face of air-handling unit.

2)  		Install conduit and conductors from motor to control panel for single point connection.

3.  	Fan motor shall be factory wired to NEMA 1, N-F disconnect located in the units control panel for field connection by others.  Disconnect shall be operable from the exterior of the control panel.

a. 		All transformers, terminal strips and wiring to be furnished any factory installed.

b. 		All conduit shall be piped to the exterior of the unit for final field connection where the conduit penetrates the unit casing, the penetration shall be factory sealed airtight.

c. 		Electrical components, devices and, materials shall be sized in accordance with NEC requirements.

d. 		Wiring and Conduits

1)  		All electrical wiring shall be installed in EMT,  electro-galvanized thin-wall steel electrical metallic tubing, dipped galvanized steel conduit, minimum size of 3/4 in..  Do not run EMT conduit where accessible for people to stand upon or to use for support.  Use liquid tight flexible metal conduit at motors, transformers, any device subject to vibration and where rigid conduit is not applicable; however, each length of flexible conduit shall not exceed 24 in..

2)  		Provide low voltage wire and cable with conductors of soft-drawn annealed copper, Class "B" stranding, which is free of kinks, cuts, and abrasions at the time of installation, in accordance with the following schedule:

a) 	Underwriters Type THHN/THWN (90-deg. Celsius (C) dry, 75-deg. C wet), single conductor, for general use in dry and wet locations as branch circuits and control wiring.  (No. 12 AWG min. for branch circuits; No. 14 AWG min. for control wiring.)

b) 	Underwriters Type XHHW (75-deg. C wet/90-deg. C dry), single conductor, as feeder circuits No. 6 AWG and larger.

3)  		Color Coding

a) 	Provide color coding for single and multi-conductor power circuits as follows:

Voltage O/A   O/B   O/C Neutral

240    Black  Red   Blue White

and below

250 - 600BrownOrangeYellowWhite

w/Tracer

- 	For specified insulations and jackets not manufactured with integral colors, use conductors with black insulation or jacket and color coding tape.

- 	Color code conductors entering boxes, troughs, cabinets, and other enclosures.

- 	lor code conductors in wire-ways, trenches, and other locations where conductors are continuously accessible at intervals not exceeding 5 ft..

b) 	Insulated Equipment Ground - Green.

c) 	Control Cables

- 	Single Conductors:  Red (AC), Blue (DC).

- 	Multi-conductor:  Comply with ICEA S-66-524, "Method I", Table K-2.

d) 	Signal Cables:  Comply with ICEA S-82-552, "Method 9", Table E-2.  In addition, number multiple pairs, triads, and quads.

e) 	Thermocouple Extension Wire:  ANSI MC96.1 and ICEA S-82-552, Table E-4.

4)  		Connections between conduits and steel boxes shall be made with double lock nuts and grounding bushings.

5)  		Wiring and wire markings shall be in accordance with ESI and NEC, and NFPA 79.

6)  		A grounding conductor with green insulation shall be installed in all raceways containing conductors with a potential greater than 24 V.  Grounding conductors shall be bonded to all raceways, boxes, equipment enclosures, motors, and fixtures.

e. 		Control Panels

1)  		Provide centrally located electrical panels exterior to the unit casing having appropriately sized and identified terminal blocks for lighting circuits and control wiring and main power feed.

2)  		Terminals shall be 600-V rated, track mounted, tubular screw type, with pressure plate and separate marking strip.

f. 		All control components, wiring, and auxiliaries as designated as "Furnished by unit manufacturer" on Control Drawing 104658 C9 through C14 shall be furnished and installed at the factory.  Reference Control Drawing 104663 C5 for typical control box wiring diagram.

D.  	Module Component Requirements

1.  	Filters

a. 		Final Filters - Air filters shall be 12-in. thick, high performance, deep pleated, totally rigid and totally disposable type.  Each filter shall consist of high density media, media support grid, contour stabilizers, diagonal support bracing and enclosing frame.  The filter shall be listed by Underwriters' Laboratories as Class 2.

b. 		Filter Media - Filter media shall be of high density microfine glass fibers, laminated to a reinforcing backing to form a lofted filter blanket.  The filter media shall have an average efficiency of 90-95 percent on ASHRAE Test Standard 52-76.  It shall have an average arrestance of  97 percent on that standard.  Initial resistance at 50 fpm approach velocity shall not exceed 1 inch w.g.

Final filter media is supplied in supply section only.  Final filter media will mount glidepack aluminum extrusions suitable for side access service.

Final filter media shall be FARR RF-15 or approved equal.

2.  	Magnehelic Gauges:  Dwyer Gauges or approved equal for the filter banks shall be factory mounted on the face of the unit control panel.  The pressure gage shall have a 0 to 3 in. w.g. range.

3.  	Cooling Coils

a. 		Primary Surface shall be round seamless 5/8-in. O.D.  .020 copper tubes on 1-1/2-in. centers, staggered in the direction of airflow.  All joints shall be brazed.

b. 		Secondary Surface shall consist of rippled .0075-in. aluminum plate fins for higher capacity and structural strength.  Fins shall have full drawn collars to provide a continuous surface cover over the entire tube for maximum heat transfer.  Bare copper tube shall not be visible between fins and the fins shall have no openings punched in them to accumulate lint and dirt.  Tubes shall be mechanically expanded into the fins to provide a continuous primary to secondary compression bond over the entire finned length for maximum heat transfer rates.  Fin height and length shall be as specified on schedule.

c. 		Casings shall be constructed of stainless steel with 3/8-in. diameter bolt holes for mounting on 6-in. centers.  Coil side plates shall be of reinforced flange type.

d. 		Coils shall have the connections located to permit universal mounting of the coil for right - or left-hand airflow and have equal pressure drop through all circuits.  Coils shall be circuited for counterflow heat transfer to provide the maximum mean effective temperature difference for maximum heat transfer rates.  Coil fin height shall not exceed 48 in.

1)  		Water coils:  Headers on water coils shall be seamless copper tubing.  The headers shall have intruded tube holes to provide a large brazing surface for maximum strength and inherent flexibility.

2)  		The complete coil core shall be tested with 315 pounds air pressure under warm water and be suitable for operation at 250 psig working pressures.  Individual tube test and core tests before installation of headers is not considered satisfactory.  Hydrostatic tests alone will not be acceptable.  Water cooling coils shall be circuited for drainability and for service without removing individual plugs from each tube.  Use of internal restrictive devices to obtain turbulent flow will not be acceptable since they prevent complete draining of the coil.

e. 		One side of this section shall have a gasketed, and bolted, removable access panel.

f. 		Each coil shall have a condensate drain pan extending a minimum of 12 in. downstream of the coil face for upper coils, and 18 in. for the lower most coil.  All condensate drain pans shall be stainless steel.  All intermediate drain pans shall be fitted with downspouts to drain condensate to primary drain pan.  Trapping of primary drain will be furnished and installed by contractor external to the unit casing.

g. 		Cooling coils shall be ARI certified for scheduled performance and bear the ARI seal.  Coils shall be manufactured by Heatcraft or approved equal.

h. 		Chilled water piping shall be internally headered and extend through the casing and be sealed airtight at the factory.

I.		Each coil shall have either a flanged connection or union inside the unit to facilitate coil removal.

4.  	Flexible Connections

a. 		Provide flexible connections between unit components as required for vibration isolation.

b. 		Flexible connections shall be made of neoprene coated glass fabric of fire, water and weather resistant cotton.

c. 		Flexible connections shall be installed with sufficient slack to prevent transmission of vibration.

d. 		Flexible connectors shall be suitable for duct pressure up to 10-in. w.g.

e. 		Arrange components in each module for easy accessibility and servicing.

f. 		Manufacturer and Type - "Ventglas" by Ventfabrics, Inc. or approved equal.

5.  	Dampers

a. 		Automatically-operated dampers shall be of the multi-blade, parallel-blade type.  Single blade dampers are not acceptable.

b. 		Frames shall be fabricated of 6-in. wide by 16-USS-ga. (minimum) roll-formed galvanized steel or 6-in. galvanized structural channel with integral reinforcing ribs and mounting flanges for ease of installation.  Provide a 2-in., mounting flange.

c. 		Blades shall be airfoil and shall be fabricated of 16-USS-ga. (minimum) galvanized steel and sized no greater than 6-in. width or 48-in. length.

d. 		Blade shafts shall be continuous from bearings one side of the frame to the bearings on other side of the frame.  The blade shafts shall be 1/2-in. hex or square, galvanized or cadmium plated steel.  A 6-in. shaft extension shall be provided for the damper operator.

e. 		Stainless steel sleeve or oil-impregnated bronze bearings mounted in the damper frame shall be provided for the blade shafts.

f. 		Linkage shall be a galvanized or cadmium plated steel assembly of interconnecting linkage attached to the shaft of each damper blade.  This linkage is to be mounted external to the airstream.

g. 		Damper shall be provided with electric actuators (factory installed) as indicated on the Referenced Control Drawings.

h. 		Dampers shall be low-leakage type.

i. 		Ruskin Model CD50 or an approved equal.

6.  	Supply Fan

a. 		The fans shall be of the centrifugal plenum designed without a scroll type housing.  Fans shall incorporate a nonoverloading type backward inclined airfoil blade wheel, heavy gauge reinforced steel inlet plate, structural steel frame, and shaft and bearings in AMCA arrangement #3 configuration.  Each fan shall be run fully assembled at the factory, prior to shipment, at the operating RPM or the maximum class RPM.  The total fan assembly shall be checked for balance and compared against the acceptable levels on the Rathbone Chart.

b. 		Frame and Inlet Plate:  Inlet plates are to be of heavy gauge reinforced steel construction.  The inlet plates shall be welded to the heavy structural angle frame to form an integral unit.  The inlet plate incorporates a removable spun inlet cone designed for smooth airflow into the accompanying venturi-shaped inlet cones of the fan wheel.  A square formed lip surrounds the unit suitable for attachment of a boot connector, or an optional round inlet ring can be provided.

c. 		Fan Wheels:  All fan wheels shall have spun inlet cones providing a minimum separation in airflow.  Blades shall be die formed airfoil shaped.  All nine blades shall be continuously welded to the inlet cones as well as the backplates.  No. partial welding will be acceptable.

d. 		Class I and II wheels shall have cast iron hubs.  All wheels shall be "true" lines, statically and dynamically balanced on precision electronic balancers.  Each wheel shall be designed for critical speeds of at least 1.25 times the maximum class speed.  Initial operating fan RPM shall not exceed 90 percent of fan class maximum RPM to allow for final system air balance.

e. 		Fan Shafts:  All sizes are to have shafts of solid AISI C-1040, or C-1045 hot rolled steel accurately turned, ground, polished, and ring gauged for accuracy.  All shafts must be dial indicated for straightness after the keyways are cut and straightened as required.  Shafts shall have first critical speeds at least 1.35 times the maximum speeds of the fan.

f. 		Bearings:  All fans are to have heavy duty, grease lubricated, precision anti-friction ball or roller, self-aligning, pillow block type bearings.  Bearings are to be selected for minimum average bearing life (AFBMA L-50) in excess of 200,000 hours when operating at maximum catalogued class conditions.  All bearings shall be equipped with re-greaseable zerk fittings and where necessary, extended lube lines for easy access for relubrication.

g. 		Painting:  Each fan component shall be thoroughly degreased and deburred before the application of a rust-preventative blue primer.  After complete assembly, a finished coat as previously described in Section 2.02D shall be applied to the complete assembly.

h. 		All fans shall be AMCA certified for sound and air performance and bear the AMCA seal.  Fans shall be manufactured by Barry Blower or approved equal.

i. 		Supply fan section shall be complete with supply fan, inlet screen, access panel for wheel removal, motor, drive, support frame, open type spring isolators, and fan wheel guard.

j. 		Fan and motor shall be mounted on a welded and painted structural steel channel base frame.  This assembly shall be isolated from the casing and floor.  Outlet of the fan is to be separated from unit casing by use of factory assembled flexible connection.  The fan, motor and base frame assembly shall be mounted on a minimum of four (4) coil spring vibration isolators with neoprene pads.  Vibration isolators shall be selected for 95 percent efficiency.

k. 		Furnish extended copper lubrication lines from fan bearings to zerk fitting on unit casing, mounted and prepacked with grease at the factory.

l. 		Fan assembly to be statically and dynamically balanced in the factory then given a final test with motor and rive in place.  Drive assembly to include an expanded metal belt guard with an RPM measurement port.

2.05	MOTORS

A.  	General

1.  	Apply requirements below to motors covered by this Section except as otherwise indicated.

2.  	Motors:  Polyphase.

3.  	Frequency Rating:  60 Hertz.

4.  	Voltage Rating:  Determined by voltage of circuit to which motor is connected for the following motor voltage ratings (utilization voltages):

a. 		Motors: 480 V circuit, 460 V - motor rating.

5.  	Service factors indicated for motors are minimum values and apply at frequency and utilization voltage at which motor is connected.  Provide motors which will not operate in service factor range when supply voltage is within 10 percent of motor voltage rating.

6.  	Capacity:  Minimum size as indicated.  If not indicated, sufficient to start and operate connected loads at designated speeds in indicated environment, and with indicated operating sequence, without exceeding nameplate ratings.  Provide motors rated for continuous duty at 100 percent of rated capacity.

7.  	Temperature Rise:  Based on 40 deg. C ambient except as otherwise indicated.

8.  	Enclosure:  Open drip-proof, unless noted otherwise.

9.  	Motor Speed:  Single, multiple, or variable as indicated.

B.  	Polyphase Motors

1.  	Squirrel-cage, induction-type, general-purpose conforming to the following requirements except as otherwise indicated.

2.  	NEMA Design Letter Designation:  "B," unless specifically designated "C" for high starting torque.

3.  	Energy Efficient Motors:  Nominal efficiency equal to or greater than that stated in NEMA MG 1, table 12-6C for that type and rating of motor.

4.  	Variable Speed Motors for Use With Solid-State Drives:  Energy efficient, squirrel-cage induction, design B units with ratings, characteristics, and features coordinated with and approved by drive manufacturer.

5.  	Internal Thermal Overload Protection For Motors:  For motors so indicated, protection automatically opens control circuit arranged for external connection.  Protection operates when winding temperature exceeds safe value calibrated to the temperature rating of the motor insulation.

6.  	Bearings:  Double-shielded, pre-lubricated ball bearings suitable for radial and thrust loading of the application, unless noted otherwise.

PART 3 - EXECUTION

3.01	INSTALLATION/APPLICATION/ERECTION

A.  	Unit manufacturer shall provide a qualified supervisor to instruct and supervise the Contractor in rigging, erecting, pre-operation check-out and starting of unit at time of installation.

B.  	Unit manufacturer shall provide a qualified supervisor to instruct the SNL's personnel on maintenance and operation of the air-handling unit for a minimum of 4 hours after final acceptance.

C.  	Unit manufacturer shall provide the necessary installation materials required for installation of the unit.

3.02	FIELD QUALITY CONTROL

A.  	The unit will be field tested by an independent Testing, Adjusting, and Balancing Contractor after installation.  Testing shall be basically the same as required under Paragraph 1.02, Factory Tests above.  Any deficiencies found at this time shall be corrected by the unit manufacturer at no cost to SNL.

3.03 COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.  Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

END OF SECTION

EXCEPT FOR ATTACHMENTS

SK AHU-5, 6, 7, 8, 9, 10, 11, 12, 13, 14