Silicon Detector Facility

ODH Analysis

Dan Olis	6/1/2004

LAB A Control Room Addendum

Herman Cease 	4/8/05

LAB A Control Room LN2 Auto Fill System Addendum

Herman Cease 11/29/05

# SUMMARY

A component of the Silicon Detector Facility’s utility infrastructure is a gaseous nitrogen header.  Nitrogen is used primarily to purge enclosures to eliminate ambient moisture and, in some cases, the presence of oxygen.  The Silicon Detector Facility (SiDet) includes Labs A, B, C, D, A-B Bridge, C-D Cross-connect, and adjoining hallways.  This analysis is inclusive of all lab spaces within the facility that have any part of the nitrogen header running through them or that are fed by nitrogen piping drops.  Separate calculations are included for each portion of the facility that can be isolated by closed doors.  This analysis shows that all regions within SiDet are class 0 ODH environments.

Note: This document supercedes the ODH analysis done for the Lab A/B Bridge.  The analysis for that single volume has been revised and incorporated into this facility-wide document.

INTRODUCTION

Gaseous nitrogen is primarily used in the Silicon Detector Facility for purging enclosures of sensitive items.  Although the plumbing system is extensive, the total nominal flow rate into the facility less than 5 SCFM.  Compared to facilities holding cryogenic piping, the nitrogen supply at SiDet is very low risk.  The supply is a 5000-gallon liquid nitrogen dewar located outdoors at the north end of Lab D.  It has an operating pressure of 34 PSIG and relief valves set to 45 PSIG.  A gaseous nitrogen header is fed from the dewar through two Pennwalt CVI vaporizers and the header pressure is nominally the same as the dewar’s.  The header is piped throughout the facility, interconnecting piping in Lab A, Lab B, Lab C, Lab D, Lab A-B Bridge, and the C-D Cross Connect into a single system.  Smaller lines drop from the header as take off points where nitrogen is used.  A restricting orifice outdoors in the main feed puts an upper limit on the total possible flow into the facility at 25 SCFM.  Additionally, orifices in the individual branches inside the facility limit downstream spills to 2-4 SCFM.

Spreadsheets are attached which show the ODH analysis for each isolated space within the facility that is currently using nitrogen purge or that has the header running through it.  The analysis is done as described in Fermilab ES&H chapter 5064, Oxygen Deficiency Hazards.  This document shows that all regions within SiDet are class 0 ODH environments.

# Si-DET PIPING AND PURGE USAGE OVERVIEW

The piping schematic of the header and dewar is drawing 9214.000-ME-435001.  It is attached.  The nitrogen header (indoors) is plumbed entirely with type-K copper tube with sweated joints.  At points of delivery, flexible poly lines are most frequently used to make the connection to purge enclosures.  In addition to serving as a continual purge supply, the nitrogen gas is used in some work areas to periodically spray contaminants from delicate work pieces.

It is facility policy that all purge enclosures use a rotometer style flow meter to set and monitor usage.   A summary of all purge usage at the time of this writing of this document is shown in the table below.

The left column shows how low the facility’s nitrogen consumption is.  The right column of the table shows the assumed purge rates used in these analyses.  The table illustrates a fairly conservative overestimate of the nitrogen consumption is used.  This allows the facility to add to or move a significant number of purge volumes around the system without requiring a revision to this document.

A restricting orifice in the supply line connecting the dewar to the facility limits the maximum flow of nitrogen into the facility to 25 SCFM.  This orifice is outdoors.  The calculation assumes a catastrophic failure of the downstream piping and uses the dewar’s relief valve pressure, not the current operating pressure, as the differential pressure across the orifice.  Within the facility, the presence of flow limiting orifices in each drop places a strict upper limit on the nitrogen that can be delivered to a room (typically 2 SCFM).  The piping component totals, number of purge enclosures, and ventilation and spill rates are presented for each separate enclosed room within the facility in the following sections.

A time-delayed shutoff valve is installed in the gas supply just at the inlet to the system.  The valve is a normally closed solenoid, held open by an uninterruptible power supply (UPS).  The valve is EV-3101 on the piping schematic.  During short power outages, nitrogen flow to the facility is maintained.  During longer outages, the continued flow of nitrogen into some clean rooms could present an oxygen deficiency hazard since forced ventilation is lost.  Purge rates are low, so the time to an ODH risk is typically 24 hours or greater.  A relay with a timer is set to shutoff gas flow after a 12-hour loss of commercial power.  This system is wired for fail-safe operation.  The bypass valve shown in the schematic is to be opened only during maintenance and safety tests.  It is locked out and labeled with a yellow caution tag.  The lock’s key is on file with the facility’s secretary.  This safety system is tested once a year.   A copy of the test log is included in the appendix.  The tests are the responsibility of the facility’s systems technician.

This document assumes that each port on the gas line in an area has a purge volume attached to it.  The quantity of purge enclosures listed is an upper limit estimate as to how many could be attached in a given area.  Since purges are ‘intentional leaks’ they are assigned a probability of 1.0 in the calculations.  The leak rate assigned to the purge volumes is 0.1 SCFM (6 SCFH), a conservative estimate.

As stated previously, purge volumes are connected to the system through a Dwyer style flow meter with integrated flow control valve.  These flow meters are counted as ‘valves’ in the analyses.  In the spreadsheet calculations, the total number of valves in an area includes all the valves that are part of the hard copper piping plus additional flow meter control ‘valves’ attached to ports in the piping to make use of the nitrogen utility.

Some technicians make use of spray nozzles to periodically blow dust from work pieces.  This too represents an intentional ‘leak’ but the time averaged usage is too small to consider.  The spray nozzles are commercial products and can also be accounted as ‘valves’ in the analyses.  There is not a separate line item in the calculations for the spray nozzles since it is assumed that a spray nozzle would be used at a port in place of a purge enclosure (with integrated flow control valve).  This is a conservative approach since these spray nozzles do not have a continual purge rate associated with them.

# VENITILATION AND ODH ANALYSES FOR EACH LAB AREA

A description of the ventilation system and ODH analysis of each room volume at 
SiDet is presented in the sections below.  To simplify counting of joints in the piping system, the number is estimated by conservatively assuming one joint for every five feet of pipe length.  A 5 SCFM spill rate is assumed in leaky joints in the main header.  Spill rates in leaky joints in the branches of the system are smaller and assigned the maximum flow rate allowed by the orifice controlling that branch.  The leak rate for catastrophic failure of a pipe or valve is assumed equal to the maximum spill rate calculated for the controlling restricting orifice.  For pipes and valves in the main run of the header, 25 SCFM is used per the discussion in the introduction.  This calculation is in the appendix.  In side branches of the system, leak rates are assumed equal to the maximum flow rate of the restricting orifice in that branch.  These rates are described in subsequent sections.  The probability of failure of the piping components is taken from the NEC tables included in FESHM 5064.  The probability of the ‘leak rates’ of the purge boxes is assigned to 1.0 since they are continually present.

Ventilation rates in the analyses for the building shells (not the internal clean rooms) are generated by assuming each building’s natural leakiness, or infiltration, provides adequate fresh air for its occupants and the operations taking place within it.  The estimated infiltration rate is a conservative estimate based on 1 building volume change per day.  The 1989 American Society of Heating and Refrigeration Fundamentals Handbook shows this to be a conservative estimate.  The Infiltration section in Chapter 23 indicates that office buildings constructed in mid-1980’s have infiltration rates of 0.1 to 0.6 air exchanges per hour.  This is equivalent to 2.4 to 14.4 air exchanges per day.  The 1 volume change per day assumed in this analysis is conservative for SiDet buildings.

Ventilation rates for clean rooms and smaller workspaces are measured rates and described in more detail in the sections below.

Appended to the ODH Analysis spreadsheets are additional documents: calculations, an explanation of the spreadsheet columns, sheets showing the equations used in the spreadsheets, and a copy of the failure rate tables taken from FESHM 5064.

#### Lab A

Lab A houses office space around the perimeter of the second floor and technician workspace on the first floor.  It also holds a large class 5000 clean room in the center of the building.  Adjacent to the class 5000 clean room is a smaller class 1000 clean room.  Nitrogen is used in the first floor technician areas and in the clean rooms.

Six small HVAC units serve Lab A.  Four of these units draw outside makeup air (100 CFM each) but the units run only when heating and cooling are called for.  The estimated infiltration rate for the building is 20 CFM and is simply a conservative estimate based on 1 building volume change per day.  The calculation is shown here:

There are many spaces within SiDet that have enclosures within larger rooms (e.g. clean rooms within a larger building shell).  In these cases, the piping within these smaller rooms is included in the ODH analysis of the larger room volume because a leak within the clean room may eventually find its way into the larger volume.  That is to say, the smaller room is considered a part of the larger space it occupies.  A separate analysis is then done for the smaller interior spaces (individual clean rooms) to prove that there is not a concentrated risk as a result of the clean room enclosure.

The main nitrogen header in this space is 1” type-K copper.  There is currently one purge enclosure in the technician area drawing 0.01 SCFM of nitrogen.  The analysis assumes three may exist at some point in the future, each drawing 0.1 SCFM.  Furthermore it this analysis, it is assumed that any nitrogen spill in the clean rooms finds its way into the larger tech area.  Therefore, the attached spreadsheet calculation includes the piping components found in both the technician area and in the clean rooms.  Those components are summarized below and in the spreadsheets in the appendix.

The calculation shows that Lab A is an ODH class 0 environment.

#### Lab A Class 5000 Clean Room

The class 5000 clean room occupies the center of the building and the volume extends up into the bubble-shaped roof.  The space is more accurately described as a semi-clean room because it is not sealed very well to the inside of Lab A or to the outdoors through the roof.  The large presence of bugs and an occasional bird attest to its leakiness.

The room volume is filtered by large HEPA filters, fed by a McQuay Model LYP108C 14-9/16” airfoil powered by a 10 HP motor.  The measured makeup rate is 100 CFM.  It draws from the Lab A shell.  Like all clean rooms, a mechanical failure of the air-handling unit would be quickly recognized and addressed.

The class 1000 clean room is a smaller volume contained inside the class 5000 clean room so the piping components in both areas are included here.  The attached analysis summarizes the current piping sizes and lengths and the number of valves inside the clean rooms.  The piping feed to the clean room is a single ½” drop from the header.  A restricting orifice, located in the larger Lab A volume, limits the maximum flow of nitrogen to 3.8 SCFM.  The orifice calculation is included in the appendix.

There are currently six enclosures in the class 5000 room and four in the class 1000 room receiving nitrogen purge.  The current consumptions are 0.32 and 0.25 SCFM of nitrogen respectively.  To be conservative, a purge rate of 1.7 SCFM is used in the ODH analysis.  This is calculated by assuming a purge enclosure is added to each of the existing (10) ports in the class 5000 room and the (7) ports in the class 1000 room.  It’s assumed each draws 0.1 SCFM of nitrogen.

The analysis shows that the class 5000 clean room has an ODH class 0 rating.  The first calculation shows the normal ventilation condition.  The second calculation includes the probability of failure of the ventilation system.  The probability assigned to the mechanical failure of the air-handling unit was taken from Table 2 in FESHM 5064 for the failure of an electrical motor (1x10-5events/hr).  A column is added to the table to multiply the probability of the leak times the probability of a ventilation failure due to motor failure.  The 5 SCFM fresh air makeup rate used in this calculation is quite reasonable considering the leakiness of the volume previously described.

Ventilation loss as a result of a power outage occurs more frequently at Fermilab.  Power outages typically last a few hours at most.  Table 1 in FESHM 5064 provides a 1-hour duration for unplanned outages.  It would take more than 98 hours of a 1.7 SCFM purge and zero makeup air to lower the oxygen concentration in the clean room to 18%.  This calculation is included in the appendix.  The 12-hour time-delay shutoff in the facility’s main nitrogen feed line eliminates any ODH concern for long-term outages.

#### Lab A Class 1000 Clean Room

The class 1000 clean room sits between the class 5000 clean room and an exterior wall.  The ventilation system for the room is shown in the following sketch.  A Train Company ventilation unit cools the space but draws no makeup air.  The supply side of the unit discharges into the drop ceiling, in a volume called a plenum.  There are (18) fan-powered HEPA units installed in the drop ceiling.  Each unit includes a filter and its own fan.  These ceiling units draw air from the plenum space within the drop ceiling and discharge into the room below.  Each ceiling unit moves approximately 616 CFM of air for a total delivery to the room of 18 x 616 = 11,090 CFM of air.  The plenum pressure is negative to the room volume, running at approximately -0.08” WC.  An intake attached to the plenum draws makeup air from the larger class 5000 clean room.  The makeup rate is 100 CFM.

The attached analysis summarizes the current piping sizes and lengths and the size and number of valves inside the clean room.  The piping is fed from the larger class 5000 clean room through a single ½” line.  The same size restricting orifice that controls flow to the class 5000 clean room limits the maximum flow of nitrogen to 3.8 SCFM.

There are currently four enclosures receiving nitrogen purge.  The current consumption is 0.25 SCFM.  To be conservative, a purge rate of 0.7 SCFM is used in the ODH analysis.

The analysis shows that the class 1000 clean room has an ODH class 0 rating.  The first calculation shows the normal ventilation condition.  The second calculation includes the probability of a single point failure of the ventilation system.  The class 1000 clean room has a very robust ventilation system since it is assembled from (18) parallel fans on the HEPA units.  With a failure of a single unit, seventeen are still operational and the ventilation makeup is essentially unchanged.

It would take more than 36 hours of a 0.7 SCFM purge and zero makeup air to lower the oxygen concentration in the clean room to 18%.  This calculation is included in the appendix.  The 12-hour time-delay shutoff in the facility’s main nitrogen feed line eliminates any ODH concern for long-term outages.

#### Lab A Control Room Addendum H. Cease 4/8/05

Attached to the Lab A area is an enclosed room known as the Lab A Control Room. Utilities to the room include building nitrogen gas. A restricting orifice (0.052” diam.) in the nitrogen gas line feeding the room limits the maximum flow to 1.8 SCFM. The total room volume is approximately 5500 FT3. The room is partitioned for a gowning area reducing the room volume to approximately 3800 FT3. Infiltration to the room is assumed to be one volume exchange per day –or about 2.6 cfm makeup air. At no time does the nitrogen gas purge rate exceed the natural infiltration rate of fresh air.

Three fan powered HEPA units in the ceiling circulate air throughout the room. A baffle is used to take air from the LAB A general area and mix it with the Control Room air at a rate greater than 20 FT3/min. The Control Room has a positive pressure with respect to the surrounding Lab A area. If a single fan fails, the mixing of air with Lab A remains about the same. The fuse panel for the fans are locked out and labeled with a yellow caution tag. The lock’s key is on file with the facility’s secretary

LN2 will be used in the control room. The total room volume is approximately 5500 FT3. The room is partitioned for a gowning area reducing the room volume to approximately 3800 FT3. A 21 liter LN2 spill is allowed and maintains an ODH Class 0; the Oxygen partial pressure does not dip below 18%. Using a fresh air makeup of 20 FT3/min, approximately 25 minutes are needed to return the partial pressure of oxygen to 21.9%. Signs are posted to limit the amount of liquid nitrogen in the room to 21 liters. A Job Hazard Analysis is written to ensure workers understand proper personal protection when handling liquid nitrogen, the limitation on the amount of liquid nitrogen that can be stored in the control room, and no additional liquid nitrogen to be brought into the room during a power failure.

#### Lab A Control Room with LN2 Auto Fill System Addendum H. Cease 11/29/05

An automatic LN2 fill system is replacing the need to hand fill small dewars inside the Control Room.  The automatic fill system has a 1000 liter dewar outside the building, a single plumbing line enters the building and runs through the Lab A space, then into the Lab A control room. The supply line of the 1000 liter dewar has a solenoid valve such that in the event of a power failure, LN2 supply is stopped from entering the building. The ODH in Lab A remains Class 0 since the probability of a plumbing line failure is low independent of flow rate.  Oxygen monitors on the wall in the Lab A Control Room are used in a fail safe mode where in the event of a power failure or a drop in the partial pressure of Oxygen, the LN2 supply solenoid valve is closed. The Oxygen monitor power is tied to the powered ventilation in the room. If power fails to the ventilation, the Oxygen monitor power also fails, closing the LN2 supply solenoid. The ODH in the Lab A Control Room is Class 0 since in the event of a failure, the LN2 supply is shut off.

The total room volume is approximately 5500 FT3. The room is partitioned for a gowning area reducing the room volume to approximately 3800 FT3. A 21 liter LN2 spill is allowed and maintains an ODH Class 0; the Oxygen partial pressure does not dip below 18%. Using a fresh air makeup of 20 FT3/min, approximately 25 minutes are needed to return the partial pressure of oxygen to 21.9%. Signs are posted to limit the amount of liquid nitrogen in the room to 21 liters. Although carrying in hand flasks with LN2 is no longer needed, the amount of LN2 stored in internal dewars remains limited to 21 liters.

A Job Hazard Analysis is revised to ensure workers understand proper personal protection when handling liquid nitrogen, the limitation on the amount of liquid nitrogen that can be stored in the control room, no additional liquid nitrogen to be brought into the room during a power failure, and to leave the room in the event the Oxygen monitor is tripped.

#### Lab B Shop and Basement

Lab B houses a small machine shop and technician work area.  It also held the old Bubble Chamber and for that reason is the only building at SiDet with a basement.  The shop area and basement around the bubble chamber are considered a single building volume since they are interconnected through large openings.

Lab B has corrugated steel walls and a large rollup door to the outside.  The infiltration rate into the building due to the leaky nature of the structure is estimated to be 35 CFM based on one building volume change per day.

Lab B is the terminal branch of the nitrogen header.  The pipe lengths, number of valves, purge enclosures, and potential spill rates are summarized in the appended analysis.

Freezers in the basement are purged with nitrogen to reduce the accumulation of ice inside them.  Currently, 0.03 SCFM of purge gas is used.  The analysis conservatively assumes 0.3 SCFM or purge may eventually be drawn in the shop.  A restricting orifice in the line feeding this drop limits the maximum flow to 1.8 SCFM.  The calculation shows that the Lab B shop is an ODH class 0 environment.

#### Lab B Lotema Room

Three smaller rooms are attached to the larger Lab B shop.  They are each analyzed separately.  The construction of these rooms is the same as the rest of Lab B.  The estimated infiltration rate into the Lotema Room due to the leaky construction is 33 CFM.

The Lotema Room is usually used to setup tests and experiments.  There are currently no purge volumes in the room but nitrogen is sometimes used as a purge when running cold tests to prevent the formation of condensation on test pieces.  A half-inch nitrogen header runs the perimeter of the room.  A restricting orifice in the line limits the maximum flow into the room to 1.8 SCFM.  For this analysis, it is assumed that a second valve is attached to each of the five drops and each is drawing 0.1 SCFM of nitrogen gas.

The attached analysis shows that the Lotema room is a class 0 ODH environment.

#### Lab B Mycom and Norwalk Rooms

These rooms are fairly small (6300 ft3 for Mycom and 5000 ft3 for Norwalk) so the estimated infiltrated rates do not provide enough confidence that natural infiltration is an adequate source of fresh air.  Forced ventilation of 550 CFM is provided to each room with fans (Comair-Rotron brand, Caravel model).  The switches on the fans are locked out and labeled with a yellow caution tag.  The lock’s key is on file with the facility’s secretary.  The facility’s systems technician verifies operation regularly.   A copy of the verification log is included in the appendix.

The Mycom room is currently used as an assembly area.  There are currently two volumes in the room drawing 0.03 SCFM of nitrogen.  A half-inch nitrogen header runs the room’s perimeter and includes three drops.  A restricting orifice in the line limits the maximum flow into the room to 1.8 SCFM.  For this analysis, it is assumed that a second valve is attached to each of the three drops and each is drawing 0.1 SCFM of nitrogen gas.

The attached analysis shows that the Mycom room is a class 0 ODH environment for both ‘normal ventilation’ and ‘ventilation failure’ cases.  A 1 CFM of infiltration was assumed for the ventilation failure analysis.  It is equivalent to a room air change every 4.3 days.  A calculation in the appendix shows that a leak of 0.3 SCFM of nitrogen gas into the room will result in an oxygen level of 18% after 54 hours.  This calculation is included in the appendix.  The 12-hour time-delay shutoff in the facility’s main nitrogen feed line eliminates any ODH concern for outages of 12 hours or more.

The Norwalk room is currently used as an assembly area.  Currently there are no users attached to the nitrogen lines in the room.  A restricting orifice limits the maximum flow into the room to 1.8 SCFM.  For this analysis, it is assumed that a second valve is attached to each of the three drops and each is drawing 0.1 SCFM of nitrogen gas.

The attached analysis shows that the Norwalk room is a class 0 ODH environment for both ‘normal ventilation’ and ‘ventilation failure’ cases.  A 1 CFM of infiltration was assumed for the ventilation failure analysis.  It is equivalent to a room air change every 3.5 days.  A calculation in the appendix shows that a leak of 0.3 SCFM of nitrogen gas into the room will result in an oxygen level of 18% after 43 hours.  This calculation is included in the appendix.  The 12-hour time-delay shutoff in the facility’s main nitrogen feed line eliminates any ODH concern for outages of 12 hours or more.

#### A-B Bridge

The A-B Bridge is a steel shell industrial building on a concrete pad.  It houses both offices and lab space.  The building is ventilated by AC-1, a Trane model YCH330 unit rated to deliver 11,000 CFM.  The minimum fresh air intake on the unit is 646 CFM but is delivered only when the thermostat calls for operation.  Like other industrial buildings, fresh air is maintained by infiltration leakage.  This number is estimated as 64 CFM.

The attached analysis summarizes the current piping sizes and lengths and the size and number of valves inside the A-B Bridge.  There are three possible modes of nitrogen delivery to the bridge considered: full rupture of the piping or valves, leakage from a joint failure on the piping, and intentional purging of nitrogen gas into dry boxes.  For conservativeness, it is assumed that one purge box is used at each of the eight nitrogen drops.  There is currently only one enclosure in the bridge that is fed a nitrogen purge.  The total current purge consumption is 0.01 SCFM of nitrogen.  To be conservative, a purge rate of 0.8 SCFM is used in the ODH analysis.  This is calculated by assuming a purge enclosure is added to each of the existing (8) drops from the nitrogen header and each draws 0.1 SCFM.  Since purging is intentional and continual, the probability of this mode of delivery assigned in the spreadsheet is 1.

The probabilities assigned to a pipe rupture, valve rupture, and leaky joint (weld) are taken from Table 2 in FESHM chapter 5064.  The spill rate out of a leaking joint in the header is conservatively assigned 5 SCFM.  The spill rate from a ruptured valve or pipe is 25 SCFM, the maximum flow that can be delivered to the system.  Orifices in each drop limit the maximum flow rate to 0.9 SCFM.  This calculation is in the appendix.

The attached analysis shows that the Lab A-B Bridge is a class 0 ODH environment.

#### Lab C

Lab C is an industrial building shell constructed on a concrete pad with corrugated steel walls and an asphalt roof.  The building is heated and cooled by a unit that runs only when called for by a thermostat.  The building’s natural leakiness, or infiltration, provides adequate fresh air for its occupants and the operations taking place within it.  The estimated infiltration rate for the building is 69 CFM.  The building volume is 100,000 FT3.

The gaseous nitrogen supply header enters from the C-D Cross Connection and exits towards Lab A.  There is additional piping inside the Lab C clean room, which resides in the volume of the Lab C shell.  The nitrogen is fed to the clean room through a single ½-inch line dropped through the ceiling.  Since the clean room is contained within the larger shell, any nitrogen leak in the clean room eventually finds its way into the larger high bay volume.  The attached Lab C analysis summarizes the piping found in the high bay and the clean rooms.  The pipe lengths and valve count are included.  A spill rate of 25 SCFM for catastrophic failure of components is used for piping in the high bay.  The flow-limiting orifice in the feed to SiDet sets this limit.  The spill rate from components inside the clean room is controlled by a flow-limiting orifice in the ½-inch pipe feeding the clean room.  The maximum spill is 3.8 SCFM.

The calculation shows that the Lab C high bay is an ODH class 0 environment.  Since the ventilation of the building is supplied by natural infiltration, no analysis is required for the case of a ‘ventilation failure’.

#### Lab C Clean Rooms

A glass wall separates the clean rooms into ‘north’ and ‘south’.  The two sides are connected with a walk-through door and a large rollup door (normally closed).  The ventilation system is described in FESS drawing number 8-2-125.  The two sides have identical ventilation systems.  Each includes two parallel cooling units that feed a larger ventilation blower with associated HEPA filtration.  The cooling units each have a 5 HP direct-drive blower.  They supply the suction side of an airfoil scroll unit driven by a 10 HP motor.  The makeup rate on each cooling unit specified on the drawing is 500 CFM, or 1000 CFM of fresh air to each clean room.  Measurements indicate the makeup rate is currently 1240 CFM to the north and 1232 to the south.  The analysis uses 1000 CFM per the design specification.  Ventilation makeup is drawn from the Lab C shell.

The attached analysis summarizes the current piping sizes and lengths and the size and number of valves inside the clean room.  Since the piping, ventilation, and sizes of the two halves are very similar a single analysis is valid for both sides.  The piping system is fed by a single ½” drop from the header through the clean room roof.  A restricting orifice in the drop, located above the clean room roof, limits the maximum nitrogen flow to 3.8 SCFM.  The orifice calculation is included in the appendix.

There is currently one enclosure in the north side and seven in the south that are receiving nitrogen purge.  The current consumptions are 0.14 and 0.25 SCFM of nitrogen respectively.  To be conservative, a purge rate of 1.0 SCFM per side is used in the ODH analysis.  This is calculated by assuming a purge enclosure is added to each of the existing (10) ports on the nitrogen header and each draws 0.1 SCFM of nitrogen.  The valve total in the tables also shows that a valve is assumed to be included on each purge enclosure.

The analysis shows that Lab C clean rooms have ODH class 0 rating.  The analysis in the appendix is for the normal ventilation condition.  The second condition to consider includes the probability of failure of the ventilation system.  This is discussed in the following paragraph.

From the perspective of controlling oxygen deficiency hazards, the ventilation system is very robust.  The system for each half of the clean room includes three fans.  Although a mechanical failure of the main HEPA blower would reduce the nominal makeup, the smaller 5 HP units will very easily draw the minimum makeup required to control the hazard.  As stated above, each half of the clean room normally is fed 1200 CFM of makeup air.  When considering the probability of mechanical failure of the primary blower, it is calculated that only 2 CFM of makeup air is needed to control the oxygen deficiency hazard.  The parallel Liebert blowers feeding the larger unit will continue to push 450 CFM of makeup air through the system when the main unit is inoperable.  This was determined by a test.  Therefore the hazard is controlled in the event of a mechanical failure of the main blower.  The probability of failure of two of the three blowers is Pevent = Pn, where P = 1e-5 motor failures/hr and n = 2 motors.  Therefore the probability of a complete loss of ventilation on either half of the clean room from mechanical failure is 1e-10/hr and further calculation is not required.

Because each clean room has its own separate ventilation system, there is an additional level of ventilation redundancy.  Each clean room is pressurized to 0.04”WC.  A total failure of one unit, and subsequent depressurization of the clean space, would cause leakage of air from the other half of the clean room (whose ventilation system is still operational) around the cracks in the window seals and around the walk-through and rollup doors separating the two sides.  A 1.4 in2 leak area between the north and south clean rooms provides 5 CFM of air into the depressurized room.

During a power outage, it would take more than 50 hours of a 1.0 SCFM purge and zero makeup air to lower the oxygen concentration in the either half of the clean room to 18%.  This calculation is included in the appendix.  The 12-hour time-delay shutoff in the facility’s main nitrogen feed line eliminates any ODH concern for outages of 12 hours or more.

#### C-D Cross Connect

The C-D Cross Connect holds both office and testing space.  It is constructed in the same style as other industrial buildings in the complex.  The building temperature is controlled by an HVAC unit that runs only when the thermostat calls for heating or cooling.  The estimated infiltration rate for the building is 53 CFM, based on one air exchange per day for the building’s 75,600 FT3 volume.

The gaseous nitrogen supply header enters from Lab D and exits to Lab C.  Nitrogen gas is available in the testing area for purge volumes.  The attached analysis summarizes the piping found in the C-D cross connect.  The pipe lengths and valve count are included.  A spill rate of 25 SCFM for catastrophic failure of components is used for the overhead piping while the flow-limiting orifice in the drops controls the maximum spill in the testing area to 1.8 SCFM.

There are currently eight enclosures in the cross-connect receiving nitrogen purge.  The current consumption is 0.2 SCFM.  To be conservative, a purge rate of 1.1 SCFM is used in the ODH analysis.  This is calculated by assuming a purge enclosure is added to each of the existing (11) ports on the nitrogen header and each draws 0.1 SCFM of nitrogen.

The calculation shows that the C-D cross connect is an ODH class 0 environment.  Since the ventilation of the building is supplied by natural infiltration, no analysis is required for the case of a ‘ventilation failure’.

#### Lab D

Lab D is an industrial building shell constructed on a concrete pad with corrugated steel walls and an asphalt roof.  The building is heated and cooled by AHU-1.  The unit runs only when heating and cooling are required.  The building’s natural infiltration provides adequate fresh air for its occupants and the operations taking place within it.  The estimated infiltration rate for the building is 72 CFM, assuming one volume change per day.  The building volume is 103,800 FT3.

The gaseous nitrogen supply line enters the Silicon Facility through the northeast corner of Lab D.  Additionally, there is piping inside the Lab D clean room and Bonding Area, which reside inside the shell of Lab D.  Since the clean room and bonding area are contained within the larger shell, any nitrogen leaked in theses spaces will eventually find its way into the larger high bay volume.  The attached analysis summarizes the piping found in the high bay, clean room, and bonding area.  The pipe lengths and valve count are included.  A spill rate of 25 SCFM for catastrophic failure of components is used for piping in the high bay.  The orifice outside the building that controls the total flow to the facility sets this limit.  The spill rate from components inside the clean room and bonding area is controlled by flow limiting orifices in the individual pipe drops to these spaces.  This number is 1.8 SCFM.

The calculation shows that the Lab D high bay is an ODH class 0 environment.  Since the ventilation of the building is supplied by natural infiltration, no analysis is required for the case of a ‘ventilation failure’.

#### Lab D Clean Room

The Lab D clean room resides inside the Lab D high bay.  The clean room has a separate air-handling unit (ACU-2) on the roof of Lab D.  It draws fresh air from outdoors.  The makeup on the unit is 1100 CFM.  The unit runs continuously.

The attached analysis summarizes the current piping sizes and lengths and the size and number of valves inside the clean room.  The system is fed by four ½” drops from the above header in the Lab D high bay.  A restricting orifice in each drop limits the maximum flow to 1.8 SCFM in each line.  The orifices are located in the drops above the clean room roof.  Therefore a catastrophic failure of any piping component results in a maximum spill of 1.8 SCFM.  The orifice calculation is included in the appendix.

There are currently eleven enclosures in the clean room that are fed a nitrogen purge.  The total current consumption is 0.5 SCFM of nitrogen.  To be conservative, a purge rate of 2.4 SCFM is used in the ODH analysis.  This is calculated by assuming a purge enclosure is added to each of the existing (24) ports on the nitrogen header and each draws 0.1 SCFM of nitrogen.

The attached analysis shows that with a ventilation rate of 1100 CFM provided by the air-handling unit, the risk of death by asphyxiation from the nitrogen system is very low and the space has an ODH class 0 rating.

In the event that forced ventilation to the clean room is lost due to a mechanical failure of the air handling unit, the second table shows that the simultaneous probability of a leak event and the mechanical breakdown of the AHU is so unlikely that the clean room remains an ODH class 0 environment.  For this case, a minimum infiltration rate of 5 CFM of fresh air is assumed due to leakage from the attached annex called the Bonding Area.  The Bonding Area has its own ventilation system and is connected to the Lab D clean room by a walkthrough door and a large rollup door.  Both doors are usually closed but present enough of a leak path around cracks to easily provide the 5 CFM used in the analysis.  Additional sources of leakage include stack effects to the outdoors through the clean room’s ventilation system as well as normal opening and closing of doors.

The probability assigned to the mechanical failure of the air-handling unit was taken from Table 2 in FESHM 5064 for the failure of an electrical motor (1x10-5events/hr).  A column is added to the table to multiply the probability of the leak times the probability of a ventilation failure due to motor failure.

Ventilation loss as a result of a power outage is a more frequent event at Fermilab.  Power outages typically last a few hours at most.  Table 1 in FESHM 5064 provides a 1-hour duration for unplanned outages.  It takes 30 hours of a 2.4 SCFM purge to lower the oxygen concentration in the clean room to 18%.  This calculation is included in the appendix.  The 12-hour time-delay shutoff in the facility’s main nitrogen feed line eliminates any ODH concern for outages of 12 hours or more.

#### Lab D Bonding Area

The Bonding Area is adjacent to the clean room.  It is a semi-clean space heated and cooled by a small air-handling unit in the hallway.  The AHU delivers approximately 1400 CFM to the suction side of three HEPA units installed in the ceiling.  A makeup rate of 25 CFM is drawn from the high bay.

The nitrogen header does not run through this area but some nitrogen is fed to the room through plastic lines to feed dry boxes and as a utility at some of the bonding stations.   An orifice in the copper line that feeds this space limits the maximum spill rate to 1.8 SCFM.  The purge volumes currently consume 0.2 SCFM but 1.0 SCFM is used in the analysis.  The analysis assumes one valve for each of the six bonding stations and one on each of ten possible dry boxes.

From an ODH standpoint, the ventilation system is robust since it includes the main blower on the AHU as well as individual fans on the three ceiling-mounted HEPA units.  Forced ventilation will still exist with a single failure on the main blower or one of the HEPA units.   Furthermore, the adjacent Lab D clean room normally operates at 0.01”WC of positive pressure.  This provides a constant rate of leakage into the bonding area through the large rollup door, walkthrough door, and pass through window.  A small 5 CFM of makeup air is assumed in the analysis for the case of a mechanical breakdown of one of the HEPA units or the main blower.

For both normal operation of the ventilation system and a possible single mechanical failure in the system, the attached analyses show the space has an ODH class 0.  In the event of a power outage, it would take 23 hours of a 1.0 SCFM purge to lower the oxygen concentration in the clean room to 18%.  This calculation is included in the appendix.  The 12-hour time-delay shutoff in the facility’s main nitrogen feed line eliminates any ODH concern for outages of 12 hours or more.