| REQUEST FOR QUOTATION | This RFQ | X |  |  | is not a small Business set-aside | Page | 1 | of | 10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (THIS IS NOT AN ORDER) |  |  |  |  |  |  |  |  |  |
| 1.REQUEST NO | 2.DATE ISSUED | 3.REQUISITION/PURCHASE REQ NO. | 4. CERT FOR NAT. DEF. UNDER BDSA REG 2 AND/OR DMS REQ. 1 | RATING |
| DE-RQ65-02WG60833 | JULY 16,2002 | G60833 |  |  |
| 5a. ISSUED BY | 6. DELIVERY BY (Date) |
| U.S. DEPT OF ENERGY | November 28, 2002 |
| WESTERN AREA POWER ADMIN | 7. DELIVERY |
| 615 S 43rd AVENUE |  |
| PHOENIZ, AZ 85009-5313 | X | FOB Destination |  | Other (See Schedule) |
| 5b. FOR MORE INFORMATION CALL (No Collect Calls) | 9. DESTINATION PAO-WHSE |
| NAME | Area Code | Telephone | a. NAME OF CONSIGNEE |
| Lary A. Martin | G06 | 602 | 352-2646 | WESTERN AREA POWER ADMINISTRATION |
| 8. TO | b. STREET ADDRESS |
| a. NAME | b. COMPANY | 615 SOUTH 43RD AVENUE |
|  |  | PHOENIX, AZ 85009 |
| c. STREET ADDRESS | c. CITY |
|  | PHOENIX |
| d. CITY | e. STATE | f. ZIP CODE | d. STATE | e. ZIP CODE |
|  |  |  | AZ | 85009 |
| 10. PLEASE FURNISH QUOTATIONS TO THE ISSUING OFFICE IN BLOCK 5A ON OR BEFORE CLOSE OF BUSINESS (DATE) | IMPORTANT: This is a request for information and quotations furnished are not offers. If you are unable to quote, please so indicate on this form and return it to the address in Block 5A. This request does not commit the Government to pay any costs incurred in the the submission of this quotation or to contract for supplies or services. Supplies are of domestic origin unless otherwise indicated by Any representations and/or certifications to this Request for Quotations must be completed by the quoter. |
| July 29, 2002 |  |
| 11. SCHEDULE (Indicate applicable Federal, State and local taxes) |
| ITEM NO. (a) | SUPPLIES/SERVICES (b) | QUANTITY (c) | UNIT (d) | UNIT PRICE (f) | AMOUNT (f) |  |
| 0001 | CHARGER, BATTERY: 125 volt,55 ampere DC output, 1-phase 240 volt AC input source, for Lone Butte Substation Stage 02, FOB Destination 2 EA $_________ $_________ BIDDING ON: Manufacturer's Name:________________. Model/Type:___________ | 2 | EA | ______________ | ______________ |  |
| 0002 | Spare Parts for Item 0001,for Lone Butte Substation, Stage 02, FOB Destination Responses can be faxed to 602-352-2483 | 1 | SET | ______________ | ______________ |  |

## 52.213-4 Terms and Conditions-Simplified Acquisitions (Other Than Commercial Items).  (Apr 2002)

## (a) The Contractor shall comply with the following Federal Acquisition Regulation (FAR) clauses that are incorporated by reference:

(1) The clauses listed below implement provisions of law or Executive order:

(i) 52.222-3, Convict Labor (Aug 1996) (E.O. 11755).

(ii) 52.222-21, Prohibition of Segregated Facilities (Feb 1999)(E.O. 11246)

(iii) 52.222-26, Equal Opportunity (Apr 2002)(E.O. 11246)

(iv) 52.225-13, Restrictions on Certain Foreign Purchases (July 2000) (E.O.'s 12722, 12724, 13059, 13067, 13121, and 13129).

(v) 52.233-3, Protest After Award (Aug 1996) (31 U.S.C. 3553).

(2) Listed below are additional clauses that apply:

(i) 52.232-1, Payments (Apr 1984).

(ii) 52.232-8, Discounts for Prompt Payment (May 1997).

(iii) 52.232-11, Extras (Apr 1984).

(iv) 52.232-25, Prompt Payment (June 1997).

(v) 52.233-1, Disputes (Dec 1998).

(vi) 52.244-6, Subcontracts for Commercial Items and Commercial Components (Dec 2001).

(vii) 52.253-1, Computer Generated Forms (Jan 1991).

(b) The Contractor shall comply with the following FAR clauses, incorporated by reference, unless the circumstances do not apply:

(1) The clauses listed below implement provisions of law or Executive order:

(i) 52.222-20, Walsh-Healey Public Contracts Act (Dec 1996) (41 U.S.C. 35-45) (Applies to supply contracts over $10,000 in the United States, Puerto Rico, or the U.S. Virgin Islands).

(ii) 52.222-35, Equal Opportunity for Special Disabled Veterans, Veterans of the Vietnam Era, and Other Eligible Veterans (Dec 2001) (38 U.S.C. 4212) (Applies to contracts of $25,000 or more).

(iii) 52.222-36, Affirmative Action for Workers with Disabilities (June 1998) (29 U.S.C. 793) (Applies to contracts over $10,000, unless the work is to be performed outside the United States by employees recruited outside the United States.)  (For purposes of this clause, United States includes the 50 States, District of Columbia, Puerto Rico, the Northern Mariana Islands, American Samoa, Guam, the U.S. Virgin Islands, and Wake Island.)

(iv) 52.222-37, Employment Reports on Special Disabled Veterans, Veterans of the Vietnam Era, and Other Eligible Veterans (Dec 2001) (38 U.S.C. 4212) (Applies to contracts of $25,000 or more).

(v) 52.222-41, Service Contract Act of 1965, As Amended (May 1989) (41 U.S.C. 351, et seq.) (Applies to service contracts over $2,500 that are subject to the Service Contract Act and will be performed in the United States, District of Columbia, Puerto Rico, the Northern Mariana Islands, American Samoa, Guam, the U.S. Virgin Islands, Johnston Island, Wake Island, or the outer continental shelf lands).

(vi) 52.222-19, Child Labor-Cooperation with Authorities and Remedies (Dec 2001) (E.O. 13126). (Applies to contracts for supplies exceeding the micro-purchase threshold.)

(vii) 52.223-5, Pollution Prevention and Right-to-Know Information (Apr 1998) (E.O. 12856) (Applies to services performed on Federal facilities).

(viii) 52.225-1, Buy American Act-Balance of Payments Program-Supplies (Feb 2000) (41 U.S.C. 10a - 10d) (Applies to contracts for supplies, and to contracts for services involving the furnishing of supplies, for use within the United States if the value of the supply contract or supply portion of a service contract exceeds the micro-purchase threshold and the acquisition-

(A) Is set aside for small business concerns; or

(B) Cannot be set aside for small business concerns (see 19.502-2), and does not exceed $25,000).

(ix) 52.232-33, Payment by Electronic Funds Transfer-Central Contractor Registration (May 1999). (Applies when the payment will be made by electronic funds transfer (EFT) and the payment office uses the Central Contractor Registration (CCR) database as its source of EFT information.)

(x) 52.232-34, Payment by Electronic Funds Transfer-Other than Central Contractor Registration (May 1999). (Applies when the payment will be made by EFT and the payment office does not use the CCR database as its source of EFT information.)

(xi) 52.247-64, Preference for Privately Owned U.S.-Flag Commercial Vessels (June 2000) (46 U.S.C. 1241). (Applies to supplies transported by ocean vessels.)

(2) Listed below are additional clauses that may apply:

(i) 52.209-6, Protecting the Government's Interest When Subcontracting with Contractors Debarred, Suspended, or Proposed for Debarment (July 1995) (Applies to contracts over $25,000).

(ii) 52.211-17, Delivery of Excess Quantities (Sept 1989) (Applies to fixed-price supplies).

(iii) 52.247-29, F.o.b. Origin (June 1988) (Applies to supplies if delivery is f.o.b. origin).

(iv) 52.247-34, F.o.b. Destination (Nov 1991) (Applies to supplies if delivery is f.o.b. destination).

(c) FAR 52.252-2, Clauses Incorporated by Reference (Feb 1998). This contract incorporates one or more clauses by reference, with the same force and effect as if they were given in full text. Upon request, the Contracting Officer will make their full text available. Also, the full text of a clause may be accessed electronically at this/these address(es):

_____www.arnet.gov/far_______________________

___________________________________________

[Insert one or more Internet addresses]

(d) Inspection/Acceptance. The Contractor shall tender for acceptance only those items that conform to the requirements of this contract. The Government reserves the right to inspect or test any supplies or services that have been tendered for acceptance. The Government may require repair or replacement of nonconforming supplies or reperformance of nonconforming services at no increase in contract price. The Government must exercise its postacceptance rights-

(1) Within a reasonable period of time after the defect was discovered or should have been discovered; and

(2) Before any substantial change occurs in the condition of the item, unless the change is due to the defect in the item.

(e) Excusable delays. The Contractor shall be liable for default unless nonperformance is caused by an occurrence beyond the reasonable control of the Contractor and without its fault or negligence, such as acts of God or the public enemy, acts of the Government in either its sovereign or contractual capacity, fires, floods, epidemics, quarantine restrictions, strikes, unusually severe weather, and delays of common carriers. The Contractor shall notify the Contracting Officer in writing as soon as it is reasonably possible after the commencement of any excusable delay, setting forth the full particulars in connection therewith, shall remedy such occurrence with all reasonable dispatch, and shall promptly give written notice to the Contracting Officer of the cessation of such occurrence.

(f) Termination for the Government's convenience. The Government reserves the right to terminate this contract, or any part hereof, for its sole convenience. In the event of such termination, the Contractor shall immediately stop all work hereunder and shall immediately cause any and all of its suppliers and subcontractors to cease work. Subject to the terms of this contract, the Contractor shall be paid a percentage of the contract price reflecting the percentage of the work performed prior to the notice of termination, plus reasonable charges that the Contractor can demonstrate to the satisfaction of the Government, using its standard record keeping system, have resulted from the termination. The Contractor shall not be required to comply with the cost accounting standards or contract cost principles for this purpose. This paragraph does not give the Government any right to audit the Contractor's records. The Contractor shall not be paid for any work performed or costs incurred that reasonably could have been avoided.

(g) Termination for cause. The Government may terminate this contract, or any part hereof, for cause in the event of any default by the Contractor, or if the Contractor fails to comply with any contract terms and conditions, or fails to provide the Government, upon request, with adequate assurances of future performance. In the event of termination for cause, the Government shall not be liable to the Contractor for any amount for supplies or services not accepted, and the Contractor shall be liable to the Government for any and all rights and remedies provided by law. If it is determined that the Government improperly terminated this contract for default, such termination shall be deemed a termination for convenience.

(h) Warranty. The Contractor warrants and implies that the items delivered hereunder are merchantable and fit for use for the particular purpose described in this contract.

(End of clause)

52.211-5 Material Requirements (Aug 2000)

(a) Definitions.

As used in this clause--

"New" means composed of previously unused components, whether manufactured from virgin material, recovered material in the form of raw material, or materials and by-products generated from, and reused within, an original manufacturing process; provided that the supplies meet contract requirements,

including but not limited to, performance, reliability, and life expectancy.

"Reconditioned" means restored to the original normal operating condition by readjustments and material replacement.

"Recovered material" means waste materials and by-products recovered or diverted from solid waste, but the term does not include those materials and

by-products generated from, and commonly reused within, an original manufacturing process.

"Remanufactured" means factory rebuilt to original specifications.

"Virgin material" means--

(1) Previously unused raw material, including previously unused copper, aluminum, lead, zinc, iron, other metal or metal ore; or

(2) Any undeveloped resource that is, or with new technology will become, a source of raw materials.

(b) Unless this contract otherwise requires virgin material or supplies composed of or manufactured from virgin material, the Contractor shall provide

supplies that are new, reconditioned, or remanufactured, as defined in this clause.

(c) A proposal to provide unused former Government surplus property shall include a complete description of the material, the quantity, the name of the

Government agency from which acquired, and the date of acquisition.

(d) A proposal to provide used, reconditioned, or remanufactured supplies shall include a detailed description of such supplies and shall be submitted

to the Contracting Officer for approval.

(e) Used, reconditioned, or remanufactured supplies, or unused former Government surplus property, may be used in contract performance if the

Contractor has proposed the use of such supplies, and the Contracting Officer has authorized their use.

(End of clause)

#### 52.225-2 Buy American Act--Balance of Payments Program Certificate.  (Feb 2000)

(a) The offeror certifies that each end product, except those listed in paragraph (b) of this provision, is a domestic end product as defined in the clause of this solicitation entitled "Buy American Act--Balance of Payments Program--Supplies" and that the offeror has considered components of unknown origin to have been mined, produced, or manufactured outside the United States. The offeror shall list as foreign end products those end products manufactured in the United States that do not qualify as domestic end products.

(b) Foreign End Products:

Line Item No 		Country of Origin

______________ 	_________________

______________ 	_________________

______________ 	_________________

[List as necessary]

(c) The Government will evaluate offers in accordance with the policies and procedures of Part 25 of the Federal Acquisition Regulation.

(End of provision)

52.243-1 Changes--Fixed Price (Aug 1987)

(a) The Contracting Officer may at any time, by written order, and without notice to the sureties, if any, make changes within the general scope of this contract in any one or more of the following:

(1) Drawings, designs, or specifications when the supplies to be furnished are to be specially manufactured for the Government in accordance with the drawings, designs, or specifications.

(2) Method of shipment or packing.

(3) Place of delivery.

(b) If any such change causes an increase or decrease in the cost of, or the time required for, performance of any part of the work under this contract, whether or not changed by the order, the Contracting Officer shall make an equitable adjustment in the contract price, the delivery schedule, or both, and shall modify the contract.

(c) The Contractor must assert its right to an adjustment under this clause within 30 days from the date of receipt of the written order. However, if the Contracting Officer decides that the facts justify it, the Contracting Officer may receive and act upon a proposal submitted before final payment of the contract.

(d) If the Contractor's proposal includes the cost of property made obsolete or excess by the change, the Contracting Officer shall have the right to prescribe the manner of the disposition of the property.

(e) Failure to agree to any adjustment shall be a dispute under the Disputes clause. However, nothing in this clause shall excuse the Contractor from

proceeding with the contract as changed.

(End of clause)

The following clause applies only to solicitations/contracts set-aside for Small Businesses:

52.219-6 Notice of Total Small Business Set-Aside (Jul 1996)

(a) Definition. "Small business concern," as used in this clause, means a concern, including its affiliates, that is independently owned and operated, not

dominant in the field of operation in which it is bidding on Government contracts, and qualified as a small business under the size standards in this solicitation.

(b) General. (1) Offers are solicited only from small business concerns. Offers received from concerns that are not small business concerns shall be

considered nonresponsive and will be rejected.

(2) Any award resulting from this solicitation will be made to a small business concern.

(c) Agreement. A small business concern submitting an offer in its own name agrees to furnish, in performing the contract, only end items manufactured

or produced by small business concerns in the United States. The term "United States" includes its territories and possessions, the Commonwealth of Puerto Rico, the trust territory of the Pacific Islands, and the District of Columbia. If this procurement is processed under simplified acquisition procedures and the total amount of this contract does not exceed $25,000, a small business concern may furnish the product of any domestic firm. This paragraph does not apply in connection with construction or service contracts.

(End of clause)

The following clause is incorporated by reference and applies only to Purchase Orders with Individuals:

52.223-6  Drug-Free Workplace (May 2001)

The following clauses apply to any awards made with ‘appropriated funds.’  Contact the contracting officer to see if these clauses will apply to this particular solicitation or award:

LH.0000-0078 Lobbying Restriction (Energy and Water Development Appropriations Act, 2000 (WAPA, Feb 2000)

The contractor agrees that none of the funds obligated on this award shall be expended, directly or indirectly, to influence Congressional action on any legislation or appropriation matters pending before Congress, other than to communicate to Members of Congress as described in 18 U.S.C. 1913.  This restriction is in addition to those prescribed elsewhere in statute and regulation.

(End of Clause)

LH.0000-0079 Notice Regarding the Purchase of American-Made Equipment and Products – Sense of Congress (WAPA, Feb 2000)

It is the sense of the Congress that, to the greatest extent practicable,

all equipment and products purchased with funds made available under this award should be American-made.

(End of Notice)

The following clause only applies to Purchase Orders greater than $25,000:

DE.0222-0037 Compliance With Veteran’s Employment Reporting  Requirements (WAPA, Jan  2000)

(a) The Offeror represents that, if it is subject to the reporting requirements of 38 U.S.C. 4212(d) (i.e. VETS-100 report required by the Federal Acquisition Regulation clause 52.222-37, Employment Reports on Disabled Veterans and Veterans of the Vietnam Era), it has (____), has not (____) submitted the most recent report required by 38 U.S.C. 4212(d).

(b) An Offeror who checks 'has not' may not be awarded a contract until the required reports are filed. (31 U.S.C. 1354)

(End of Provision)

52.219-1 Small Business Program Representations (Apr 2002)

(a)(1) The North American Industry Classification System (NAICS) code for this acquisition is 327113.

(2) The small business size standard is 500.

(3) The small business size standard for a concern which submits an offer in its own name, other than on a construction or service contract, but which proposes to furnish a product which it did not itself manufacture, is 500 employees.

(b) Representations. (1) The offeror represents as part of its offer that it ____ is, ____ is not a small business concern.

(2) [Complete only if the offeror represented itself as a small business concern in paragraph (b)(1) of this provision.] The offeror represents, for general statistical purposes, that it ____ is, ____ is not, a small disadvantaged business concern as defined in 13 CFR 124.1002.

(3) [Complete only if the offeror represented itself as a small business concern in paragraph (b)(1) of this provision.] The offeror represents as part of its offer that it ____ is, ____ is not a women-owned small business concern.

(4) [Complete only if the offeror represented itself as a small business concern in paragraph (b)(1) of this provision.] The offeror represents as part of its offer that it ____ is, ____ is not a veteran-owned small business concern.

(5) [Complete only if the offeror represented itself as a veteran-owned small business concern in paragraph (b)(4) of this provision.] The offeror represents as part of its offer that it ____ is, ____ is not a service-disabled veteran-owned small business concern.

(6) [Complete only if the offeror represented itself as a small business concern in paragraph (b)(1) of this provision.]  The offeror represents, as part of its offer, that-

(i)  It ____ is, ____ is not a HUBZone small business concern listed, on the date of

this representation, on the List of Qualified HUBZone Small Business Concerns maintained by the Small Business Administration in accordance with 13 CFR part 126; and

(ii)  It ____ is, ____ is not a joint venture that complies with the requirements of 13 CFR part 126, and the representation in paragraph (b)(6)(i) of this provision is accurate for the HUBZone small business concern or concerns that are participating in the joint venture.  [The offeror shall enter the name or names of the HUBZone small business soncern or concerns that are participating in the joint venture:_____________________ .]  Each HUBZone small business concern participating in the joint venture shall submit a separate signed copy of the HUBZone representation.

(c) Definitions. As used in this provision--

"Service-disabled veteran-owned small business concern"--

(1) Means a small business concern--

(i) Not less than 51 percent of which is owned by one or more service-disabled veterans or, in the case of any publicly owned business, not less than 51 percent of the stock of which is owned by one or more service-disabled veterans; and

(ii) The management and daily business operations of which are controlled by one or more service-disabled veterans or, in the case of a veteran with permanent and severe disability, the spouse or permanent caregiver of such veteran.

(2) Service-disabled veteran means a veteran, as defined in 38 U.S.C. 101(2), with a disability that is service-connected, as defined in 38 U.S.C. 101(16).

"Small business concern" means a concern, including its affiliates, that is independently owned and operated, not dominant in the field of operation in which it is bidding on Government contracts, and qualified as a small business under the criteria in 13 CFR part 121 and the size standard in paragraph (a) of this provision.

"Veteran-owned small business concern" means a small business concern--

(1) Not less than 51 percent of which is owned by one or more veterans (as defined at 38 U.S.C. 101(2)) or, in the case of any publicly owned business, not less than 51 percent of the stock of which is owned by one or more veterans; and

(2) The management and daily business operations of which are controlled by one or more veterans.

"Women-owned small business concern" means a small business concern--

(1) That is at least 51 percent owned by one or more women; or, in the case of any publicly owned business, at least 51 percent of the stock of which is owned by one or more women; and

(2) Whose management and daily business operations are controlled by one or more women.

(d) Notice. (1) If this solicitation is for supplies and has been set aside, in whole or in part, for small business concerns, then the clause in this solicitation providing notice of the set-aside contains restrictions on the source of the end items to be furnished.

(2) Under 15 U.S.C. 645(d), any person who misrepresents a firm's status as a small, HUBZone small, small disadvantaged, or women-owned small business concern in order to obtain a contract to be awarded under the preference programs established pursuant to section 8(a), 8(d), 9, or 15 of the Small Business Act or any other provision of Federal law that specifically references section 8(d) for a definition of program eligibility, shall--

(i) Be punished by imposition of fine, imprisonment, or both;

(ii) Be subject to administrative remedies, including suspension and debarment; and

(iii) Be ineligible for participation in programs conducted under the authority of the Act.

(End of provision)

Alternate I (Apr 2002). As prescribed in 19.307(a)(2), add the following paragraph (b)(7) to the basic provision:

(7) [Complete if offeror represented itself as disadvantaged in paragraph (b)(2) of this provision.] The offeror shall check the category in which its ownership falls:

_____ Black American.

_____ Hispanic American.

_____ Native American (American Indians, Eskimos, Aleuts, or Native Hawaiians).

_____ Asian-Pacific American (persons with origins from Burma, Thailand, Malaysia, Indonesia, Singapore, Brunei, Japan, China, Taiwan, Laos, Cambodia (Kampuchea), Vietnam, Korea, The Philippines, U.S. Trust Territory of the Pacific Islands (Republic of Palau), Republic of the Marshall Islands, Federated States of Micronesia, the Commonwealth of the Northern Mariana Islands, Guam, Samoa, Macao, Hong Kong, Fiji, Tonga, Kiribati, Tuvalu, or Nauru).

_____ Subcontinent Asian (Asian-Indian) American (persons with origins from India, Pakistan, Bangladesh, Sri Lanka, Bhutan, the Maldives Islands, or Nepal).

_____ Individual/concern, other than one of the preceding.

LH.0000-0071 Electronic Submission of Documents via the DOE IIPS System  (WAPA, 12/2001)

The following requirements apply if proposals or other documents are submitted electronically via the Dept of Energy's 'Industry Interactive Procurement System' (IIPS) or by other electronic means (e.g., electronic files on a CD-ROM):

(a) The terms and conditions contained in the 'Notice of Disclaimer' on the DOE IIPS system (agreed to when vendors register to use the IIPS system)are hereby incorporated into this solicitation/award document.

(b) All document files submitted electronically must be submitted in one or more of the following Microsoft Office 97 for Windows (or newer) file formats (e.g., .doc, .xls, .mdb, .ppt); portable document format (.pdf); or in the following graphic file formats (.gif or .jpg).  Use whichever format is most appropriate for the type of document involved.  Engineering drawings, if any, must be in AutoCAD, PDF, or in one of the acceptable graphic file formats.  NOTE:  if there are an

inordinately large number of drawings, or if the file sizes are prohibitively large, contact the Contracting Officer before the proposal due date and time for further instructions.

(c) Offerors are responsible for ensuring their electronically-submitted files are free from viruses, are in the prescribed, readable format, and are not corrupted.  Replacement of corrupt or unreadable files may be allowed at the sole discretion of the Contracting Officer.  The Contracting Officer may notify the offeror and provide an opportunity for the offeror to submit clear and convincing evidence: 1) of the content of the proposal as originally submitted; and 2) that the

unreadable condition of the proposal was caused by, or is the fault of, the Government.

(d) For purposes of determining the timeliness of proposal submissions, the date/time stamp (DTS) assigned by the IIPS system will be used.  The IIPS DTS uses Eastern Time, so proposal due dates expressed in other time zones will be converted to Eastern Time to make the timeliness determination.

(e) Electronic signatures:  submission of proposals via DOE's IIPS system will constitute 'signed' copies of the required documents.  The name of the authorized, responsible company official who would normally sign that document shall be entered on the signature line. In addition, the Contracting Officer may require, at his or her discretion, a signed, paper copy of each original signature page to be submitted via US Mail or by facsimile.

(f) Updates or changes to proposals or other documents originally submitted via the IIPS system must also be submitted via IIPS. In the event that a conflict or discrepancy is discovered between a paper copy of a vendor or Government document, the copy as posted on the IIPS system shall

be considered the official, 'controlling' version of the document.

(g) Offerors must use discrete file names (and descriptions, where applicable) for all files uploaded to the IIPS system.

(h) Offerors agree to, and certify, that they have not made any changes to Government-originated files/documents - other than for expected signatures or fill-ins - that must be returned to the Government (e.g., Representations and Certifications).  Any questions or concerns about any

Government documents must be communicated directly to the Contracting Officer.

End of Clause

The following provision is required to be completed for Quotes greater than $10,000:

52.222-22  Previous Contracts and Compliance Reports (Feb 1999)

The offeror represents that--

(a) It ____ has, ____ has not participated in a previous contract or subcontract subject the Equal Opportunity clause of this solicitation;

(b) It ____ has, ____ has not filed all required compliance reports; and

(c) Representations indicating submission of required compliance reports, signed by proposed subcontractors, will be obtained before subcontract

awards.

(End of provision)

The following provision is required to be completed for quotes greater than $10,000:

52.222-25 Affirmative Action Compliance (Apr 1984)

The offeror represents that--

(a) It ____ has developed and has on file, ____ has not developed and does not have on file, at each establishment, affirmative action programs required by the

rules and regulations of the Secretary of Labor (41 CFR 60-1 and 60-2); or

(b) It ____ has not previously had contracts subject to the written affirmative action programs requirement of the rules and regulations of the Secretary of

Labor.

(End of provision)

SPECIFICATIONS

DESCRIPTION/SPECIFICATIONS

125 VOLT BATTERY CHARGERS FOR LONE BUTTE SUBSTATION, STAGE 02

1. 	GENERAL: The chargers shall conform to the latest edition/revision of National Electrical Manufacturers' Association (NEMA) Standards Publication No. PE-5 (Utility Type Battery Chargers) and any standards referenced therein. The latest known edition/revision of NEMA PE-5 is dated 1996, with a copyright dated 1997.

In the event of contradiction between NEMA or NEMA-referenced standards and these requirements, the requirement that provides for a safer, quieter, and better designed and built charger shall apply.

2.	ALTERNATING CURRENT INPUT:  Nominal system voltage is 240 volts AC single phase (two legs of a 240V delta) with a +/-10 percent variation in input voltage allowed. Frequency will be 60 Hertz with variation allowed as in referenced NEMA standards.  The battery charger shall operate at a minimum 80 percent efficiency and at a 70 percent or better power factor at full load.

3.	DIRECT CURRENT OUTPUT: Each battery charger shall be part of a 58 cell, 125 volt lead acid lead-calcium flooded cell battery system.  The battery to be charged will be rated 510-535 AHR.

a.	Voltage: The voltage regulation shall be +/- 1 percent over a load range of 1 to 100 percent.  Battery charger design shall provide for float voltage control from 124.7 - 136.3 volts and equalize (a.k.a. “high rate”) voltage control from 127.6 - 142.1 volts.

b.	Current Limiting:  The current limiting circuit shall be adjustable from at least 90 - 110 percent.  Full output (i.e., 100 percent) current rating of the charger at the altitude specified below shall be as specified in the Bid Schedule.

c.	Parallel & Load Sharing Operation:  The charger shall be capable of parallel operation with two compatible battery chargers connected in parallel, and without interconnecting control wiring.

The parallel battery chargers shall also be capable of "forced" load sharing (with interconnecting wiring) any load from 0 amps load to full rated current such that the difference between two parallel chargers shall be no more than 20 percent of the sum of the combined rated charger output currents (e.g., if each charger's rated full output is 55 Amperes, then the difference could not exceed 22 Amperes [20% of 55+55]).

In addition, all parallel and load-shared chargers shall be free from output current instability (hunting) from 20 percent to rated output current.

Any single charger (when operating either in parallel or load sharing with another charger) shall continue to operate without interruption or failure in the event that its counter part fails.

d.	Stand-Alone/No Load Sharing:  Chargers shall each be capable of operating in a stand-alone" mode (no load sharing - one charger "OFF,” one charger "ON"), even with the load sharing wiring connected.

e. 	Effect of Altitude: The charger shall provide the full rated output at an altitude of 1,100 feet above sea level (and lower), with an ambient air temperature range of 0 to 50 degrees C.

4.	PROTECTION:  The AC input shall be protected by a properly sized two-pole circuit breaker.  The DC output shall be protected by a properly sized two-pole circuit breaker.  Both the AC input and the DC output circuits shall be protected from surge and transient voltage and current occurrence, including that related to powering-up the charger from a "cold" start (no previous charge on surge and filter capacitors).

5.	COMPONENTS/CAPABILITIES: Battery charger design must incorporate the following components/capabilities:  (Light emitting diodes (LEDs), neon lamps, long life incandescent lamps, and LCD displays are examples of acceptable forms of indicating lamps.)

a.	Filtering:  Charger output ripple shall be limited to 30 millivolts rms on and 500 millivolts rms off the battery.

b.	Battery Eliminator Capability:  The charger must be able to operate effectively with the battery disconnected from the system.  In addition, the charger shall provide a "soft start" automatic startup with a resistive load only (i.e., battery disconnected) or when connected to the battery.

c.	Battery Discharge Protection:  Circuitry shall prevent the battery from discharging back through the charger in the event of:  AC power failure, being turned OFF (whether via local or remote), or other charger shutdown situations.  Extremely low current requirements of load-side powered controls need not be considered as a cause of battery discharge.

d.	AC Pilot Lamp/LED: This lamp (or LED) shall be a continuous-duty type providing an indication of energized AC input.

e. 	Float Level Control:  Float voltage level control shall be obtained utilizing a variable control, e.g., potentiometer or microprocessor system equivalent.

f.	Equalize Level Control:  Equalize voltage level control shall be obtained utilizing a variable control, e.g., potentiometer or microprocessor system equivalent.

g.	Equalize “Timer Switch” and Lamps/LEDs/LCD display: This control device shall comprise a 0 to 24 hour timer (wider range is acceptable) with an automatic return to float mechanism and operational mode indicator lamps/LEDs.  Equalize mode is to be manually operator selected, and is NOT to occur automatically after loss and restoration of the AC power source.

h.	Automatic Charger Restart:  Each charger shall restart (in float mode) automatically upon loss and restoration of the AC input power.

Local manual ON/OFF control, if provided by the charger manufacturer, shall be accessible from the front (exterior) panel of the charger.

i.	Battery Temperature Compensation:  Each battery charger shall be provided with temperature compensation that varies the charger float voltage (measured at the battery terminals) to compensate for battery temperature variations from 77 degrees F (25 degrees C) per the following equations:

V corrected = V77°F - ((T actual - 77°F) x (0.003V/°F)) or

V corrected = V25°C - ((T actual - 25°C) x (0.0055V/°C))

Each charger shall provide the proper voltage for the 58 cell 125 volt battery, with a rated float voltage of 2.17 – 2.25 volts per cell at 77°F.  Each charger shall be provided with a remote (for mounting on the battery) sensor, complete with 50 feet of insulated jacket shielded cable per sensor. The sensor will be connected by the customer to the negative post of a middle cell, using the intercell terminal connection bolt, washer, and straps provided by the battery manufacturer.  A type of sensor using an adhesive for attachment/mounting to the battery is NOT acceptable.

Use/non-use of the temperature compensation circuit shall be customer selectable (IN or OUT), by a switch, jumper, or software equivalent.

j.	Meters:  DC ammeter and DC voltmeter (either analog or digital display types) shall be accurate within one percent of full scale.

k.	Terminal blocks:  Terminal blocks for external wiring to the alarm relay contacts and the alarm timer shall be rated with at least 600 volt insulation and 5 amperes.  The blocks shall be molded-block barrier type and accommodate ring lugs for #16 AWG wire.

Arrangement and location of the blocks shall be such that incoming and outgoing cables can be supported and all wiring to the blocks shall be completely accessible without having to remove other devices for accessibility.

6.	SUPERVISORY CONTROLS/CHARGER ALARMS: The following supervisory controls/alarms, or their equivalents, shall be integrated into each battery charger circuitry, as described in NEMA PE-7, and as additionally required herein.

a. 	Charger Failure Alarm (a.k.a., Rectifier Failure Alarm): Isolated form "C" contacts shall be provided to indicate a battery charger failure, such as tripped circuit breaker, overvoltage shutdown, and no output voltage.

b. 	Low DC Voltage Alarm:  Isolated form "C" contacts for alarm indication when DC output voltage falls below a (customer adjustable) preset level.  The minimum voltage adjustment range for pickup and dropout shall be 98.6 to 127.6 volts.

c. 	High DC Output Voltage Alarm Relay:  Isolated form "C" contacts for alarm indication when DC output voltage rises above a (customer adjustable) preset level. The minimum voltage adjustment range for pickup and dropout shall be 127.6 to 145 volts.

d.	AC Power Failure Alarm:  Isolated form "C" contacts for alarm indication in case of low AC input voltage or interrupted AC input.

e.	Low Direct-Current Alarm:  This alarm is not required, but if this alarm is provided, it shall be capable of being blocked (or not used) by the Customer.

f. 	Indicator Lamps/LEDs:  Each alarm shall also activate individual long-life indicator lamps/LEDs to indicate alarm condition. Light emitting diodes (LEDs), neon lamps, long life incandescent lamps, and microprocessor system LCD displays are examples of acceptable forms of indicating lamps.

7.	MECHANICAL DESIGN REQUIREMENTS: The battery charger shall be designed for Ventilation Class 1 (i.e., natural convection cooling, without fans).  Adequate ventilation openings shall be provided to allow mounting the charger back up to 6 inches from a wall and with both sides against other equipment.

The cabinet shall be constructed to facilitate floor mounting and fastening the back to a wall (for stability).  The charger can not be mounted on a wall, as the walls of the eventual site locations are not rated for the load.  If a rack-mounted charger is offered, and/or the charger cabinet is less than 36-inches high, the manufacturer shall provide a rack frame or suitable stand to support the charger.

Entry shall be from the bottom via raised access flooring or sides via conduit knockouts (both entry locations are preferred, bottom access is required) .  Conduit knockouts shall provide a minimum 1.5-inch inside diameter in the appropriate conduit fittings, and accommodate the sizes and numbers of incoming and outgoing cables.  Cutouts and removable cover plates (or gland plates) or conduit knockouts shall be provided at cable entry points.  A ground lug/pad shall be provided for bonding the charger to the building ground mat, via a customer provided #4 AWG copper cable.

8. 	PAINT: The battery charger cabinet shall be finished, inside and outside, by the manufacturers' standard painting system. The charger exterior shall be painted with ANSI 61 - light gray semigloss enamel  (or the manufacturer’s standard ANSI 61 finish).

9. 	AUDIBLE NOISE: The charger shall be operated under all conditions of line voltages, output voltage, and load current to determine the conditions which produce the highest audible sound level.  This highest audible noise level of a single charger (excluding ambient noise) shall be less than 65 dB (+/- 2 dB meter accuracy) at a distance of five feet from any/all charger surface(s), over the frequency range of 32 to 10,000 Hz (i.e., “C weighting curve”).  The contribution of the charger shall be extracted from the total noise (ambient plus charger) using:

Lchgr = 10 log (10(total level/10) - 10(Level with chgr off/10))

[ e.g. for total level = 70 dB and level with charger off = 65 dB,

Lchgr = 10 log (10(70/10) - 10(65/10))

Lchgr = 10 log (10(7) - 10(6.5)) = 68.35 dB  ]

10.	INPUT, OUTPUT, AND RADIO FREQUENCY NOISE:  The conducted and radiated electromagnetic interference (EMI) and other electrical noise products of individual chargers shall conform to NEMA PE-5.

11.	TESTING:  The equipment to be furnished on this contract shall have met all of the requirements of the design and production tests described in NEMA PE-5.  Test reports documenting the results of these tests shall be included in the final documentation (i.e., instruction manuals.)

12.	DOCUMENTATION:  The drawings and data required under this purchase order include form, fit, and function data, and manuals, instructional material, and other drawings and data needed by the Customer for the installation, operation, and routine maintenance.  These drawings and data are included in the term “instruction manual.”

All documents, including typical and contract-specific drawings and data shall be pre-punched and inserted into standard letter-sized 3-ring binders or equivalent binding.

The review and final documentation shall include:

-	charger specifications and ratings (which verify all technical requirements)

-	charger cabinet details; (dimensions, weight, component arrangements, external cable entry details and structural details)

-	installation instructions

-	circuit description

-	schematic diagrams

-	logic diagrams

-	wiring diagrams; (suitable for trouble shooting by Customer field personnel and to allow for installation of field wiring, i.e., AC and DC wiring, alarms)

-	operating instructions

-	trouble shooting guide

-	replacement and replaceable parts list, with prices guaranteed for 1 year from delivery of the associated charger(s).

a.	Review documentation: The contractor shall provide two sets of drawings and instruction books, one to each of the following addresses for review and comment within 30 days from date of contract award.

The information will be used to verify compliance with the requirements of this solicitation and resulting contract(s) and verify adequacy for operations and maintenance personnel, and to ensure that the Customer’s designs utilizing this charger are adequate (AC power sources, handling/installing weights, cabinet dimensions, etc.).

b.	Final documentation (Instruction books and drawings):

Four sets of final instruction manuals and included drawings shall be shipped with the equipment.

c.	Addresses for shipment of review documentation and correspondence:

Post Office Box Address:

Western Area Power Administration		Western Area Power Administration

ATTN:  Max Morse  A7910			ATTN:  Neil Messer  G5636

P. O. Box 281213					P.O. Box 6457

Lakewood, CO  80228-8213			Phoenix, AZ  85005-6457

or to:

Street Address:

Western Area Power Administration		Western Area Power Administration

ATTN:  A7910  Max Morse			ATTN:  Neil Messer  G5636

12155 W. Alameda Parkway			615 S. 43rd Avenue

Lakewood, CO  80228-2802			Phoenix, AZ 85009-

13.	WARRANTY:  Each charger shall be warranted to be free of defect in workmanship and material for at least one year from the date of delivery, or the manufacturer's warranty period, whichever is longer.

14.	SPARE PARTS:  The contractor shall furnish a list, with prices guaranteed for one year after the delivery of the battery charger, of the spare parts provided, and of any other replaceable parts not included as spare parts.  All spare parts provided shall be pre-tested for correct operation prior to shipment.

The contractor shall also furnish spare parts.  The spare parts to be provided at time of equipment delivery, under Item 002 of this contract shall include the following:

a.	One spare logic card or electronic module of each type furnished.  This is to include control modules, alarm boards/modules, and alarm/shutdown boards/modules.

b.	Two spare discrete silicon controlled rectifiers or one spare rectifier module of each type used.

c.	Two spare discrete diodes or two spare diode modules of each type used.

d.	One spare equalize/high rate timer (unless included in another spare module).

e.	Three spare fuses of each type and rating used.

f.	Three spare LED's or lamps of each type and color used (unless included in another spare module).

g.	One spare filter capacitor of each type and rating used.

h.	One alarm relay board/module of each type used.

i.	One spare alarm relay of each type used (unless included in “h” above).

j.	Two spares of each resistor or capacitor not included as part of a circuit board or module.

k.	Two spare remote temperature compensation sensors.

15.	DELIVERY REQUIREMENTS:   Delivery of the chargers, spare parts, and final instruction manuals is required required no sooner than November 4, 2002 and no later than November 28, 2002.  Items shall be delivered “F.O.B. Destination” prepaid (the contractor's cost of shipping shall be included in the quoted price) to:

Western Area Power Administration, Lone Butte Substation.  Lone Butte Substation is located south of Phoenix in Maricopa County, Arizona.  The substation is at the end of an approximately one-half mile-long dirt road, just south of the intersection of Queen Creek Road and Maricopa Road/State Highway 347.  This area is approximately 2 miles west of Interstate 10.

The shipper is to contact Jack DeCenso at 602-352-2613 (Fax no. 602-352-2410) [alternate is David Radosevich at 602-352-2681 ], to verify the delivery site is ready for delivery, to refine the delivery destination directions, and to coordinate delivery at least seven days and again 24 hours prior to delivery.  The above destination may not always have someone on site and pre-arrangements are required.  Delivery shall be made between 8:00 a.m. and 2:30 p.m. Monday through Thursday, excluding Government holidays

Responsibility for risk of loss of or damage to supplies shall remain with the Contractor until, and shall pass to the Customer upon, delivery of the supplies to the destination. However, if supplies are rejected due to failure to conform to the contract requirements, the risk of loss or damage remains with the Contractor until cure or acceptance.  The Contractor shall NOT be liable for loss of or damage to supplies caused by the negligence of officers, agents, or employees of the Customer.

Preservation, packaging, and packing for shipment or mailing of all work deliverable shall be according to good commercial practice and adequate to insure acceptance by common carrier and safe transportation.  The contractor shall provide itemized packing lists that enumerate the specific contents of each shipping container with the equipment, as follows:

(a) One copy to accompany shipment

(b) One copy to each of:

Western Area Power Administration

ATTN:  Max Morse  A7910

P. O. Box 281213

Lakewood, CO  80228-8213

Western Area Power Administration

ATTN:  Jack DeCenso  G5624

P.O. Box 6457

Phoenix, AZ  85005-6547

*********Last page of the Technical Specifications*********