# Appendix A:  Utility Bill Analysis to Determine Electrical Energy Savings

Table A.1 presents the monthly electricity use in Fort Polk’s North and South Fort areas for the last 12 months of the pre-retrofit period and the first 12 months of the post-retrofit period. Also included are the monthly base-65°F heating and cooling degree days (HDD and CDD).

Table A.1.  Pre- and post-retrofit monthly electricity use and base-65°F heating and cooling degree days for North Fort and South Fort, Fort Polk

|  |  |  |  | Monthly electricity use (kWh) |
| --- | --- | --- | --- | --- |
|  | Month | HDD | CDD | South Fort | North Fort |
| Pre-retrofit | Mar-94 | 182 | 50 | 10,791,312 | 2,334,600 |
|  | Apr-94 | 66 | 155 | 11,711,616 | 2,323,650 |
|  | May-94 | 7 | 231 | 13,867,308 | 2,686,450 |
|  | Jun-94 | 0 | 450 | 16,129,008 | 3,325,700 |
|  | Jul-94 | 0 | 486 | 17,445,540 | 3,511,700 |
|  | Aug-94 | 0 | 451 | 17,338,440 | 3,518,200 |
|  | Sep-94 | 4 | 323 | 15,002,316 | 2,908,100 |
|  | Oct-94 | 57 | 165 | 12,693,408 | 2,454,750 |
|  | Nov-94 | 118 | 60 | 10,116,372 | 2,114,200 |
|  | Dec-94 | 346 | 13 | 10,521,756 | 2,241,150 |
|  | Jan-95 | 424 | 12 | 11,405,604 | 2,629,900 |
|  | Feb-95 | 276 | 7 | 9,874,032 | 2,252,550 |
| Post-retrofit | Sep-96 | 5 | 331 | 13,112,400 | 2,720,950 |
|  | Oct-96 | 41 | 147 | 10,815,084 | 2,240,500 |
|  | Nov-96 | 190 | 45 | 9,057,972 | 1,984,100 |
|  | Dec-96 | 311 | 21 | 9,313,584 | 2,013,200 |
|  | Jan-97 | 486 | 35 | 10,412,220 | 2,571,250 |
|  | Feb-97 | 321 | 23 | 8,923,068 | 2,146,850 |
|  | Mar-97 | 80 | 86 | 9,522,492 | 2,128,550 |
|  | Apr-97 | 86 | 48 | 9,299,304 | 2,011,800 |
|  | May-97 | 0 | 251 | 11,893,980 | 2,334,900 |
|  | Jun-97 | 0 | 401 | 13,884,024 | 3,033,450 |
|  | Jul-97 | 0 | 564 | 15,681,624 | 3,455,950 |
|  | Aug-97 | 0 | 511 | 15,210,300 | 3,389,450 |

To normalize electricity use to a typical year at the site, we fit the pre- and post-retrofit monthly electrical energy use for each area of the base to a function of heating and cooling degrees:

E (kWh) = a + h · HDD + c · CDD

Then, since a typical year at Fort Polk contains 1909 heating degree days and 2493 cooling degree days, the energy use in a typical year is 12 · a + 1909 · h + 2493 · c.

The regression equations are as follows:

Pre-retrofit

North Fort:	E = 1,712,029 + 1,829 · HDD + 3,766 · CDD

South Fort:	E = 9,177,092 + 3,638  · HDD + 17,223 · CDD

Post-retrofit

North Fort:	E = 1,636,307 + 1,457 · HDD + 3,322 · CDD

South Fort:	E = 8,376,563 + 2,249 · HDD + 13,475 · CDD

Substituting in the heating and cooling degree days for a typical year into each of the four equations in turn gives the results shown in Table A.2, which also provides estimated 95% confidence intervals for each of the parameters, obtained using a bootstrap technique (Davison 1997).

Table A.2.  Weather-normalized annual electricity use (million kWh)

|  | Pre-retrofit | Post-retrofit | Savings |
| --- | --- | --- | --- |
| North Fort | 33.4 ± 0.6 | 30.8 ± 0.6 | 2.7 ± 0.9 |
| South Fort | 160.0 ± 3.4 | 138.4 ± 2.0 | 21.6 ± 3.9 |
| Total | 193.4 ± 3.4 | 169.2 ± 2.1 | 24.3 ± 4.0 |

Statistical analyses of the regression equations are presented in tables A.3 through A.6.

Table A.3.  Regression analysis of pre-retrofit monthly energy use in North Fort

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | 1,712,029 | 92,196 | 18.6 | 1.75E–08 |
| HDD | 1,829 | 324 | 5.7 | 3.12E–04 |
| CDD | 3,766 | 263 | 14.3 | 1.67E–07 |
| R-squared: |  | 0.9713 |  |  |
| Adjusted r-squared: | 0.965 |  |  |

Table A.4.  Regression analysis of pre-retrofit monthly energy use in South Fort

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | 9,177,092 | 500,022 | 18.4 | 1.93E–08 |
| HDD | 3,638 | 1,755 | 2.1 | 6.81E–02 |
| CDD | 17,223 | 1,424 | 12.1 | 7.21E–07 |
| R-squared: |  | 0.9722 |  |  |
| Adjusted r-squared: | 0.9660 |  |  |

Table A.5.  Regression analysis of post-retrofit monthly energy use in North Fort

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | 1,636,307 | 75,746 | 21.6 | 4.60E–09 |
| HDD | 1,457 | 258 | 5.7 | 3.12E–04 |
| CDD | 3,322 | 210 | 15.8 | 7.23E–08 |
| R-squared: |  | 0.9716 |  |  |
| Adjusted r-squared: | 0.9653 |  |  |

Table A.6.  Regression analysis of post-retrofit monthly energy use in South Fort

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | 8,376,563 | 246,991 | 33.9 | 8.31E–11 |
| HDD | 2,249 | 840 | 2.7 | 2.53E–02 |
| CDD | 13,475 | 686 | 19.6 | 1.07E–08 |
| R-squared: |  | 0.9859 |  |  |
| Adjusted r-squared: | 0.9828 |  |  |

# Appendix B:  Utility Bill Analysis to Determine 
Electricity Demand Savings

As one might expect, patterns of peak electrical demand were much more difficult to understand than patterns of monthly electricity use. To get a better idea of what was happening, we used all 18 months of available pre-retrofit data and 24 months of post-retrofit data, instead of just one year pre- and post-retrofit as we did with the energy use data.

The reason is that in the pre-retrofit period, billed peak demand in both areas of Fort Polk depended on the season: For the most part, peak monthly demand in November through February was a function of the monthly low temperature, while in March through October peak monthly demand was a function of the monthly high temperature. However, because family housing made up 67% of the pre-retrofit electricity load in North Fort (compared with only 37% in South Fort), the supplemental resistance heating on the pre-retrofit heat pumps caused North Fort to have more winter-peaking months than the South Fort. For example, in March 1994 demand in North Fort seemed to follow the pattern for a winter month, while demand in South Fort followed the pattern of a summer month. In February of 1995, North Fort also followed the winter pattern while South Fort followed the summer pattern.

With only three or four heating months, one year’s data was insufficient to develop meaningful regressions. Thus Table B.1 presents the monthly billed peak demand in Fort Polk’s North Fort and South Fort areas for the last 18 months of the pre-retrofit period, and Table B.2 presents the peak demands for the first 24 months of post-retrofit period. The tables include monthly high and low temperatures, and indicate for each month whether the demand followed the winter or summer pattern. This data was used to estimate demand savings.

Figure B.1 plots monthly peak demand for the South Fort, pre- and post-retrofit. In the pre-retrofit period, peak demand was a linear function of monthly high temperature during summer months and a linear function of monthly low temperature in the winter months. In the post-retrofit period, monthly peak demand is strictly a function of the monthly high temperature. Clearly, the winter peaking was caused by electric supplemental heating on the pre-retrofit heat pumps. Once the heat pumps were replaced with GHPs (which have no supplemental heat) the winter peak disappeared.

Figure B.2 plots pre- and post-retrofit monthly billed peak demand for North Fort. With smaller electricity loads in this area the data shows more scatter than that of the South Fort, but the pattern is still clear. Note that the August 1993 peak demand of 9740 kW is an outlier.

Table B.1.  Pre-retrofit monthly billed peak demand and monthly high and low temperatures

|  | Temperature (°F) | South Fort | North Fort |
| --- | --- | --- | --- |
| Month | High | Low | Peak demand (kW) | Season | Peak demand (kW) | Season |
| Jun-93 | 96 | 58 | 30,072 | Summer | 5,920 | Summer |
| Jul-93 | 99 | 71 | 32,424 | Summer | 5,760 | Summer |
| Aug-93 | 101 | 72 | 33,399 | Summer | 9,740 | Summer |
| Sep-93 | 99 | 51 | 31,786 | Summer | 6,820 | Summer |
| Oct-93 | 89 | 30 | 26,107 | Summer | 5,040 | Summer |
| Nov-93 | 84 | 29 | 19,421 | Winter | 5,240 | Winter |
| Dec-93 | 75 | 28 | 20,496 | Winter | 5,200 | Winter |
| Jan-94 | 72 | 21 | 25,133 | Winter | 7,900 | Winter |
| Feb-94 | 78 | 24 | 23,923 | Winter | 7,020 | Winter |
| Mar-94 | 83 | 32 | 21,034 | Summer | 6,020 | Winter |
| Apr-94 | 87 | 36 | 25,805 | Summer | 5,240 | Summer |
| May-94 | 87 | 53 | 26,813 | Summer | 6,160 | Summer |
| Jun-94 | 94 | 66 | 30,778 | Summer | 6,920 | Summer |
| Jul-94 | 94 | 63 | 31,752 | Summer | 6,600 | Summer |
| Aug-94 | 93 | 63 | 30,576 | Summer | 6,700 | Summer |
| Sep-94 | 93 | 48 | 29,602 | Summer | 6,160 | Summer |
| Oct-94 | 91 | 43 | 26,712 | Summer | 5,160 | Summer |
| Nov-94 | 84 | 44 | 21,538 | Summer | 4,700 | Summer |
| Dec-94 | 78 | 29 | 21,336 | Winter | 5,520 | Winter |
| Jan-95 | 76 | 25 | 23,285 | Winter | 6,660 | Winter |
| Feb-95 | 78 | 30 | 22,075 | Summer | 6,600 | Winter |

Table B.2.  Post-retrofit monthly billed peak demand and monthly high and low temperatures

|  | Temperature (°F) | South Fort | North Fort |
| --- | --- | --- | --- |
| Month | High | Low | Peak demand (kW) | Season | Peak demand (kW) | Season |
| Oct-96 | 86 | 39 | 20,899 | Summer | 4,540 | Summer |
| Nov-96 | 82 | 32 | 19,891 | Summer | 4,400 | Summer |
| Dec-96 | 79 | 19 | 17,808 | Summer | 4,500 | Summer |
| Jan-97 | 79 | 23 | 18,379 | Summer | 5,520 | Summer |
| Feb-97 | 81 | 32 | 17,775 | Summer | 4,440 | Summer |
| Mar-97 | 86 | 43 | 17,069 | Summer | 4,000 | Summer |
| Apr-97 | 88 | 39 | 20,227 | Summer | 4,160 | Summer |
| May-97 | 90 | 52 | 24,159 | Summer | 4,460 | Summer |
| Jun-97 | 93 | 59 | 25,872 | Summer | 5,900 | Summer |
| Jul-97 | 97 | 68 | 26,981 | Summer | 6,140 | Summer |
| Aug-97 | 97 | 63 | 27,048 | Summer | 6,260 | Summer |
| Sep-97 | 95 | 59 | 25,267 | Summer | 5,940 | Summer |
| Oct-97 | 90 | 39 | 23,285 | Summer | 5,260 | Summer |
| Nov-97 | 77 | 30 | 15,994 | Summer | 4,100 | Summer |
| Dec-97 | 73 | 28 | 16,968 | Summer | 4,320 | Summer |
| Jan-98 | 73 | 30 | 16,699 | Summer | 4,360 | Summer |
| Feb-98 | 73 | 34 | 16,263 | Summer | 4,160 | Summer |
| Mar-98 | 81 | 28 | 17,103 | Summer | 4,400 | Summer |
| Apr-98 | 82 | 43 | 19,522 | Summer | 4,080 | Summer |
| May-98 | 99 | 57 | 24,763 | Summer | 4,800 | Summer |
| Jun-98 | 99 | 59 | 27,351 | Summer | 6,520 | Summer |
| Jul-98 | 104 | 72 | 27,485 | Summer | 6,600 | Summer |
| Aug-98 | 104 | 70 | 27,519 | Summer | 6,560 | Summer |
| Sep-98 | 97 | 70 | 27,048 | Summer | 6,000 | Summer |

Figure B.2.  North Fort billed monthly peak demand. Pre-retrofit demand had winter and summer peaks, while post-retrofit peak demand is always a function of monthly high temperature.

To estimate peak demand savings in a typical year, we began by correlating monthly billed peak demand with monthly low temperature for pre-retrofit winter months, and with monthly high temperature for pre-retrofit summer months and all post-retrofit months. The outlier in Figure B.2 was omitted because, even if this was not a billing error, omitting the outlier leads to a conservative estimate of peak demand savings, and there is no plausible justification for attributing the value to pre-retrofit housing as opposed to a one-month mission-related anomaly. The regression equations are the following.

Pre-retrofit

North Fort summer demand (kW) = 	100.5 · Tmax  –  3333.4	(B.1a)

North Fort winter demand (kW) = 	–193.4 · Tmin  +  11,541	(B.1b)

South Fort summer demand (kW) =	592.2 · Tmax  –  25,976	(B.2a)

South Fort winter demand (kW) = 	–644.9 · Tmin  +  39,032	(B.2b)

Post-retrofit

North Fort demand (kW) = 	75.6 · Tmax  –  1571.4	(B.3)

South Fort demand (kW) = 	417.1 · Tmax  –  14,829	(B.4)

In a typical year at Fort Polk, the annual low temperature is 19.9°F, and the annual high is 100.9°F. Equations (B.1a) and (B.1b) show that in the pre-retrofit period, the peak demand for North Fort would occur in the winter, at 7692 kW compared with 6807 kW in the summer. However, the overall pre-retrofit peak would occur in the summer when, according to Eq. (B.2a), the demand in the South Fort is 33,777 kW. Combined with the 6807 kW in North Fort, annual peak demand in a typical year would be 40,584 kW.

The post-retrofit peak demand in the North Fort in a typical year is 6057 kW, and peak demand in South Fort is 27,256 kW, for a combined peak of 33,313 kW. The demand savings for a typical year is then 40,584 – 33,313 = 7271 kW.

To estimate the uncertainty in the estimate of demand savings, we used a bootstrap technique (Davison 1997). A 95% confidence interval for the demand savings is 7.3 ± 3.1 MW.

Statistical analyses of Eqs. (B.1) through (B.4) are presented in tables B.3 through B.8.

Table B.3.  Regression analysis of North Fort pre-retrofit cooling peak demand

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | –3333.4 | 3624.1 | –0.92 | 0.3793 |
| Tmax | 100.52 | 39.27 | 2.56 | 2.84E–02 |
| R-squared |  | 0.3958 |  |  |
| Adjusted r-squared | 0.3354 |  |  |

Table B-4.  Regression analysis of North Fort pre-retrofit heating peak demand

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | 11,541.3 | 1,991.3 | 5.80 | 0.0012 |
| Tmax | –193.44 | 72.52 | –2.67 | 3.72E–02 |
| R-squared |  | 0.5425 |  |  |
| Adjusted r-squared | 0.4663 |  |  |

Table B.5.  Regression analysis of South Fort pre-retrofit cooling peak demand

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | –25,976.2 | 5,297.6 | –4.90 | 0.0003 |
| Tmax | 592.19 | 57.95 | 10.22 | 1.40E–07 |
| R-squared |  | 0.8893 |  |  |
| Adjusted r-squared | 0.8808 |  |  |

Table B.6.  Regression analysis of South Fort pre-retrofit heating peak demand

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | 39,032.2 | 2,852.1 | 13.69 | 0.0002 |
| Tmax | –644.87 | 109.00 | –5.92 | 4.09E–03 |
| R-squared |  | 0.8974 |  |  |
| Adjusted r-squared | 0.8718 |  |  |

Table B.7.  Regression analysis of North Fort post-retrofit peak demand

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | –1571.4 | 1072.8 | –1.46 | 0.1571 |
| Tmax | 75.57 | 12.20 | 6.20 | 3.09E–06 |
| R-squared |  | 0.6357 |  |  |
| Adjusted r-squared | 0.6192 |  |  |

Table B.8.  Regression analysis of  South Fort post-retrofit peak demand

|  | Coefficients | Std Error | t Stat | P-value |
| --- | --- | --- | --- | --- |
| Intercept | –14,828.9 | 2,858.4 | –5.19 | 3.35E–05 |
| Tmax | 417.11 | 32.49 | 12.84 | 1.08E–11 |
| R-squared |  | 0.8822 |  |  |
| Adjusted r-squared | 0.8769 |  |  |

# Appendix C:  
Analysis to Determine Persistence of Savings

The energy conservation measures installed in 1995 – 1996 had a definite impact on electricity use and demand at Fort Polk, shown clearly in Figures 2 and 3 of the body of the report. But starting in about August of 2000, total Fort Polk electricity use began a steady rise, and by June 2003 the weather-normalized annual consumption was about half way back to the where it was before the conservation measures were installed. What happened? Was there a take-back effect in family housing, or did this increase take place in the non-housing areas of Fort Polk?

At Fort Polk, electricity is supplied to family housing through 16 separate electrical feeders. Each feeder contains a submeter that the Army reads manually once per month to track family housing electricity use. We obtained these manual readings for the same period for which we obtained Fort Polk’s utility bills, June 1993 to June 2003. Figure C-1 presents the sum of these monthly meter readings for the 16 feeders. As with electricity use for the entire facility, the raw data is not very informative. There seems to be a drop in electricity use around the time the energy conservation measures were installed, but the scatter in the data makes the reduction difficult to quantify.

Figure C-1.   Monthly sums of readings from the 16 electric submeters in the family housing areas of Fort Polk.

Figure C-2, which takes data from the 12 months ending with the graphed months and normalizes the data to a TMY, makes it much clearer what has happened, at least initially. Annual electricity use in family housing fell from about 77-79 million kWh per year before the retrofits to about 51-53 million kWh per year afterwards. It remained at this level for several years, but between September 1999 and July 2000, energy use suddenly dropped by 21%, then increased by about 41% over the next 14 months (this trough is visible in Figure C-1 as well).

Figure C-2.  Annual electricity use in Fort Polk family housing. The bars represent weather-normalized kWh for the 12-month period ending with the graphed month.

One factor that could have changed energy use in family housing is demolition of housing units:  Between September 1998 and August 2002, a total of 362 older residences were demolished, leaving only 3641 of the original 4003 units. About 10.4% of the original square footage of housing was demolished, leaving 89.7%. But in Figure C-3 we overlay the percentage of remaining housing square footage on the weather-normalized manual meter readings. Obviously, demolition of housing units does not account for what the data are showing. For this reason, we believe the manual readings from the family housing meters are unreliable.

In our original study of the Fort Polk retrofit project, we attached data loggers to 14 of the 16 family housing electric submeters in order to read them electronically at 15-minute intervals. In July 2003, we were able to rehabilitate 11 of our original 14 data loggers and began collecting electric use data once again. To date the results have been mixed. For example, Figure C-4 presents daily electricity use vs. daily average temperature on

Figure C-3.  Weather-normalized total of manually read submeters in family housing, and percentage of original housing units remaining. Each bar represents kWh for the 12-month period ending with the graphed month.

Figure C-4.  Daily electricity use vs. daily average temperature for submetered Feeder 5, 1996-1997 and 2003-2004. Either this meter was not working correctly in 2003 – 2004, or the feeder serves a different set of loads than it did in 1996 – 1997.

Feeder 5 from our original data collection effort from 1996 to 1997, along with the more recent data. In 1996-1997, the data had the expected pattern for electricity use in all-electric housing —  more energy was used at the extreme temperatures in both summer (for cooling) and in winter (for heating). But in the later data, the pattern seems to be inverted — less energy is used as outdoor air temperatures become more extreme. Either this meter is no longer functioning properly, or the electricity use is no longer limited to housing.

Another example is presented in Figure C-5, which plots daily energy use vs. daily average temperature for Feeder 14. Here at least the more recent data corresponds to what we expect for a housing load, but the number of housing units served by this feeder seems to have increased drastically. In 1996-1997, baseline energy use (i.e., the portion unaffected by heating and cooling) was about 1800 kWh per day, whereas in 2003-2004 it has increased to 5300 kWh per day. This is nearly a 300% increase, and clearly much greater than one would expect from an increase in electric appliances.

Figure C-5.  Daily energy use on Feeder 14 increased after 1996-1997 by nearly 300% according to data gathered in 2003-2004, but this increase is certainly due to an increase of housing units being served by the feeder.

Altogether, of the eleven feeders we rehabilitated in 2003, data from seven are so different from the 1996-1997 data as to be unusable. On the other hand, data from four of the eleven feeders (Feeders 3, 4, 6, and 16) were very similar to the 1996-1997 data, as can be seen in Figure C-6. Coincidentally, there were no demolitions on these feeders, so their energy use is directly comparable.

Figure C-6.  Electricity use on four submetered feeders to Fort Polk family housing appears to have changed very little, based on comparison of 1996-1997 and 2003 – 2004 data sets.

We cannot be certain why the manual readings from the family housing meters and the 15-minute-interval data from 7 of 11 data loggers would be unreliable. However, we have a theory that explains what we see in the data. Our theory, suggested by Figure C-2, is that electrical distribution system circuits were switched in September 1999 and again in July 2000, creating a period between these dates when housing submeters did not capture all of the housing loads; and that after July 2000 large non-housing loads were being served through the housing submeters. It is also possible that some of the housing submeters are no longer functioning properly, especially since they are maintained by the Army and not the utility. This theory would also explain why the use of manual readings from the housing submeters as part of the M&V procedures for the actual ESPC project was abandoned a few years into the project.

For each of the four feeders with usable data, we fit daily electricity use data from 1996-1997 and 2003-2004 to a five-parameter function of daily average temperature using the technique described in our 1998 evaluation of the Fort Polk project (Hughes and Shonder 1998). This regression analysis allowed us to predict annual energy use for a typical year. If there have been no increases in energy use, then the TMY predictions from the two data sets should be roughly the same. Table C-1 shows the results of the regression analysis of 1996-1997 and 2003-2004 electricity use data for the four feeders.

Table C-1.  Annual electricity use predicted for a TMY by regression analysis of 1996-1997 and 2003-2004 electricity use data for four submetered Fort Polk family housing feeders.

| Feeder | TMY energy use based on 1996-1997 data (kWh) | TMY energy use based on 2003-2004 data (kWh) | Percentage change |
| --- | --- | --- | --- |
| 3 | 977,428 | 882,651 | –9.7% |
| 4 | 176,601 | 166,838 | –5.5% |
| 6 | 999,035 | 1,037,816 | 3.9% |
| 16 | 4,763,891 | 4,982,995 | 4.6% |
| Total | 6,916,955 | 7,070,300 | 2.2% |

The analysis indicates that energy use on some of the feeders has decreased, and on some it has increased. Some of the changes are undoubtedly due to changes in occupancy, for which we have no information. Overall, energy use for the four feeders has increased by 2.2% over 7 years. This is an annual rate of increase of just 0.3%.

Based on this analysis of a large sample of Fort Polk’s housing, we conclude that there have been only small increases in electricity use in Fort Polk’s family housing since the retrofits were installed. The 0.3% annual increase is smaller than housing load growth predicted in the 1998 evaluation based on national averages at the time, for plug load growth. Since in ESPC projects the ESCO is not accountable for plug load growth, it follows that the ESPC energy savings have persisted.

# Appendix D:  
Utility Bill Analysis to Determine Electrical Cost Savings

In Appendix A we derived equations that predict pre- and post-retrofit electrical use in the North and South Fort areas of Fort Polk given base-65°F heating and cooling degree days. Subtracting the post-retrofit electrical use from the pre-retrofit electrical use gives electrical savings as a function of heating and cooling degree days:

North Fort

Monthly savings (kWh) = 75,722 + 372 · HDD + 444 · CDD	(D.1)

South Fort

Monthly savings (kWh) = 800,529 + 1,389 · HDD + 3,748 · CDD	(D.2)

Likewise, from Appendix B we can derive equations for monthly peak demand savings as a function of monthly high and low temperatures:

North Fort

Summer demand savings (kW) = 24.96 · Tmax – 1,761.9	(D.3a)

Winter demand savings (kW) = –75.57 · Tmax – 193.44 · Tmin + 13,113	(D.3b)

South Fort

Summer demand savings (kW) = 175.08 · Tmax – 11,147	(D.4a)

Winter demand savings (kW) = – 417.11 · Tmax  – 644.87 · Tmin + 53,861	(D.4b)

Given these equations we can predict the demand and energy savings in any given month knowing the base-65°F heating and cooling degree days that occurred, and the monthly high and low temperature. This provides a way of determining how much Fort Polk would have paid for electricity had the project not been implemented. For each month in the post-retrofit period, we estimate the energy and demand savings using equations (D.1) through (D.4). Adding the estimated energy savings to the actual billed energy use gives an estimate of what the energy use would have been without the project. Likewise adding the estimated demand savings to the actual billed peak demand gives an estimate of what demand would have been without the project. Then given energy use and demand without the project, we use the same rate schedule to estimate what the electric bill would have been in that month.

## Electricity Rates

In the period from June 1993 to June 2003, Fort Polk’s serving electric utility has charged four different rates. These rates had two different structures. The LGS rate structures in effect through October 2001 included declining block rates for both demand and energy. Consider for example the LGS-15 rate in effect through June 1995. For demand, the first block of 60 kW was billed at $4.83 per kW, and the remaining demand was billed at $3.00 per kW. For energy, the first block of 30,000 kWh was billed at 0.0436 per kWh, the second block (up to 400 times the monthly peak demand) was billed at $0.0341 per kWh, and the remainder at $0.0249 per kWh. The LGS-16 and LGS-17 rates were similar, with slightly lower rates in all blocks.

In November 2001 Fort Polk was switched to the Small General Service Rate (GS-1S), which is a declining block rate for energy only. First, there is a customer charge of $9.89 per month. The first block of energy — sized at 1575 kWh plus 55 times the peak demand — is billed at $0.0918 per kWh; the second block, up to 24,500 kWh, is billed at $0.0476 per kWh. The charge for the remaining energy depends on the season. From November through April, the rate is $0.0288 per kWh, and from May through October the rate is $0.0335 per kWh.

Table D.1 presents the rates Fort Polk has paid and the periods during which these rates were in effect. In addition to the rates, Fort Polk’s electricity bill depended on a number of riders as well. For example, according to the utility’s Rider G, energy and demand charges are discounted by 5% in the South Fort bill because service is delivered at a primary line voltage higher than 13,800 volts, and Fort Polk owns and maintains all of the service transformers. Beginning in June 1996, a “Formula Rate Plan” took effect, which provides a per-kWh discount that varies from month to month.

Table D.1.  Fort Polk Utility Rates

| Rate | Effective date | 1st demand charge, per kW | 2nd demand charge, per kW | 1st energy charge, per kWh | 2nd energy charge, per kWh | 3rd energy charge, per kWh |
| --- | --- | --- | --- | --- | --- | --- |
| LGS-15 | June-93 | $4.83 | $3.00 | $.0436 | $.0341 | $.0250 |
| LGS-16 | Jul-95 | $4.68 | $2.92 | $.0442 | $.0330 | $.0240 |
| LGS-17 | Oct-95 | $4.62 | $2.87 | $.0417 | $.0326 | $.0239 |
| GS-1S | Nov-04 | none | none | $.0918 | $.0475 | $.0288/$.0335 |

Interestingly, a high portion of Fort Polk’s electricity bill depends not on the particular rate charged, but on the Fuel Cost Realignment rider. This is a per-kWh charge applied monthly that is intended to recover the utility’s fuel costs. Over the 121 months of records available, the fuel adjustment charge ranged from $0.0125 to $0.0540 per kWh. On average over this period, fuel adjustment costs accounted for 45% of the total bills.

## An Example

During the month of September 1996 — the first month after completion of the energy conservation retrofits — peak demand in the South Fort was 25,301 kW, with 13,112,400 kWh consumed. Fort Polk was paying the LGS-17 rate at the time. Table D.2 shows a breakdown of the bill for that month.

Table D.1.  Breakdown of Fort Polk utility bill for September 1996

| Charge | Calculation | Value |
| --- | --- | --- |
| First demand charge | $4.62 ( 60 | $ 277.20 |
| Second demand charge | $2.87 ( (25,301 – 60) | $ 72,441.67 |
| First energy charge | $0.0417(30,000 | $ 1,251.00 |
| Second energy charge | $0.0326 ( (400 ( 25,301 – 30,000) | $ 328,947.04 |
| Third energy charge | $0.0239 ( (13,112,400 – 400 ( 25,301) | $ 71,508.80 |
| Subtotal, energy and demand |  | $ 474,425.71 |
| Primary voltage discount | –0.05 ( subtotal | $ (23,721.29) |
| Fuel adjustment cost | $0.02493 ( 13,112,400 | $ 326,892.13 |
| Formula rate reduction | –$0.0001234 ( 13,112,400 | $ (16,179.52) |
| Total |  | $ 761,417.04 |

Now, from weather records we find that the month of September 1996 had 5 heating degree days and 331 cooling degree days, and the high temperature for the month was 91.4°F. From equation (C.2), the energy savings during this month is estimated as

800,529 + (1,389)(5) + (3,748)(331) = 2,048,062 kWh .

Given that the actual electrical use for the month was 13,112,400 kWh, we can estimate that if the project had not been installed, the electrical use would have been 13,112,400 + 2,048,062 = 15,160,462 kWh.

From Eq. (D.4a) the demand savings during the month is estimated as

(175.08)(91.4) – 11,147 = 4,855 kW .

So given that the actual peak demand was 25,301 kW, we can estimate that had the energy conservation measures not been installed the peak demand for this month would have been 25,301 + 4855 = 30,156 kW.

Now we use the same rates to calculate what the electrical bill would have been with a peak demand of 30,156 kW and an electrical use of 15,160,462 kWh. The calculations are summarized in Table D.3.

Table D.2.  Calculated Fort Polk electricity cost for September 1996 without savings

| First demand charge | $4.62 ( 60 | $ 277.20 |
| --- | --- | --- |
| Second demand charge | $2.87 ( (30,156 - 60) | $ 86,375.52 |
| First energy charge | $0.0417 ( 30,000 | $ 1,251.00 |
| Second energy charge | $0.0326 ( (400 ( 30,156 – 30,000) | $ 392,256.24 |
| Third energy charge | $0.0239 ( (15,160,462 - 400 ( 30,156) | $ 74,043.68 |
| Subtotal, energy and demand |  | $ 554,203.64 |
| Primary voltage discount | –0.05 ( subtotal | $ (27,710.18) |
| Fuel adjustment cost | $0.02493 ( 15,160,462 | $ 377,950.32 |
| Formula rate reduction | –$.0001234 ( 15,160,462 | $ (18,706.65) |
| Total |  | $ 885,737.13 |

Now given the results of Table D.2 and D.3, we define the energy savings in September 1996 to be $885,737.13 – $761,417.04 = $124,320.09.

# Text boxes

Figure B.1.  South Fort billed monthly peak demand, pre- and post-retrofit. Before the retrofit, there are winter and summer peaks, whereas post-retrofit peak demand is always a function of monthly high temperature.