## Site Data
Facility Name |  | Street Address |  | City |  | State |  | Zipcode
MN Hospital |  | 1234 W. Main St |  | Milwakee |  | WI
Facility Type |  | SIC |  | Classification
Commercial
Contact |  | Title |  | E-Mail Address |  | Phone Number |  | Fax Number |  | Industrial
Commercial
Institutional
| Electricity |  |  | Fuels
| Energy | Peak Demand | % of Total Cost from Peak Demand Charges | Cost* | Gas |  | Fuel Oil | #2 | #2
[5 empty] | Energy | Cost* | Energy | Cost | #6 | Electric Sell Back Desired | No
| kWh | kW |  | $ | Therms | $ | Gallons | $ |  | Peak Electric Rates Apply | Yes
2003-01-01 | 640495 | 1079 | 34.9% | 31682 | 54340 | 41434 |  |  |  | Standby Demand Charge | 1.5 | $/kw/month
2003-02-01 | 580107 | 1076 | 37.31% | 29567 | 45840 | 34953 |  |  |  | Electric Sell Back Price | 1.5 | ¢/kWh
2003-03-01 | 650700 | 1199 | 36.95% | 33223 | 44290 | 33768 |  |  |  | Cogen Fuel Cost | 4 | $/MMBTU
2003-04-01 | 648328 | 1155 | 36.35% | 32718 | 31540 | 24045 |  |  |  | W/O Cogen Fuel Cost | 6.4001 | $/MMBTU
2002-05-01 | 716199 | 1311 | 36.77% | 36522 | 25220 | 11144 |  |  |  | Existing Boiler Efficiency | 80 | %
2002-06-01 | 743382 | 1385 | 37.25% | 38165 | 25950 | 11465
2002-07-01 | 794868 | 1429 | 36.58% | 40059 | 28980 | 12803
2002-08-01 | 794062 | 1435 | 36.42% | 40516 | 31020 | 13705
2002-09-01 | 722532 | 1329 | 37.34% | 36461 | 23030 | 10176
2002-10-01 | 691080 | 1249 | 36.52% | 35103 | 26700 | 11797
2002-11-01 | 636733 | 1228 | 38.37% | 32895 | 34330 | 26179
2002-12-01 | 640442 | 1087 | 35.45% | 31425 | 50040 | 38153
* Excludes Taxes | 8258928 | 1246.8333 | 36.68% | 418336 | 421280 | 269622
Yes
[9 empty] | No |  |  | 1
Step 1: Enter Site Data
Enter Information in Yellow Fields!

## Baseline Report
Baseline Report for | MN Hospital
|  | 0 | Electricity |  |  | Fuels
|  | 0 | Energy | Peak Demand | Cost* | Gas | 0 | Fuel Oil | #2
|  | 0 |  |  |  | Energy | Cost* | Energy | Cost
|  | 0 | kWh | kW | $ | Therms | $ | Gallons | $
|  | 2003-01-01 | 640495 | 1079 | 31682 | 54340 | 41434 | N/A | N/A
|  | 2003-02-01 | 580107 | 1076 | 29567 | 45840 | 34953 | N/A | N/A
|  | 2003-03-01 | 650700 | 1199 | 33223 | 44290 | 33768 | N/A | N/A
|  | 2003-04-01 | 648328 | 1155 | 32718 | 31540 | 24045 | N/A | N/A
|  | 2002-05-01 | 716199 | 1311 | 36522 | 25220 | 11144 | N/A | N/A
|  | 2002-06-01 | 743382 | 1385 | 38165 | 25950 | 11465 | N/A | N/A
|  | 2002-07-01 | 794868 | 1429 | 40059 | 28980 | 12803 | N/A | N/A
|  | 2002-08-01 | 794062 | 1435 | 40516 | 31020 | 13705 | N/A | N/A
|  | 2002-09-01 | 722532 | 1329 | 36461 | 23030 | 10176 | N/A | N/A
|  | 2002-10-01 | 691080 | 1249 | 35103 | 26700 | 11797 | N/A | N/A
|  | 2002-11-01 | 636733 | 1228 | 32895 | 34330 | 26179 | N/A | N/A
|  | 2002-12-01 | 640442 | 1087 | 31425 | 50040 | 38153 | N/A | N/A
|  | * Excludes Taxes |  |  | 0.36683 | 418336 | 421280 | 269622 | 0

## Equipment
Thermal-to-Electric Ratio | = | 1.0818 |  | 1 | 1=Commercial, 2=Institttional, 6000=Industrial
0.5
Recommended Prime Mover(s) |  |  |  | 714.5
Gas Engine | Recommended
Microturbine |  |  |  | Estimated Hours of Operation | Electric Generators |  | Absorption Chillers |  | Desiccant
Gas Turbine (Simple Cycle) | Recommended |  |  |  | 3200 | Hours/Year | 846 | Hours/Year | 846 | Hours/Year
Phosphoric Acid Fuel Cells
Select Prime Mover |  | Gas Engine | [6 empty] | Paraitic Electric Use
Would backup generation have been installed anyway? |  | Yes |  | Costs |  |  | Estimated* | Known | Estimated* | Known |  | Total kWh/Year
If "Yes", indicated planned size |  | 1200 | kWe | Generator | 1200 | per kWe | 1380000 |  | 0 |  | kWe | 0 | kWh
Recommended Generation |  | 714.5 | kWe | Heat Recovery Unit* |  |  | Included |  | Included |  | kWe | 0 | kWh
Chose Size (per Unit) |  | 750 | kWe | Absorption Chiller | 850 | per RT | 279834.1765 |  | 11.7413 |  | kWe | 9933.1348 | kWh
Chose Number of Units |  | 2 | Unit(s) | Desiccant | 5.5 | per SCFM | 0 |  | 8 |  | kWe | 6768 | kWh
Total Selected Capacity |  | 1500 | kWe | Installation* |  |  | Included
Electric Efficiency |  | 35 | % | Other | [6 empty] | kWe | 0 | kWh
Gross Heat Rate Exhaust (LHV) |  | 6336.5714 | BTU/kWhe | Total |  |  | 1659834.1765 |  | 19.7413 |  | kWe | 16701.1348 | kWh
Recoverable Heat Rate (LHV) |  | 4435.6 | BTU/kWhe
O&M Costs |  | 0.008 | $/kWh/yr | * Estimated Costs includes heat recovery unit and installation costs.
Electric Use |  | 0 | kWe/kWe
375
Include Absorption Chiller |  | Yes
Will the Absorption ChillerDisplace an Electric Chiller? |  | Yes
Size |  | 391.3765 | RT
Thermal Input |  | 6653.4 | MBTU/hr
O&M Costs |  | 30 | $/RT/yr
Electric Use |  | 0.03 | kWe/RT
Electric Displaced |  | 0.6 | kWe/RT
Select Desiccant |  | Solid
Would a desicant have been installed anyway? |  | Yes
Chose Size (per Unit) |  | 10000 | SCFM | Total Electric Displaced by Non-Electric Chillers
Chose Number of Units |  | 1 | Unit(s) | 249.8259 |  | kWe | 211352.6965 | kWh
Total Selected Capacity |  | 10000 | SCFM
Regeneration Requirements (200°F) |  | 450000 | BTU/hr
O&M Costs |  | 0.075 | ¢/SCFM/yr
Latent Heat Removal Rate |  | 300000 | BTU/hr
Electric Use |  | 0.8 | kWe per kSCFM
|  | None | Yes
|  | Solid | No
Liquid
|  | 450000 | Solid & Com or Inst
|  | 0 | Solid & Indus
|  | 0 | Liquid & Com or Inst
|  | 0 | Liquid & Ind
Step 3: Enter CHP Equipment Info
Enter Information in Yellow Fields!

## RESULTS
SITE
MN Hospital |  |  |  | RESULTS
1234 W. Main St
Milwakee |  | WI
ASSUMPTIONS |  |  |  | CHP RESULTS
Average Electric Cost |  | 5.0653 | ¢/kWh | Prime Mover
Peak Averge Electric Cost |  | 6.9233 | ¢/kWh | Total ECP Cost | 1659.8342 | $(1000)
Initial Electric Sell Back |  | 1.5 | ¢/kWh | Prime Mover | Gas Engine
Supplemental Elect Cost |  | 5.0653 | ¢/kWh | Parasitic Load | 19.7413 | kW
Cogen Initial Fuel Cost |  | 4 | $/MMBTU | Total Generation Capacity | 1500 | kW
W/O Cogen Fuel Cost |  | 6.4001 | $/MMBTU | Electrical Output | 4800 | MWh
Existing Boiler Efficiency |  | 80 | % | Absorption Chiller Credit | 211.3527 | MWh
Standby Demand Charge |  | 1.5 | $/kw/month | Net Total Generation Effect | 5011.3527 | MWh
Standby Capacity Required |  | 750 | kW | Elecectric Capacity Factor | 36.5297 | %
O&M Charge |  | 12529.6941 | $/yr | Gross Heat Rate (LHV) | 9750.8571 | BTU/kWh
Annual Electric Load |  | 8258.928 | MWh | Recoverable Heat | 4435.6 | BTU/kWh
Annual Heat Load |  | 30492.6476 | MMBTU | Thermal Loads
TAT Thermal Loads (June, July, August)
PURPA | (Assuming Gas or Liquid Fuel Fired) |  |  | Absorption Chiller | 5628.7764 | MMBTU
Efficiency |  | 57.7447 | % | Desiccant | 380.7 | MMBTU
Qualified Facility |  | Yes |  | Total Thermal Load with TAT | 36502.124 | MMBTU
Sell Back |  | 0 | kWh | Thermal Capacity Factor | 100 | %
Sell Back Desired |  | No |  | Thermal Energy Output
|  |  |  | From Generator | 21290.88 | MMBTU
FINANCIAL RESULTS |  |  |  | From Auxiliary Boiler | 9201.7676 | MMBTU
COSTS WITHOUT COGENERATION $(1000) |  |  |  | Fuel Requirements:
Electricity Costs |  |  | 418.336 | For Generator (HHV) | 51730.8632 | MMBTU
Thermal Energy Costs |  |  | 269.622 | For Auxiliary Boiler (HHV) | 12712.9684 | MMBTU
|  | TOTAL | 687.958
COSTS WITH COGENERATION $(1000) |  |  |  | Generation Costs | 4.3109 | ¢/kWh
Supplemental Electric Purchase |  |  | 164.4981
Peak Electric Charge Adjustment |  |  | -153.4584
Fuel |  |  | 257.7753
Electricity Sold |  |  | 0
O&M |  |  | 12.5297
Standby Charges |  |  | 13.5
|  | TOTAL | 294.8447
| SAVINGS | 393.1133
| SIMPLE PAYBACK | 4.2223 | Years

## Graphs
1
Full Page Graphs

## SUPPORTING INFORMATION
1
STOP! ONLY SUPPORTING INFORMATION FOLLOWS

## Baseline
BASELINE

## Energy Consumption & Costs
|  | Electricity |  |  |  | Fuels | [7 empty] | Thermal Load
|  | Energy | Peak Demand | Average Demand | Cost | Gas |  |  |  | Fuel Oil |  |  | #2 | Energy | Average Demand | Average Demand
[6 empty] | Energy | Average Demand | Average Demand | Cost | Energy | Average Demand | Average Demand | Cost
Month | Hour/Month | kWh | kW | kW | $ | Therms | BTU/h | kW | $ | Gallons | BTU | kW | $ | BTU | BTU/h | kW
2003-01-01 | 744 | 640495 | 1079 | 860.8804 | 31682 | 54340 | 7303763.4409 | 2140.1088 | 41434 | 0 | 0 | 0 | 0 | 3933180952.381 | 5286533.5381 | 1549.0312
2003-02-01 | 672 | 580107 | 1076 | 863.2545 | 29567 | 45840 | 6821428.5714 | 1998.7777 | 34953 | 0 | 0 | 0 | 0 | 3317942857.1429 | 4937414.966 | 1446.7343
2003-03-01 | 744 | 650700 | 1199 | 874.5968 | 33223 | 44290 | 5952956.9892 | 1744.3029 | 33768 | 0 | 0 | 0 | 0 | 3205752380.9524 | 4308806.9636 | 1262.5431
2003-04-01 | 720 | 648328 | 1155 | 900.4556 | 32718 | 31540 | 4380555.5556 | 1283.5664 | 24045 | 0 | 0 | 0 | 0 | 2282895238.0952 | 3170687.8307 | 929.0576
2002-05-01 | 744 | 716199 | 1311 | 962.6331 | 36522 | 25220 | 3389784.9462 | 993.2563 | 11144 | 0 | 0 | 0 | 0 | 1825447619.0476 | 2453558.6278 | 718.9283
2002-06-01 | 720 | 743382 | 1385 | 1032.475 | 38165 | 25950 | 3604166.6667 | 1056.0732 | 11465 | 0 | 0 | 0 | 0 | 1878285714.2857 | 2608730.1587 | 764.3959
2002-07-01 | 744 | 794868 | 1429 | 1068.371 | 40059 | 28980 | 3895161.2903 | 1141.3389 | 12803 | 0 | 0 | 0 | 0 | 2097600000 | 2819354.8387 | 826.1119
2002-08-01 | 744 | 794062 | 1435 | 1067.2876 | 40516 | 31020 | 4169354.8387 | 1221.6816 | 13705 | 0 | 0 | 0 | 0 | 2245257142.8571 | 3017818.7404 | 884.2648
2002-09-01 | 720 | 722532 | 1329 | 1003.5167 | 36461 | 23030 | 3198611.1111 | 937.2395 | 10176 | 0 | 0 | 0 | 0 | 1666933333.3333 | 2315185.1852 | 678.3829
2002-10-01 | 744 | 691080 | 1249 | 928.871 | 35103 | 26700 | 3588709.6774 | 1051.5441 | 11797 | 0 | 0 | 0 | 0 | 1932571428.5714 | 2597542.2427 | 761.1176
2002-11-01 | 720 | 636733 | 1228 | 884.3514 | 32895 | 34330 | 4768055.5556 | 1397.1096 | 26179 | 0 | 0 | 0 | 0 | 2484838095.2381 | 3451164.0212 | 1011.2412
2002-12-01 | 744 | 640442 | 1087 | 860.8091 | 31425 | 50040 | 6725806.4516 | 1970.759 | 38153 | 0 | 0 | 0 | 0 | 3621942857.1429 | 4868202.765 | 1426.4542
Total | 8760 | 8258928 | N/A | N/A | 418336 | 421280 | N/A | N/A | 269622 |  |  |  |  | 30492647619.0476 | N/A | N/A
Average | 730 | 688244 | 1246.8333 | 942.2918 | 34861.3333 | 35106.6667 | 4816529.5912 | 1411.3132 | 22468.5 | 0 |  |  | 0 | 2541053968.254 | 3486249.9898 | 1021.5219
Maximum |  | 794868 | 1435 | 1068.371 | 40516 | 54340 | 7303763.4409 | 2140.1088 | 41434 | 0 |  |  | 0 | 3933180952.381 | 5286533.5381 | 1549.0312
#2
Estimated Hours of Operation |  | Electric Generators |  | Absorption Chillers | [8 empty] | #6
|  | 3200 | Hours/Year | 846 | Hours/Year

## Electric Load Profile
|  | Electric |  |  |  | kWe @ |  | Hours > System Capacity | Demand Follow Capability
|  | Energy | Peak Demand | Average Demand | Cumulative | 2191.7808 | Hours
Month | Hour/Month | kWh | kW | kW | Hours | 849.1285 |  | 0 | Peak kW | Avg kW
Maxium |  |  | 1435 | 1068.371 | 0 |  |  | 714.5 | 1435 | 1068.371
2002-07-01 | 1902-01-13 | 794868 | 1429 | 1068.371 | 744 | N/A | 0 | 714.5 | 1429 | 1068.371
2002-08-01 | 1902-01-13 | 794062 | 1435 | 1067.2876 | 1488 | N/A | 0 | 714.5 | 1435 | 1067.2876
2002-06-01 | 1901-12-20 | 743382 | 1385 | 1032.475 | 2208 | 849.1285 | 0 | 714.5 | 1385 | 1032.475
2002-09-01 | 1901-12-20 | 722532 | 1329 | 1003.5167 | 2928 | N/A | 0 | 714.5 | 1329 | 1003.5167
2002-05-01 | 1902-01-13 | 716199 | 1311 | 962.6331 | 3672 | N/A | 0 | 714.5 | 1311 | 962.6331
2002-10-01 | 1902-01-13 | 691080 | 1249 | 928.871 | 4416 | N/A | 0 | 714.5 | 1249 | 928.871
2003-04-01 | 1901-12-20 | 648328 | 1155 | 900.4556 | 5136 | N/A | 0 | 714.5 | 1155 | 900.4556
2002-11-01 | 1901-12-20 | 636733 | 1228 | 884.3514 | 5856 | N/A | 0 | 714.5 | 1228 | 884.3514
2003-03-01 | 1902-01-13 | 650700 | 1199 | 874.5968 | 6600 | N/A | 0 | 714.5 | 1199 | 874.5968
2003-02-01 | 1901-11-02 | 580107 | 1076 | 863.2545 | 7272 | N/A | 0 | 714.5 | 1076 | 863.2545
2003-01-01 | 1902-01-13 | 640495 | 1079 | 860.8804 | 8016 | N/A | 0 | 714.5 | 1079 | 860.8804
2002-12-01 | 1902-01-13 | 640442 | 1087 | 860.8091 | 8760 | N/A | 0 | 714.5 | 1087 | 860.8091
Minimum |  |  | 1076 | 860.8091 |  | N/A | 0 | 714.5
Total | 8760 | 8258928 |  | 942.2918

## Total Thermal Profile
Total Thermal Use
|  | Average Demand | Average Demand | Cumulative
Month | Hour/Month | BTU/h | kWt | Hours
|  | 3933180952.381 | 1549.0312 | 0
2003-01-01 | 744 | 3933180952.381 | 1549.0312 | 744 | 744
2003-02-01 | 672 | 3317942857.1429 | 1446.7343 | 1416 | 1416
2002-12-01 | 744 | 3621942857.1429 | 1426.4542 | 2160 | 2160
2003-03-01 | 744 | 3205752380.9524 | 1262.5431 | 2904 | 2904
2002-11-01 | 720 | 2484838095.2381 | 1011.2412 | 3624 | 3624
2003-04-01 | 720 | 2282895238.0952 | 929.0576 | 4344 | 4344
2002-08-01 | 744 | 2245257142.8571 | 884.2648 | 5088 | 5088
2002-07-01 | 744 | 2097600000 | 826.1119 | 5832 | 5832
2002-06-01 | 720 | 1878285714.2857 | 764.3959 | 6552 | 6552
2002-10-01 | 744 | 1932571428.5714 | 761.1176 | 7296 | 7296
2002-05-01 | 744 | 1825447619.0476 | 718.9283 | 8040 | 8040
2002-09-01 | 720 | 1666933333.3333 | 678.3829 | 8760 | 8760
|  | 1666933333.3333 | 678.3829 | 8760
Total | 8760 | 30492647619.0476

## CHP
CHP

## CHP Electric Load Profile
|  | Electric |  |  |  | kWe @ |  | Hours > System Capacity
|  | Energy | Peak Demand | Average Demand | Cumulative | 3200 | Hours
Month | Hour/Month | kWh | kW | kW | Hours | 988.57 |  | 2222.5084
|  |  |  | 1993.0196 | 0
2002-07-01 | 744 | 1482806.5753 | 573.2 | 1993.0196 | 744 | N/A | 744
2002-08-01 | 744 | 1482000.5753 | 579.2 | 1991.9363 | 1488 | N/A | 1488
2002-06-01 | 720 | 1087351.2877 | 529.2 | 1510.2101 | 2208 | N/A | 2208
2002-09-01 | 720 | 722532 | 1329 | 1003.5167 | 2928 | N/A | 2222.5084
2002-05-01 | 744 | 716199 | 1311 | 962.6331 | 3672 | 988.57 | 0
2002-10-01 | 744 | 691080 | 1249 | 928.871 | 4416 | N/A | 0
2003-04-01 | 720 | 648328 | 1155 | 900.4556 | 5136 | N/A | 0
2002-11-01 | 720 | 636733 | 1228 | 884.3514 | 5856 | N/A | 0
2003-03-01 | 744 | 650700 | 1199 | 874.5968 | 6600 | N/A | 0
2003-02-01 | 672 | 580107 | 1076 | 863.2545 | 7272 | N/A | 0
2003-01-01 | 744 | 640495 | 1079 | 860.8804 | 8016 | N/A | 0
2002-12-01 | 744 | 640442 | 1087 | 860.8091 | 8760 | N/A | 0
|  |  |  | 860.8091 | 9132 | N/A | 0
Total | 8760 | 8258928 |  | 1136.2112

## Generation Capability
|  | Electric Generation Electricity (Estimated) |  |  |  | Electric Generation Thermal (Estimated)
|  | Generated Energy | Average Power | Actual Energy | Electric Sold | Energy | Average Output | Cumulative
Month | Hour/Month | kWhe | kWe | kWhe | kWhe | kWht | kWt | Hours | Electric Capacity Factor
|  |  | 547.9452 |  |  |  | 712.1618 | 0 | 36.53% | No Sell Back
2003-01-01 | 744 | 407671.2329 | 547.9452 | 1482806.5753 | 0 | 529848.371 | 712.1618 | 372
2003-02-01 | 672 | 368219.1781 | 547.9452 | 1482000.5753 | 0 | 478572.7222 | 712.1618 | 1080 | 0
2003-03-01 | 744 | 407671.2329 | 547.9452 | 1087351.2877 | 0 | 529848.371 | 712.1618 | 1788
2002-05-01 | 744 | 407671.2329 | 547.9452 | 716199 | 0 | 529848.371 | 712.1618 | 2532
2002-07-01 | 744 | 407671.2329 | 547.9452 | 648328 | 0 | 529848.371 | 712.1618 | 3276 | PURPA
2002-08-01 | 744 | 407671.2329 | 547.9452 | 636733 | 0 | 529848.371 | 712.1618 | 4020 | (Assuming Gas or Liquid Fuel Fired)
2002-12-01 | 744 | 407671.2329 | 547.9452 | 640442 | 0 | 529848.371 | 712.1618 | 4764 | Efficiency |  | 57.7447 | %
2002-10-01 | 744 | 407671.2329 | 547.9452 | 580107 | 0 | 529848.371 | 712.1618 | 5508 | Qualified Facility |  | Yes
2003-04-01 | 720 | 394520.5479 | 547.9452 | 722532 | 0 | 512756.4881 | 712.1618 | 6240 | Sell Back |  | 0 | kWh | Yes
2002-06-01 | 720 | 394520.5479 | 547.9452 | 691080 | 0 | 512756.4881 | 712.1618 | 6960 | Sell Back Desired |  | No |  | No
2002-09-01 | 720 | 394520.5479 | 547.9452 | 650700 | 0 | 512756.4881 | 712.1618 | 7680 |  |  |  |  | No
2002-11-01 | 720 | 394520.5479 | 547.9452 | 640495 | 0 | 512756.4881 | 712.1618 | 8400
|  |  | 547.9452 |  |  |  | 712.1618 | 8760
Total | 8760 | 4800000 |  | 9978774.4384 | 0 | 6238537.2714 | 712.1618
Average | 730 | 400000 | 547.9452 |  | 0 | 519878.106 | 712.1618

## Thermal Profile inc TAT
Total Thermal Use
|  | Including TAT Load | Average Demand | Cumulative |  | Hours > System Capacity
Month | Hour/Month | BTU | kWt | Hours |  | 8760
|  | 5768543542.8571 |  | 0
2002-08-01 | 744 | 5768543542.8571 | 2271.8644 | 372 | 0 | Thermal Capacity Factor
2002-07-01 | 744 | 5620886400 | 2213.7116 | 1116 | 0
2002-06-01 | 720 | 5287917714.2857 | 2151.9955 | 1848 | 0 | 100%
2003-01-01 | 744 | 3933180952.381 | 1549.0312 | 2580 | 2111.6348
2003-02-01 | 672 | 3317942857.1429 | 1446.7343 | 3288 | 3288
2002-12-01 | 744 | 3621942857.1429 | 1426.4542 | 3996 | 3996
2003-03-01 | 744 | 3205752380.9524 | 1262.5431 | 4740 | 4740
2002-11-01 | 720 | 2484838095.2381 | 1011.2412 | 5472 | 5472
2003-04-01 | 720 | 2282895238.0952 | 929.0576 | 6192 | 6192
2002-10-01 | 744 | 1932571428.5714 | 761.1176 | 6924 | 6924
2002-05-01 | 744 | 1825447619.0476 | 718.9283 | 7668 | 7668
2002-09-01 | 720 | 1666933333.3333 | 678.3829 | 8400 | 8400
|  | 1666933333.3333 | 678.3829 | 8760 | 8760
Total | 8760 | 40948852419.0476

## Equipment Factors
| Units | Gas Engine |  |  | Microturbine |  | Gas Turbine (Simple Cycle) |  | Phosphoric Acid Fuel Cells** | Phosphoric Acid Fuel Cells
Size Range | kWe | 70 | 300 | 500 | 30 | 500 | 500 | 1000 | 10 | 10
Efficiency | % (LHV) | 31% | 34% | 35% | 27% | 27% | 27% | 28% | 40% | 40%
Gross Heat Exhaust (LHV) | BTU/kWh | 7594.4516 | 6623.2941 | 6336.5714 | 9225.037 | 9225.037 | 9225.037 | 8773.7143 | 5118 | 5118
Estimated Recoverable CHP Heat | % | 55% | 65% | 70% | 60% | 65% | 55% | 60% | 55% | 55%
CHP Recoverable Heat (LHV) | BTU/kWh | 4176.9484 | 4305.1412 | 4435.6 | 5535.0222 | 5996.2741 | 5073.7704 | 5264.2286 | 2814.9 | 2814.9
Installed Cost With Heat Recovery* | $/kWe | 1800 | 1500 | 1200 | 2000 | 1700 | 1100 | 900 | 4500 | 5000
O&M Costs | $/kWh | 0.015 | 0.012 | 0.008 | 0.01 | 0.009 | 0.009 | 0.0055 | 0.015 | 0.015
Parasitic Electric Use | kWe/kWe
* Costs can vary significantly due to interconnection and other siting requirements.
** Phosphoric Acid Fuel Cells (PAFC) are being produced commercially for electric generation. Solid Acid (SO) Fuel Cells and Molten Carbonate (MC) may be future players in applications >200 kWe.
Credit for Planned Installed Backup | $/kWe | 350
Absorption Cooling - Single Affect, Indirect Fired
Refrigeration Tons | RT | 10 | 55 | 100 | 200 | 300 | 500 | 1000 | 2000
Installed Cost (1) | $/RT | 1650 | 1360 | 1075 | 990 | 850 | 680 | 620 | 500
O & M Costs | $/RT-yr | 80 | 55 | 30 | 40 | 30 | 20 | 20 | 20
Thermal Input | MBTU/hr-RT | 19 | 18 | 17 | 17 | 17 | 17 | 17 | 17
Electric Use | kWe/RT | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Electric Displaced | kWe/RT | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Engine Driven Chillers
Refrigeration Tons |  | 10 | 55 | 100 | 200 | 300 | 500 | 1000 | 2000
Installed Cost (1) | $/RT
O&M Costs | $/RT-yr
Thermal Input | MBTU/hr-RT
Electric Use | kWe/RT
Electric Displaced | kWe/RT
(1) Installed cost includes cooling tower, cooling tower pumps, and gas connection.
Credit for Displacced Electric Chillers | $/kWe | 135
Desiccants - Solid
Parameter | Units | Industrial |  |  |  | Commercial
Flow Rate | SCFM | 600 | 4500 | 20000 | 40000 | 2000 | 7000 | 12000
Installed Cost | $/SCFM | 20.4 | 9.2 | 5.6 | 4.4 | 7.5 | 5.5 | 4.3
O&M Costs | ¢/SCFM/yr | 0.255 | 0.12 | 0.075 | 0.06 | 0.09 | 0.075 | 0.06
Regeneration Requirements (200°F) | BTU/hr per SCFM | 55 | 55 | 55 | 55 | 45 | 45 | 45
Latent Heat Removal | BTU/hr per SCFM | 35 | 35 | 35 | 35 | 30 | 30 | 30
Electric Use | kWh per 1000 SCFM | 1.1 | 1.1 | 1.1 | 1.1 | 0.8 | 0.8 | 0.8
Desiccants - Liquid
Parameter | Units | Industrial |  |  | Commercial
Flow Rate | SCFM | 3000 | 7500 | 84000 | 10000 | 50000 | 84000
Installed Cost | $/SCFM | 18 | 9.775 | 5.04 | 6.9 | 5.625 | 4.95
O&M Costs | ¢/SCFM/yr | 0.375 | 0.2125 | 0.1125 | 0.15 | 0.125 | 0.1125
Regeneration Requirements (200°F) | BTU/hr per SCFM | 45 | 45 | 45 | 35 | 35 | 35
Latent Heat Removal | BTU/hr per SCFM | 30 | 30 | 30 | 30 | 30 | 30
Electric Use | kWh per 1000 SCFM | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3

## Rules of Thumb & Definitions
RULES OF THUMB
Absorption Chillers
Steam Requirements |  |  |  | COP
Single Effect | = | 18 lbm/h/RT (@ 15 psig) |  | 0.6
Double Effect | = | 11 lbm/h/RT (@125 psig) |  | 0.9
Triple Effect | = | 8 lbm/h/RT (@ 125 psig) |  | Not yet commercial
Average Electric Offset | = | 0.6 kWe/RT
Auxiliary Firing Rate: |  | Rate at which fuel is added to the exhaust of the prime mover to increase the thermal output to met the thermal demands of the facility (BTU/h)
Electrical output of the prime mover (kWe)
Capacity Factor: |  | Based on equipment output vs. capacity
Electric (> 70% Desirable) | = | Avg. kW output (for period) System kW capacity
Thermal (>80% Desirable) | = | Avg. BTU output (for period) System capacity in BTUs
Steam (>80% Desirable) | = | Avg. lbm/h output (for period) System capacity in lbm/h
Emissions (lbs/MWh) | NG Reciprocating Engines |  | Gas Turbines
Generating Size | 100 - 2,000 kWe |  | 1,000 - 50,000 kWe
NOx | 12 -7.6 |  | 4.5 - 3.0
CO | 7.8 - 5.0 |  | 1.2 - 0.8
VOM | 1.6 -1.0 |  | 0.030 - 0.020
CO2 | Unknown |  | 600
Heating Values of Fuels (Typical) |  | Units |  | LHV | HHV | LHV/HHV
Natural Gas |  | BTU/CF |  | 950 | 1050 | 0.90476
#2 Fuel Oil |  | BTU/Gallon |  | 130000 | 138300 | 0.93999
#6 Fuel Oil |  | BTU/Gallon |  | 143000 | 150500 | 0.95017
Propane |  | BTU/Gallon |  | 84650 | 92000 | 0.92011
Sewage/Landfill |  | BTU/CF |  | 350 | 380 | 0.92105
Coal - Bituminous |  | BTU/lbm |  | 13600 | 14100 | 0.96454
Gas Turbines
Steam Output (300 - 600 psig) |  | 5 to 6 lbm/h/kWe
Absorption Chiller (Single Effect) |  | 0.28 to 0.33 RT/kWe
Heat Recovery from Exhaust |  | Q = MFRe x Cp x (Te - Ts)
|  | Where: Q | = | Heat Recovered |  | BTU/h
|  | MFRe | = | Mass Flow Rate Exhaust Gas |  | lbm/h
|  | Cp | = | Heat Capacity | 0.25 | BTU/lbm-°F
|  | Te | = | Temperature of Exhaust |  | °F
|  | Ts | = | Temperature of Stack |  | °F
Gross Heat Rate | = | Fuel Input (LHV ) (BTU) Power Output (kWhe)
Heating Values:
Higher Heating Value (HHV) | = | Total energy from combustion process
Lower Heating Value (LHV) | = | Assumes heat of condensation cannot be recovered
LHV is used for majority of calculations.
Internal Rate of Return (IRR): |  | Determines the discount rate necessary for a zero net present value of the cash flow beginning with the negative cash in the zero year and extending through 10 years following the beginning of operation.
Load Factor: |  | Based on site load data
Electric | = | Avg. kW (for period) Peak kW (for period)
Thermal | = | Avg. BTUs (for period) Peak BTUs (for period)
Operational Hours Consideration:
Commercial/Institutional
Building Occupancy
9 Hours/Day | ~ | 2400 Hours/Year
Peak Demand | ~ | 3200 Hours/Year
Absorption Chillers
3 Months | ~ 850 Hours/Year
(Based on operating only during peak summer demand hours)
Industrial
2 Shifts | ~ | 4200 Hours/Year
3 Shifts | ~ | 6300 Hours/Year
Continuous | = | 8760 Hours/Year
PURPA Minimum Qualifying Facility (QF):
QF Efficiency | = | (kWe x 3412.8) + 1/2(Useful Thermal Energy)
Fuel Input (BTU/h in LHV)
| > | 42.5% or
45% if < 15% Thermal Recovery
Reciprocating Engines
Steam Output (15 - 30 psig) |  | 4 to 5 lbm/h/kWe
Absorption Chiller (Single Effect) |  | 0.22 to 0.28 RT/kWe
Recoverable Heat Rate: |  | Energy recovered from the thermal output from the prime mover that is used to provide the useful thermal output to meet the thermal demands of the facility (BTU/h)
Electrical output of the engine (kWe) (adjusted for availability)
Steam Rates (Industrial Steam Turbines) | = | lbm/h steam kWe out (power) | or | lbm steam kWhe out (energy)
Standby Charge: |  | Monthly charge in $/kWe by the local power company for the right to buy purchase capacity and energy on an as required basis to backup the prime mover for any unscheduled outages or scheduled maintenance.
Thermal Coincidence: |  | Recoverable heat that can provide useful thermal output
Total recoverable heat from the prime mover (adjusted for availability)
Thermal/Power Ratio | = | Avg. BTUs Avg. kW x 3412 BTUs/kW
Guidelines for Estimating Hours
Peak Energy: |  | 3382.244 | Hours/Year |  | 9a - 10p
Peak Demand: |  | 2343.0536 | Hours/Year |  | 9a - 6p
Summer Peak Energy: |  | 845.561 | Hours/Year |  | 9a - 10p
Summer Peak Demand: |  | 585.7634 | Hours/Year |  | 9a - 6p
2 Shifts: |  | 4165.4286 | Hours/Year |  | 16 Hours (Weekdays)
3 Shifts: |  | 6248.1429 | Hours/Year |  | 24 Hours (Weekdays)
Continous: |  | 8760 | Hours/Year |  | "24/7/365"

## Conversions
CONVERSIONS
Electrical to Thermal
Energy | 1 | kWh | = | 3412.8 | BTUs
| 1 | BTU | = | 778 | ft-lbs
Rate of Energy = Power | 1 | kW | = | 3412.8 | BTU/h
| 1 | hp | = | 2545 | BTU/h
Fuel Oil #2 | 1 | Gallon | = | 130000 | BTUs | LHV
Fuel Oil #6 | 1 | Gallon | = | 143000 | BTUs | LHV
Heating Values - LHV/HHV
| Natural Gas |  | = | 0.90476
| #2 Fuel Oil |  | = | 0.93999
| #6 Fuel Oil |  | = | 0.95017
| Propane |  | = | 0.92
| Sewage/Landfill |  | = | 0.921
| Coal |  | = | 0.965 | Bituminous
Natural Gas | 1 | therm | = | 100000 | BTUs
Refrigeration Tons | 1 | RT | = | 12000 | BTUs/h
| 1 | RT-h | = | 12000 | BTUs
Steam to Thermal
Energy | 1 | lbm steam* | = | 1000 | BTUs
Rate of Energy = Power |  | lbm stm/h* | = | 1000 | BTU/h
* Use actual enthalpy values from steam tables at given pressure and temperature for more accuracy!