## ChillerData
Chiller Plant Measurement Criteria, Data Measurements, and Cost Results
Building Information1 | [5 empty] | Pre-ECP Measured2,3 | [13 empty] | Post-ECP Predicted Performance |  |  |  | Post-ECP Acceptance Measured | [19 empty] | Pre-ECP Financial Baseline |  |  | Predicted Financial |  |  |  |  | Year 1 - Post-ECP Yearly Reconciliation | [31 empty] | Year N - Post-ECP Yearly Reconciliation
[6 empty] | Condenser |  |  |  |  | Evaporator |  |  |  |  | Chiller |  | Verification | [5 empty] | Condenser |  |  |  |  | Evaporator | [7 empty] | Chiller |  |  |  |  | Verified | [9 empty] | Condenser |  |  |  |  | Evaporator | [7 empty] | Chiller | [12 empty] | Cost Reconciliation |  |  |  | Verified |  | Condenser |  |  |  |  | Evaporator | [7 empty] | Chiller |  |  |  |  | Cost Reconciliation |  |  |  | Verified
Bld ID | Loc | Name / # | Op Sched | Yearly Op Hrs | Nominal Capacity (tons) | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Heat Rejected (Btu/Hr) | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Capacity (tons) | Power (kW) | Efficiency @ 80% Load (kW/ton) | Date | By | Nominal Capacity (tons) | Guaranteed Capacity (tons) | Efficiency (kW/ton) | Guaranteed Efficiency (kW/ton) | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Heat Rejected (Btu/Hr) | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Capacity (tons) | Guaranteed Capacity (tons) | Capacity Difference (%) | Guaranteed Capacity Achieved (Yes/No) | Power (kW) | Efficiency (kW/ton) | Guaranteed Efficiency (kW/ton) | Efficiency Difference (%) | Guaranteed Efficiency Achieved (Yes/No) | Date | By | Elec Use (kWh) | Demand (kW) | Cost ($) | Elec Use (kWh) | Demand (kW) | Cost** ($) | Savings ($) | Guarantee ($) | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Heat Rejected (Btu/Hr) | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Capacity (tons) | Guaranteed Capacity (tons) | Capacity Difference (%) | Guaranteed Capacity Achieved (Yes/No) | Year 1 Energy Consumption (kWh) | Year 1 Guaranteed Consumption (kWh) | Year 1 Consumption Difference (%) | Guaranteed Energy Savings Achieved (Y/N) | Year 1 Billed Demand (kW) | Year 1 Guaranteed Demand (kWh) | Year 1 Demand Difference (%) | Guaranteed Demand Savings Achieved (Y/N) | Power (kW) | Efficiency (kW/ton) | Guaranteed Efficiency (kW/ton) | Efficiency Difference (%) | Guaranteed Efficiency Achieved (Yes/No) | Year 1 Cost** ($) | Year 1 Savings ($) | Year 1 Guarantee ($) | Year 1 Payment to ESCO ($) | Date | By | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Heat Rejected (Btu/Hr) | Temp Entering (F) | Temp Leaving (F) | Delta Temp (F) | Flow (gpm) | Capacity (tons) | Guaranteed Capacity (tons) | Capacity Difference (%) | Guaranteed Capacity Achieved (Yes/No) | Power (kW) | Efficiency (kW/ton) | Guaranteed Efficiency (kW/ton) | Efficiency Difference (%) | Guaranteed Efficiency Achieved (Yes/No) | Year N Cost** ($) | Year N Savings ($) | Year N Guarantee ($) | Year N Payment to ESCO ($) | Date | By
Totals |  |  |  |  | 0
1 For column definitions go to "DataColumnDef" worksheet.
2 Evaporator measurements are sufficent for determing the capacity and efficiency. Enter condenser measurements if measured.
3 Evaporator measurements may need to be repeated for multiple chillers.
Note on A7: Enter the building where the chiller is located.
Note on B7: Enter the chiller location in the building.
Note on C7: Enter the name of the chiller with other appropriate information

## OperatingScheds
Time Schedules
Sched # | Schedule Name | 0 0 | 0 1 | 0 2 | 0 3 | 0 4 | 0 5 | 0 6 | 0 7 | 0 8 | 0 9 | 1 0 | 1 1 | 1 2 | 1 3 | 1 4 | 1 5 | 1 6 | 1 7 | 1 8 | 1 9 | 2 0 | 2 1 | 2 2 | 2 3 | Total Hours | Peak Demand | Max Hrs / Yr
| Peak Demand Hours | [24 empty] | 3 | bar: 1 3 to 1 5
1 | 7 am - 7 pm, M-F 7 am - 12 pm Sat | [24 empty] | 11 | Yes | 3380 | bar: 0 7 to 1 7
2 | 24 Hours/Day All Year | [24 empty] | 24 | Yes | 8760 | bar: 0 0 to 2 3
3 | 12 am - 12 pm M-F | [24 empty] | 12 | No | 4380 | bar: 0 0 to 1 1
4 | 12 pm - 12 am M-F | [24 empty] | 12 | Yes | 4380 | bar: 1 2 to 2 3
5 | 6 am - 10 pm, M-F | [24 empty] | 15 | Yes | 3900 | bar: 0 6 to 2 0
Note on C2: Military Time

## AcceptRept
Acceptance Report Summary
The acceptance M&V check for the Chiller Plant ECP was performed on 4/23/03. The M&V requires that all chillers be measured at acceptance. The "ChillerData" worksheet lists the chillers that were tested and/or verified during acceptance in columns marked "Post-ECP Acceptance." All items in the "AcceptChecklist" were completed and two deficiencies were found. The capacity was low on two chillers due to undersized pumps. The pumps have been properly resized and guaranteed values have been achieved. Measurements taken during acceptance were recorded in the appropriate acceptance columns and the cost of the verifications and measurements was recorded in "MeasSpecs" spreadsheet. The Acceptance Report will contain all tabs (worksheets) in this workbook, updated with Post-ECP Acceptance Measured values.
The following table lists the individuals that performed the acceptance tests:
|  | Name | Title | Specialty
| 1 | William K. Donaldson | Engineer I | Metering/Surveys
| 2 | Jim A. Carlson | Engineer I | Metering/Surveys
| 3 | Carl K. Matheson | Technician | Metering/Surveys
|  | B. K. Wilson - Manager | Date

## AcceptChecklist
Chiller Plant Acceptance Checklist
Documents | Yes | No
Inspect design docs for complete set | x
Inspect docs for sequences / design conditions documentation | x
All equipment / users manuals in place | x
Vendor Certifications / Tests
Start-up tests (include results) | x
Performance tests (include results) | x
All OSHA requirements or local requirements met | x
All noise ordinances have been met | x
Performance Test Standards
Verify performance tests specification / all parameters specified complete | x
Overall condition
Verify the specified equipment is installed per manufacturers specifications | x
Construction, pipe hangers, other visual aspects correct | x
Check color coding and proper labeling on pipes | x
Check for proper paint priming and exterior coatings | x
Verify that access to all maintenance and inspection areas is within OSHA requirements or local requirements | x
Verify that hearing protection (ear plugs or ear covers) available | x
Water Treatment
Verify the specified equipment is installed per manufacturers specifications | x
Verify correct operational sequences | x
Input various conditions to simulate water treatment control sequences | x
All tests recorded (attach) | x
Controls
Verify the specified equipment is installed per manufacturers specifications | x
Verify and document correct installation of all sensors | x
Wiring must be installed per local code | x
Alarms functional | x
Input various conditions to simulate control sequences | x
Check temperature and flow controls | x
All tests recorded (attached) | x
Piping
Isolation valves correctly installed | x
Check operation of low water cutoff and pressure relief valves | x
Strainers installed correctly with pressure gauge across | x
Evaporator Entering temperature well installed | x
Evaporator Exiting temperature well installed | x
Condenser Entering temperature well installed | x
Condenser Exiting temperature well installed | x
15 pipe diameter long straight pipe for flow measurements installed on chilled water loop | x
15 pipe diameter long straight pipe for flow measurements installed on condenser water loop | x
Pumping
Check pump curve design / sequencing versus load calculations | x
Verify pump sequencing does not result in overload at low-loads | x
Accepted – USAF Date Certified By – “The ESCO” Date

## AnnualRept
Annual Report Year N
The annual reconciliation for the Chiller Plant ECP required that chillers be measured on an annual basis. The annual verification, and reconciliation can found in the Post-ECP Reconciliation Year 1 section of the "ChillerData" worksheet. After the inspection was conducted, all deficiencies were corrected. A summary of the calculated savings along with the savings guarantee is listed in the table below. The savings guarantees are also included in the table below. As a result of meeting the guaranteed savings, full payment with no deductions will be made. The Annual Report will contain all tabs (worksheets) in this workbook, updated with Post-ECP End of Year 1 Measured values.
Savings Summary
| Predicted Savings |  |  | 377017
| Guaranteed Savings |  |  | 339315
| Payment Deductions |  |  | 0
The following table lists the individuals that performed the annual reconciliation and verification inspections:
|  | Name | Title | Specialty
| 1 | Jim Johnson | Engineer I | Metering/Surveys
| 2 | Kim D. Anderson | Engineer I | Metering/Surveys
| 3 | Carl K. Matheson | Technician | Metering/Surveys
Accepted – USAF Date Certified By – “The ESCO” Date

## MeasSpecs
Measurement Specifications and Costs
Measurement |  |  |  |  | Instrument Used | [6 empty] | Comments
Date | Purpose | Cost $/Each | Type | By* | Accuracy | Type | Mfr | Model | Calibration
[9 empty] | Type** | Date | By***
Note: | Calibration Standard was included in Phase II Report
* | Initials of individual taking the measurements
** | Frequency of calibration was included in Phase II Report and is 1 year
*** | Initials of the individual responsible for calibrating the metering equipment.

## Tracking
M&V Contract Deliverables Tracking Form for Year 1 thru Year N
|  | ESCO Delivery |  | USAF Acceptance
Year | Reports | USAF Signature | USAF Date | USAF Signature | USAF Date
Acceptance
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
Year 7
Year 8
Year 9
Year 10
Year 11
Year 12
Year 13
Year 14
Year 15
Year 16
Year 17
Year 18
Year 19
Year 20
Year 21
Other Contract Specified Deliverables Required after Year 1 thru N

## DataColumnDef
Chiller Data Column Definitions
Column | Symbol | Definition / Equations
Bld ID |  | The Building Identification number designated by the base authority.
Loc |  | The Room Identification designated by the building authority.
Name / # |  | The name or number of the chiller if located among multiple chillers.
Op Sched |  | This is the number of the schedule listed in the "BuildingScheds" worksheet, corresponding to the hours the chiller is available for cooling.
Yearly Op Hrs | YOH | This is the number of hours the chiller is available for cooling.
Nominal Capacity (tons) | NC | The rated capacity of the chiller as stated by the manufacture.
Temp Entering (F) | Ti | Temperature of the water entering the Evaporator/Condenser.
Temp Leaving (F) | To | Temperature of the water leaving the Evaporator/Condenser.
Delta Temp (F) | DT | The difference between the Ti and To.
Flow (gpm) | Flow | Water Flow rate through the evaporator expressed in gallons per minute.
Heat Rejected (Btu/Hr) | HR | The total heat rejected to the condensing water.
Capacity (tons) | Cap | The amount of heat the chiller can absorb from the water in the evaporator expressed in tons.
Power (kW) | P | The power consumed by the chiller
Efficiency (kW/ton) | Eff | The calculated efficiency of the chiller determined using Power and Capacity. Eff = P / Cap
Guaranteed Capacity (tons) |  | The measured cooling capabilities of the chiller guaranteed by the ESCO. This number will be used for reconciliation.
Guarantee Efficiency (kW/ton) |  | The measured efficiency of the chiller guaranteed by the ESCO. This number is used for reconciliation.
Efficiency Difference (%) |  | The difference between the Measured Efficiency and the Guranteed Efficiency.
Elec Use (kWh) | EU | The total electric energy consumed for the year in question as a function of the Nominal Capacity, Efficiency and FLOP hours. EU = NC * Eff * YFH
Demand (kW) |  | The total Electric energy demand of the chiller.
Cost $ |  | This is the total cost of running the chiller for an entire year as a function of the Cost of Electricity (CE), Elec Use, Demand, and Cost of Demand (CD). Cost = CE*EU + Dmd*CD
Savings $ |  | This is the difference between the Pre-ECP cost and the Post-ECP estimated operating cost. This value may be adjusted by measured values obtained at Post ECP acceptance.
Guarantee $ |  | The annual guaranteed savings for this ECP based on expected Post-ECP Guaranteed performance.