# Notice items in RED – questions or incomplete or controversial

19march01:  	7.4.8 Peterson - cryo underground caverns

cooling specs for Beam Stop and RF Klystron Galleries

other environmental/contamination/water issues

Mokhov/Cossairt groundwater contamination calculation

### Conventional Construction and Facilities Stages 1 & 2

### Geology of the Fermilab Region

The many geologic studies for the Illinois proposal for the SSC [1,2] demonstrated that the region around Fermilab provided an almost ideal medium, Galena-Platteville dolomite,  for constructing the main tunnel (87 km circumference) and experimental facilities.  The only less-than-ideal feature was the depth of construction (approximately 400 feet below the surface) to reach this dolomite layer.  A subsequent geotechnical study for the Next Linear Collider Project [3] and generic site studies for future accelerator facilities at Fermilab[4] also reached the same conclusion.  However, due to its longer circumference (232 km), a VLHC might extend beyond the region of favorable geology.  There has been substantial experience in the Chicago area [5,6] in tunneling and underground caverns in hard rock strata, such as Silurian dolomite, Maquoketa shale, and Galena-Platteville dolomite.  There is a lack of corresponding local similar experience, or even knowledge of the mechanical/structural engineering properties of the softer strata such as Glacial drift, the Ancell layer,  the Middle Confining unit, or the Franconia formation.  These may be respectively characterized as clay, sandstone, and two strata of dolomitic sandstones.  At Fermilab, the Ancell, Middle Confining, and Franconia layers lie below the Galena-Platteville dolomite.

There is a  general sloping of the till, Silurian, Maquoketa, Galena-Platteville, Ancell, … sequence of layers from the West (higher elevation above mean sea level) to the East (lower elevation) to Lake Michigan.  However, to the Northwest and West of Fermilab are located the Troy and Rock Bedrock Valleys, where the hard rock Silurian, Maquoketa, and Galena-Platteville layers have been completely cut away by glaciers and filled to the underlying sandstones with Glacial drift.  The Sandwich Fault Zone lies to the Southwest of Fermilab, passing through Sandwich, Illinois, and running roughly NW to SE.  This fault zone does end approximately SSE of Fermilab.  To the Southwest of the Sandwich Fault Zone, the underlying Ancell and Middle Confining layers are upthrust to meet the Glacial drift at the bedrock surface, and even the Franconia layer can impact tunnels traversing the fault zone.

Figure 7.1:  General geologic features of Northeastern Illinois. (in prep – see included sketch)

If we restrict consideration to rings that would be contiguous to the existing Tevatron, only a VLHC ring with its center oriented to the North of Fermilab (North Ring) could be completely contained within the Galena-Platteville dolomite.  This ring would have a roughly North-South strike axis passing through Fermilab with a tilt of approximately 0.2 % grade to stay within the dolomite.  This ring would be bounded by Lake Michigan and the Wisconsin border.  Any ring with its center oriented farther to the West (even NNW) would be impacted by the bedrock valleys  Possible rings oriented to the South or West would traverse the Sandwich fault into softer strata, less ideal for tunneling.

Figure 7.2:  Schematic of the VLHC 232 km racetrack (R = 35 km, two 6 km straights).

In order to undertake a tunnel costing and feasibility study for various orientations of a VLHC ring, two layouts and vertical strata lampshades were prepared [7].  The simplest configuration is a  tilted (0.2% incline) North Ring which stays completely in Galena-Platteville dolomite.  The second is  a flat North Ring which transitions between the following hard rock media:  Maquoketa shale, Silurian dolomite, Maquoketa shale, Galena-Platteville dolomite, and back into Maquoketa shale.  The third is a tilted South Ring, which crosses the Sandwich Fault (only once) into the sandstone Ancell aquifer (wet) and the dolomitic sandstone Middle Confining unit and possibly the Franconia formation.  The surface plans and the vertical strata lampshades for these rings are illustrated in Figures 7.1, 7.2, 7.3, and 7.4.

Another design constraint of this costing exercise deals with the positioning and depth of the caverns for the two experimental halls.  It is desirable to have these located at the Fermilab site to be able to cluster the long straight sections (for injection/abort and interaction regions) and to utilize the Fermilab campus for the related experiment fabrication and staging buildings,  support utilities, and equipment shaft facilities.  This also helps to minimize off-site surface land requirements.

Structural features and thickness of the strata supporting the spans of the experimental halls or caverns [2] will determine the elevations at which the caverns can feasibly be sited.  This, of course, implies the elevation of the accelerator tunnel at the site of the cavern.  A general

Figure 7.3:  Lampshade diagram for North Ring orientation for flat and inclined tunnels.

rule of thumb is that there should be a depth of hard rock (dolomite) strata above the cavern at least equal to the span of the cavern.  The previous study has concluded that for 75 foot high chambers, roof spans up to 125 feet are feasible using standard methods of  roof arching and rock supports.  This assumed that the orientation axis of the cavern bisects the major joint sets.  The joints run approximately NE-SW x NW-SE so this criteria would be satisfied by VLHC ring orientations to the North, South, or West.  Possible options in elevation for the experimental caverns are depicted in Figure 7.5.

Table 7.1:  Elevation Parameters and strata fraction  for three tunnel models:

South Ring		North Ring		North Ring

0.08 % incline		     Flat			0.2 % incline

elevation at Fermilab (ft msl)	      510		     415			     244

depth at Fermilab (feet)	      235		     330			     501

average depth			      277		     371			     585

r.m.s. depth			        61		       99			     121

minimum depth		      118		     219			     342

maximum depth		      406		     603			     779

Strata (approx. %)

Silurian dolomite		       29 %		      27 %		        -

Maquoketa shale		       34 %		      27 %		        -

Galena-Platteville dolomite      21 %		      46 %		     100 %

Ancell – St. Peter sandstone       6 %		        -			        -

Middle Confining layer:	       10 %     		        -			        -

Prairie du Chien, Eminence-Postosi

dolomitic sandstones

Figure 7.4:  Lampshade diagram for South Ring orientation with inclined tunnel.

As a working hypothesis for this study, a time scale of 5 years is assumed for completion of the underground construction, including main tunnel, special tunnels, and all caverns and enclosures.  At this stage of the study, engineering design has not begun for any of these underground elements.

Figure 7.5:  Vertical siting of the experimental halls/caverns (and therefore VLHC).

Analogously to the 1997 study of  a 34 km VLHC booster tunnel with the Kenny Construction Company [8], we have entered into a tunnel costing exercise with CNA Consulting Engineers [9], to study the expected cost ranges and cost drivers of these three tunnel configurations listed above. By studying the three different tunnels,  we hope to learn the unit costs (per mile, per shaft, lined/unlined, etc.)  of a tunnel in an excellent media, that of a tunnel transitioning between three different hard rock media, and that of a tunnel which combines hard rock media, traversing the Sandwich Fault, and the softer sandstone and dolomitic sandstones, both within the aquifer, beyond. This data will allow optimizations and tradeoffs with respect to siting costs.  It is anticipated that the final tunnel cost estimating report will be available in mid-May, 2001.

  - Collider tunnel and enclosures

Since the largest volume of the underground construction is the main collider tunnel, we will first concentrate on that component.   A preliminary 12 foot clear diameter tunnel cross section is shown in Figure 7.6. However, a major purpose of this cost estimating study is to determine the sensitivity of cost to tunnel diameter.  The tunnel is envisioned to be race-track shaped with circumference of  232 km as in Figure 7.2.   It consists of arcs of radius 35 km and 10 straight sections (total length 12 km) for injection, abort, RF cavities, Interaction Regions for experiments, and beam transfers between the Stage 1 and Stage 2 rings.  The ring will be adjacent to the Fermilab Tevatron which will serve as the injector to the Stage 1 (low field) ring as in Figure 7.7. The major straight sections will be clustered (5 each cluster) at Fermilab and at the side opposite.  Keeping many of these special tunnels, the abort/beam stops, and the experimental areas at Fermilab will optimize utilization of the existing infrastructure and minimize offsite underground construction and shafts.  The cluster opposite will contain only the Stage1 to Stage 2 beam transfer and possibly beam scrapers.  Much of these opposite side straight sections can be reserved for future needs.  The cluster of straight sections near Fermilab is illustrated in Figures 7.8.a, 7.8.b, and 7.8.c.  Although one configuration for Tevatron injection is shown in these figures and used for the cost estimating exercise, other possible geometry options were discussed in Chapter 4.

Figure 7.6:  Main Tunnel cross section (diameter under discussion, see sketch).

Figure 7.7:  Extraction from Tevatron to North Ring and location of Experimental Halls/Caverns. (figure is incomplete, under construction)

The main tunnel will have a minimum finished inner clear diameter of 12 feet with 10 foot wide invert floor (Figure 7.6).  Tunnel center alignment will be required to + 4 inches.  The tunnel is specified as having an average groundwater influx of not more than 50 gallons per minute per mile.  This may require grouting or even lining of some tunnel sections to reduce the

groundwater influx to this specification.  The corrosiveness of wet soil may be an issue in design of tunnel liners. Dehumidification of the tunnel air might be required.  The four utility straight sections (injection, abort, RF, and Stage 1 to Stage 2 beam transfers) will likely require additional transverse dimensions, up to 25 feet x 25 feet square cross section. (the SSC design for RF caverns had a 25 foot horseshoe shape).   These can be finished by drill and blasting techniques after initial tunnel construction by tunnel boring machine technology. Similarly, at the 12 cryo sites and at the 12 mid-sites, additional underground caverns will be required for tunnel power distribution, cryogenics components, and quench protection systems.

Figure 7.8.a:  Straight Section Geometry adjacent to Tevatron. See Figure 7.8.b for (distorted scale) details.

Table 7.2:  Five straight sections and intervening arcs at Fermilab (top to bottom in Fig. 7.8.c)

| Major Arc | 174 degrees bend - to/from far side cluster of straight sections |
| --- | --- |
| Utility Straight | CW Phase 1 Injection, CW-1 beam scraping, CCW-1 abort, |
| 1.38 km | CW-2 abort, RF cavities with parallel PS & RF Klystron cavern |
|  | larger tunnel cross section - 25 ft x 25 ft |
| Bend Section | 28.491 mrad bend @ 35 km radius |
| 1.00 km | stub to Phase 2 Low Field Ring Bypass tunnel |
| IR Straight | experimental hall/cavern - 100 meters long |
| 1.64 km | with equipment bypass tunnel - 0.55 km @ 25 m bypass |
| Bend Section | 20.668 mrad bend @ 35 km radius |
| 0.72 km |  |
| Short Straight | CW and CCW beams cross-over, changing magnet apertures |
| 0.27 km | may require slightly enlarged tunnel |
| Bend Section | 20.668 mrad bend @ 35 km radius |
| 0.72 km |  |
| IR Straight | experimental hall/cavern - 100 meters long |
| 1.64 km | with equipment bypass tunnel - 0.55 km @ 25 m bypass |
| Bend Section | 28.491 mrad bend @ 35 km radius |
| 1.00 km | stub to Phase 2 Low Field Ring Bypass tunnel |
| Utility Straight | CCW-1 Injection, CCW-1 beam scraping, CW-1 abort, |
| 1.38 km | CW-2 abort, RF cavities with parallel PS & RF Klystron cavern |
|  | larger tunnel cross section - 25 ft x 25 ft |
| Major Arc | 174 degrees bend - to/from far side cluster of straight sections |

It is anticipated that there be 12 major equipment access shafts, 30 foot diameter, with a clear 6’ x 30’ aperture, distributed around the ring at the sites of the 12 cryogenics plants, as in Figure 7.9. The rest of the aperture of these shafts will be filled with equipment elevator, cryogenics, power, communications, and sump discharge utilities, plus an isolated emergency egress staircase. Dipoles for both Stage 1 and Stage 2 will access the tunnel through the injection ramps to the surface.  There may be a similar additional installation ramp at the cluster of straight sections opposite Fermilab. See Figure 7.8.a, 7.8.b, and 7.8.c.  For emergency egress and tunnel ventilation, there will be approximately 24 additional shafts of 15 foot diameter separated by 3.0 miles maximum (the SSCL standard was 2.7 miles, see Ch. 7.8.).  This egress shaft will be provided with an elevator, but, due to the depth, likely not a parallel staircase.

Figure 7.8.b:  Schematic (distorted scale) geometry of straight sections and Stage 2 Bypass line.

In addition, at each of the 1710 half-cells, separated by 135.5 meters, there will be a 1 foot diameter x 5 foot deep electronics drawer for instrumentation and power supplies for the correction elements. See section 7.4.7 below.

Figure 7.8.c:  Schematic geometry of the clustered straight sections.  (to be added – see enclosed figs.)

  - Injection line tunnels (various scenarios), beam abort lines,      equipment access ramps, and Stage 2 low-field ring bypass.

Options for injecting from the Tevatron to the VLHC are discussed in Chapter 4.  The Tevatron Complex and Injector, and specifically in Chapter 4.3.  Tevatron Transfer Lines.  For whatever option is chosen, the Tevatron tunnel will have a new line(s) tangential which will then pitch downward to the elevation of the VLHC as in Figure 7.10.  The major slope of this injection tunnel could be up to 4.2 % grade which will be sufficiently flat to serve as part of the equipment access ramp(s).  There will be an incentive to cross the boundary between glacial drift and bedrock surface as steeply as possible to reduce both complexity of construction and ground water influx at the interface.  The less steeply sloped equipment access tunnel would continue to the surface.

Figure 7.9:  1/12 Ring showing A-Site, B-site, and mid-Site underground caverns and shafts.(see sketch)

There also will be two sets of straight tunnels connected to the two near-Fermilab Utility Straight Sections.  One set will be for the injection lines from the Tevatron to the Stage1 low field ring and equipment access ramps to the surface.  The other set will be for the abort beam lines of both the Stage 1 and Stage 2 high field ring,.  Figure 7.x illustrates the bi-polar operation and extraction from the Tevatron.  Table 7.2 also includes the length of arcs for uni-polar and 6-9 configuration operations and extraction from the Tevatron.  Some of  lines for injection, abort, and equipment ramps could likely share some common tunnel sections.  However, the lines are now listed independently.  The interfaces between these tunnels have not yet been designed.  To facilitate construction and installation of a VLHC, it will be important to configure the equipment ramps to allow access while the Tevatron program is in operation.

It is planned to operate the Stage 1 VLHC with the low field, super-ferric magnet ring.  For Stage 2, a high field superconducting ring will be added.   The low field ring will serve as injector to the high field ring.  This beam transfer from low field ring to high field ring is anticipated to occur in the straight sections opposite Fermilab.  In order to reduce crowding and (possibly) to allow access to the experimental halls/caverns while the low field ring operates, the low-field ring will move to the inside of the main tunnel ring between, with extra and stronger bends to match its beam arc length to that of the high field ring through the main tunnel.  In the current model, stubs will be provided at the 28.4 mrad bend enclosures to allow later construction of this bypass tunnel for the low field ring in Stage 2.  No such bypass is planned for the far-side cluster of straight sections

Figure 7.10:  Schematic of injection ramps for tilted North Ring configuration.

All of these special tunnel sections are anticipated to be of the same inner finished diameter as that of the main tunnel.

  - Accelerator utility caverns (includes special requirements for abort system)

Where detailed specifications were lacking at this time, many of the design features for the SSC Lab [10] were used as a temporary model.

Table 7.3:   Special Tunnel Sections (same finished diameter as main tunnel)

| Function | # | Length ea. | Comments - all located at Fermilab site |
| --- | --- | --- | --- |
| Access Ramps | 2 | 3.5 + km | up to 4 % grade to sruface (745 ft msl) |
|  |  |  | (possibly 1 access on side opposite Fermilab) |
| Abort Lines | 2 | 3.7 km | at tunnel level to common abort/beam stop cavern |
| Injection Lines | 2 | varies: | Tevatron (722' msl) to VLHC Utility Straight Sec. |
|  |  | 3.5 km | (bi-polar configuration) |
|  |  | or 5.7 km | (uni-polar with 3.5 km radius of curvature) |
|  |  | or 3.7 km | (6-9 configuration) |
| Exp. Hall Bypass | 2 | 0.55 km | radius = 2.0 km, offset = 25 meters |
| Low Field Ring Bypass | 2 | 7.0 km | Phase 2 construction only, radius = 2.0 km |

    - Beam Stop Enclosure (1)

A single beam stop enclosure will be located on the Fermilab site at the elevation of the main tunnel.  It will house the water cooled (need cooling specs and mechanical systems, where?) beam stop which will simultaneously service the four rings:  low-field CW, low-field CCW, high-field CW, and high-field CCW.  The beam stop enclosure is fed by standard diameter tunnels from the inboard ends of the two Utility Straight Sections at the Fermilab site.  By putting all four beam stops at the same location, this plan minimizes the number of places where high energy densities and high radiation fields are encountered, and does this on the existing Fermilab site.  The size of the beam stop enclosure will be 16 m x 16 m x 40 m (WxHxL).  It will have the necessary shielding and water impervious retention linings to prevent radioactive contamination of the bedrock or groundwater either by prompt or residual radiation or by coolant leakage.  A reservoir cavern (size) below the cavern elevation will prevent contamination of the tunnels due to leakage of beam stop coolant.  This reservoir cavern will allow monitoring of the radioactivity and other contamination levels before proper discharge.  There will be a 30 foot diameter equipment access shaft and a 15 foot diameter personnel access shaft at this enclosure site.

    - RF Klystron Tube Enclosure (2) (SSC specs)

Adjacent to the utility straight sections, the Klystron Tube Galleries house the RF driver tubes and power supplies for the RF cavities.  The Klystron galleries are intended to be accessible by personnel for servicing systems during operation of the VLHC.  The position of the gallery is illustrated in Figure 7.8.c. The Klystron Gallery is 25 feet x 25 feet x 240 feet long, serviced by a 30 foot diameter equipment and personnel shaft.  This length will accommodate both Stage 1 and Stage 2 machines. It is a minimum of 30 feet from the accelerator tunnel and is joined to the RF Cavern by four 30” diameter feed throughs, and a 12 foot diameter labyrinth corridor.  Need cooling specs.  The electrical power levels and LCW cooling capacity needed for the RF systems are 20 MW (Stage 1) and 40 MW (Stage 2) for the initial enclosure and 20 MW for the second (Stage 2) enclosure.  The pairs of  Kicker Magnet Power Supply Enclosures and RF Klystron Tube Enclosures at the Fermilab site may be combined into single caverns.

    - Kicker Magnet Power Supply Enclosures (4) (SSC specs)

The Kicker Magnet Power Supply Enclosures house the power supplies for injection and abort (at the Fermilab site) and for beam transfer from Low-Field to High-Field Rings (opposite side). These enclosures are adjacent to the four Utility Straight Sections. The position of the enclosure is illustrated in Figure 7.8.c. The Kicker Power Supply Enclosure is 25 feet x 25 feet x 200 feet long, serviced by a 15 foot diameter equipment and personnel shaft. .  This length will accommodate both Stage 1 and Stage 2 machines.  It is a minimum of 30 feet from the accelerator tunnel and is joined to the Utility Straight Section by four 12” diameter feed throughs, and a 12 foot diameter labyrinth corridor.  Since the kickers are energized by capacitor discharge at a low duty factor, power requirements are minimum and air cooling seems to be sufficient. The pairs of  Kicker Magnet Power Supply Enclosures and RF Klystron Tube Enclosures at the Fermilab site may be combined into single caverns

    - Groundwater Collection Caverns and Pumping Stations (6)

The handling of groundwater seepage during the lifetime of the VLHC project will be a major concern.  The tunnel design specifies a maximum average of 50 gallons per minute per mile, or a total of 7,200 gallons per minute.  This flow will be directed through conduits through the invert floor to six collection and pumping stations at the A-sites of the cryogenics plants.  A gentle slope of the tunnel floor is required to drive this water to the collection/pumping sites. It is necessary to be able to collect at least 1 day’s (or 8 hours) flow of groundwater seepage (1.728 Million gallons = 231,000 cu. ft. per day for each of 6 pumping sites), in the event of failure of power or water systems.   At each of the 6 pumping sites, there will be groundwater collection reservoir caverns of dimensions (equivalent to) 62 ft x 62 ft x 62 ft plus volume for pumps and/or back-up emergency power dedicated for pumping.  Given this average water influx rate, the power for pumping to the surface for the entire tunnel is estimated to be 1.6 MW.  If required, any monitoring of  groundwater influx for contamination, either conventional or radioactive, can be sampled at the collection caverns before discharge. Pumping facilities could be distributed over the 6 A-sites and 6 B-sites. But what if it is contaminated?  Or even suspected to be contaminated?  We can’t stop discharging without risk of flooding the tunnel.  This task remains over the 40 year operational life of the project.  Do we need greater buffer volumes?  Maybe we need to do everything to exclude water from tunnel.

    - AC Power Distribution Alcoves (24)

These are alcoves cut into the aisle side of the tunnel wall every 10 km, each 27’ transverse x 25’ long x 10’ high, which house transformers, switch gear, and breakers to step down the 13.8 KV feeders fed through the tunnel from the cryo sites to 480/277 and 120/208 VAC for further distribution around the ring.  For redundancy, there will be four 13.8 KV transformers per alcove.  All components will be dry, without oil, to minimize fire hazards and environmental concerns below ground. Although the caverns are sized for the full Stage 1 plus Stage 2 complement, half of these components would initially be installed, with the second half installed for Stage 2.  This cavern is shown as part of Figure 7.11.

7.4.6  Cryo Valve Alcoves (12)

For each of the 12 mid-sites, between the A-sites and B-sites, there will be small alcoves, 10’ transverse x 20’ long x 15’ high, cut into the tunnel wall behind the accelerator rings with access stairs and catwalks.  These allow more room for the installation of the cryogenic turn-around boxes and valves for magnet cool down and flow control and manipulation of  bayonet cryogenic couplers.  There will be an additional cavern 30’ transverse x 20’ long x 20’ high to house the personnel staircase/beam overpass and a small chain fall crane for equipment. This cavern is shown as part of Figure 7.11.

    - Quench Resistor Caverns (12) – Stage 2

For Stage 2, quench protection resistors will pe placed at the mid-sites.  This will require caverns of size 40 ft x 30 ft x 15 ft (WxLxH) to house the resistors and cooling systems. This cavern is shown as part of Figure 7.11.

    - Cryo Systems Caverns (12) – Tom Peterson

Although most of the cryogenic refrigeration equipment will be located on the surface,  caverns will be required at the elevation of the VLHC rings for additional cryogenics refrigeration equipment to compensate for the pressure drop due to gravity.  For Stage 1, it is anticipated that there be 6 such caverns of dimensions 20’ transverse x 20’ long x 40’ high located at the A-sites.  For Stage 2, it is anticipated that there be 12 such caverns of dimensions XX’ transverse x YY’ long x ZZ’ high located at the A-sites and ad the B-sites.  Since these caverns will house vital rotating machinery requiring frequent maintenance, they will be located at 30 feet from the tunnel. This will provide adequate radiation shielding to allow occupancy by personnel during operations of the VLHC..  There will be a major 30’ diameter equipment, utilities, and access shaft, along with a Y-shaped switchback for access to the tunnel and radiation shielding.  This is depicted in Figure 7.12.

Figure 7.11:  Mid-Site Underground Enclosures/Caverns. (see sketch)

Figure 7.12:  Site-A and Site-B Underground Enclosures/Caverns.(see sketch)

7.4.9  Electronics Drawers (1710)

These are small cylindrical enclosures, 5’ deep x 1’ diameter, bored into the aisle side of the tunnel wall.  These will house low power supplies for the trim and corrector magnets for both rings, along with instrumentation and controls.  The electronics components will be isolated from the tunnel by a fire/access door, and the small heat load will be cooled by convective cooling of a heat exchanger plate by the tunnel air flow. The electronics drawers will be humidity controlled and isolated from the tunnel by a fire door. The equipment contained in this electronics drawer will be on rolling racks allowing access when extracted into the tunnel aisle.   This is illustrated in Figure 7.6.

  - Experimental caverns and bypasses (SSC model)

There is intended to be provision for two experimental caverns and installations in the IR straight sections at the Fermilab site.  These caverns, major access shafts, and associated surface structures for experimental apparatus fabrication, staging, and operations, will be located on the Fermilab site to minimize land procurement.  The model chosen is that of the designs for the caverns for the GEM and SDC experiments at the SSC [10,11].  It is understood that these caverns were optimized for a 20 TeV x  20 TeV collider, analogous to the VLHC Stage 1 Collider, and specifically not for the 87.5 TeV x 87.5 TeV VLHC Stage 2 Collider.  At this stage of this exercise, it is not fully appreciated how the cavern needs scale with collider energy.   The current model assumes that there is only one pair of experiment caverns, placed along the tunnel of the Stage 2 ring.  During Stage 1, the low field ring will also follow the Stage 2 tunnel.  For Stage 2, the low field ring will be displaced through its low-field ring bypass tunnel, away from the Experimental Caverns.  There will not be interaction regions or experimental caverns in the Stage 2 low field bypass.  Before Stage 2, the experiments will have to upgrade to the increased energy range (> 4 X), including a vertical change in the position of the interaction point, due to the difference in elevations of the low-field and high-field rings.

Cost optimization of the combination of geology, structural strength of strata, height of dolomite in spans, strength of walls, requirements of radiation shielding, and equipment access all determine the siting in elevation of the experimental caverns, and, thus, also the tunnel elevation at the Fermilab site.

Structural features and thickness of the strata supporting the spans of the experimental halls or caverns [2] will determine the elevations at which the caverns can feasibly be sited.  This, of course, implies the elevation of the accelerator tunnel at the site of the cavern.  A general rule of thumb is that there should be a depth of hard rock (dolomite) strata above the cavern at least equal to the span of the cavern.  The previous study has concluded that for 75 foot high chambers, roof spans up to 125 feet are feasible using standard methods of  roof arching and rock supports.  This assumed that the orientation axis of the cavern bisects the major joint sets.  The joints run approximately NE-SW x NW-SE so this criteria would be satisfied by VLHC ring orientations to the North, South, or West.  Possible options in elevation for the experimental caverns are depicted in Figure 7.5.

The experimental caverns are envisioned to be 30 m x 45 m x 100 m (WxHxL) as in the SSC model depicted in Figure 7.13, 7.14, and 7.15.

Figure 7.13:  Experimental Hall/Cavern, modeled on SSC-GEM.

Figure 7.14:  Experimental Area, surface structures, modeled on SSC-GEM.

Figure 7.15:  Experimental Area, isometric, modeled on SSC-GEM.

The current model does NOT have special underground cryogenic plants to service possible superconducting experiment magnet sytems.  Special cryo plant alcoves would be added parallel to, and isolated from the experimental halls.  Similarly, the experimental halls would be isolated from the accelerator tunnel to minimize the Oxygen Deficiency Hazards associated with the superconducting accelerators.

A tunnel bypass, to allow free access and transport of accelerator personnel, utilities, and equipment without entering the experimental caverns will be included.  A 25 meter maximum offset can be accommodated with  2 km radius bends over a total bypass length of 550 meters (including the 100 meters).  This would be of the same diameter as the main tunnel, likely constructed by backing up the tunnel boring machine.  Likewise, the tunnels for the abort line and the sloped tunnels for the injection lines/access ramps will pass nearby the experimental halls.

Table 7.4:  Experimental Facilities (SSC specs)

| SSC Experimental Halls Designs |  |  |  |  |
| --- | --- | --- | --- | --- |
| From SSCL-SR-1235 (1994) |  |  |  |  |
| Underground caverns |  | GEM IR-5 | SDC IR-8 | units |
| beam depth |  | 50 | 50 | meters |
| size of hall (WxLxH) |  | 30x100x45 | 30x105x45 | mxmxm |
| Cranes |  | 2 * 100/20 | 2 * 100/20 | Tons |
| Detector weight |  | 11,000 | 40,000 | Tons |
| Surface cranes |  | gantry ?? | gantry 100/20 | Tons |
| Heavy load path (on surface) |  | 1600 | ?? | Tonnes |
| pit (below beam) |  | NA | -13.9 | meters |
| main floor (below beam) |  | -13 | -6.8 | meters |
| top of experiment (clears crane) |  | +10.5 | +10 | meters |
| Installation shafts (hall to surface) |  | 2 * 28 x 18 | 2 * 11 x 18 | m x m |
| Surface structures | GEM North | GEM South | SDC AB | units |
| Assembly buildings | 64 x 110 | 60 x 110 | 60 x 134 | m x m |
| With high bay | 30 x 110 | 30 x 110 | 30 x 134 | m x m |
| Cranes | 2 * 45/10 | 2 * 35/10 | 50/100 + 2 20/5 | tons |
| Side bays | 1 story | 1 + 2 storys | 1 story |  |
| Doors | ?? | ?? | 14 x12 +18x12 | m x m |
| Personnel access buildings |  |  |  |  |
| size (free stand head house) |  | 13 x 5 | 10 x 11 | m x m |
| Shaft diameter |  | 13 x 18 | 9 meters dia. | m x m |
| Other buildings |  | EQ access | Detector Ops |  |
| size |  | 15 x 20 | 24 x 44 2 story | m x m |
| Shaft diameter |  | utility 13x17.5 | cable 9 m dia | meters dia |
| Adjacent head house |  | NA | 12 x 11 | m x m |
| Utility buildings |  | 24 x 80 | 24 x 80 | m x m |
| Shaft diameter |  | NA | 10 m dia | meters dia |
| Adjacent head house |  | NA | 14 x 14 | m x m |
| Gas mixing building |  | 16 x 13 | 17 x 10 | m x m |
| site footprint |  | 26 | 17 | acres |

  - Surface buildings, utilities, factories, and footprints

    - Stage 1

The required surface buildings include the 12 cryogenics service areas, small service areas for the beam stops,  RF Klystron tube and the Kicker Power Supply caverns.   One of the A-site cryogenics plants and the beam stop and RF Klystron/Kicker PS service areas are anticipated to be on the Fermilab site.  In addition, the emergency egress/ventilation shafts will require minimum head houses and footprints, both on- and off- the Fermilab site.  The cryogenic service areas will provide equipment and personnel access, collider power supplies, and groundwater pumping stations.  For Stage 1, there will be only 1 plant at each cryogenics A-site.  This will minimize the square-feet of building space and power and cooling requirements, and even the land footprint requirements.  However, since it seems more appropriate to consider land acquisition as a single activity, the total land needs for the Stage 2 are indicated.  The major power and heat load will be for the Helium compressors.   These requirements, also, are greatly reduced for the Stage 1 VLHC.  The choice of cooling methodology, either cooling ponds or air cooling towers, will likely be dictated as much by the local aesthetics of a possibly suburban environment as by cost considerations. There will be one power supply station for the 100 KA magnet bus.  This will be located at the cryogenics A-site at Fermilab.  It will consist of a building, 75’ x  40’, and an outdoor pad, 20’ x 25’ for transformer and oil containment.  A superconducting transmission line will carry this current to the tunnel via a vertical shaft.

At the two access ramps at the Fermilab site (and a possible third access ramp opposite) there will be the need for warehouse and assembly buildings for final fabrication of the long magnet and cryogenics systems to be installed in the tunnel.  The size, capacity, and complexity of the cryogenics test station/facility associated with these factories will be comparable to that of the Fermilab Magnet Test Facility (MTF).

Figure 7.16:  Cryogenics and Utility Plants at A-sites and B-sites for Stage 1 and Stage 2

    - Stage 2

The additional facilities for Stage 2 will include greatly increasing the capacity of  the six cryogenics A-sites, adding similar enlarged cryo plants at the six B-sites  and increasing the utilities for the RF Klystron/Kicker PS caverns.  There will also be Stage 2 magnet power supply buildings, of similar size and utilities to those of Stage 1, located at each of the twelve cryogenics service sites.

  - Survey and Magnet Alignment (Global, for Tunnel)

This section has a discussion of the errors encountered in machine installation and techniques of building networks for machine alignment. Some estimation of possible errors are made based on experiences from the Main Injector project at Fermilab.

The ability to transport beam around any separate function synchrocyclotron is directly dependent on how well the each component of the machine is installed. The total installation error can be expressed as

σ2 = σn2 + σm2 + σf2 + σs2

where:

σn  are errors in the network

σm  are errors due to measurement between control points and magnet fiducials

σf   are errors due deviation between the magnet fiducials and the magnetic center

σs  are errors due to stand adjustment

The errors in the stand adjustment (σs) are a mechanical design issue. There is a trade off between cost of the stand and the ability to precisely position the magnet. This is very important of the position along the beam line (station). The ability to move a 65 meter long magnet without causing undue stress needs to be studied. Also the lattice designers should determine how precisely in station the dipoles must be from the quadrupoles. It may be easier to have a lamination pack that can be added to or subtracted from the magnet once it is installed to make up for errors in the station. Once these values are determined a detail design for a stand can evolve.

The errors between the magnet fiducial and the magnetic center (σf) will be dominated by the quality of the lamination stamping. Experience from the Main Injector indicates that this can be controlled to ± 0.025 mm. This should be an acceptable error for the VLHC.

The errors between the control points and the fiducials (σm) are determine by the instruments used and the skill of the people doing the measurements. For the Main Injector a Laser Tracker was used for the final installation of all magnet elements. This device is a laser interferometer using a set of motor driven mirrors and a feedback system to follow a corner reflector from a base location to a desired spot. The ultimate accuracy of such a device is  ±10 microns with an angular resolution of 0.2 milli-radians. This is for short distances (less than 50 meters) and in controlled atmospheric conditions. To obtain the best results with such a device a dense network of monuments must be available near the magnets such that multiple and redundant measurements can be made. One of the major advantages of a laser tracker is that computer thereby eliminating blunders made by the alignment crew records all measurements. If a bar code system is in place for the magnets and the network monuments blunders should be virtually eliminated. A database will need to be developed to track the offsets from the magnet to the network. This database will also need to have the values determined from the construction of each magnet and magnetic field measurement.

The dominate error is the network itself (σn). Since ancient Egypt all survey networks have the same structure. They consist of a set of inter-linking triangles where the distance from the start to any point in the network is determined by either triangulation or trilateration. Triangulation consists of measuring the length of a base line and all the angles of all the triangles. The law of sines is then used to calculate the distances between each vertex (monument) of the triangles. Since the sine of angles near 0 degrees varies rapidly angles less than 30 degrees or greater than 150 degrees should be avoided. It is obvious that this is impossible inside the VLHC tunnel.

Trilateration consists of measuring the distances between the monuments in a network and at least one angle. These distances are then reduced to a plane coordinate system for error checking. By using a laser interferometer such as a Kern Mekometer errors are 0.2 mm + 0.2 10-6  * distance measured in mm. For the long narrow geometry of the VLHC tunnel this is the preferable method.

The proposed circumference of the VLHC is 232 kilometers. This will consist of long straight sections connected with arcs. Using a radius of 36,924 meters the longest line of sight (LOS) in the tunnel will be 941.4 meters. . The LOS will set the base of the primary network in the tunnel. Given that various objects such as magnets will be in the tunnel and the end points will need to be occupied with instruments the exact length of the base line will be slightly shorter. It will be possible to occupy the center point of this base line and measure to either end point with the Mekometer with an error of ± 0.39 mm. These primary base lines will serve a similar purpose to the Murphy line [12] in the Tevatron. They should be located parallel to the quadrupoles in each section. This will keep the necessary offsets constant for each quadrupole.

Figure 7.17:  Alignment schematic for technical components.

In the region of dipoles and quadrupoles the primary network will be densified, that is more monuments will be installed near the magnets to give redundant measurements. The accuracy of these monuments will depend directly on the primary base line.  Error analysis of the Main Injector network [13] indicated a tunnel monument position should be better than ±0.3 mm.

In the ideal world each of these baseline points would have a site riser located directly over so that solid connection to the outside network can be made. This works out to almost 250 site risers. Given that the VLHC will want to minimize the interaction with land holders and that some of these points will located under objects that can not have direct connection to the surface (i.e. under a lake or river) significantly less site risers will be allowed. It is important that connection to the surface be made. A strong surface network using GPS and standard survey techniques will strengthen the underground network.

Consideration should be given to the fact that IDOT region II has been installing a Class I GPS network consisting of 250 monuments [14]. This is in the area north of Interstate 80 and south of the Wisconsin border, West of the Kane-DeKalb county line to the Mississippi River. The errors between the monuments in this area are better than 1 part per 100,000. This can be used as part of the above ground network for the VLHC. This would save time and effort in the construction phase.

Given the size of the VLHC ring geodetic techniques will be required to ensure that the above ground network and the tunnel network are designed and installed properly. Care must be taken to account for variation in the geoid and gravity over the entire site. Both will be significant for this machine. It is very possible that there will be significant Variations in the local vertical due to change in the rock density. This needs to be monitors during construction, and measured after the tunnel is complete.

The exact errors in the above ground and primary underground network can be modeled once a detailed lattice and tunnel layout are known. It is reasonable to use the 0.25 mm error budget that the Main Injector applied at this time.

  - ES&H issues during construction, installation, and operations

(worker health & safety, wetlands restoration, muck disposal,

egress, etc.)

For this exercise, ES&H issues have been merely identified without detailed study or specification of proposed solutions. Most of the ES&H issues both during construction and during operations of a VLHC are discussed for generic new accelerator facilities by the Fermilab Committee on Site Studies [15].  This section is intended to focus on issues peculiar to the VLHC and its scale that are in addition to the issues discussed by the FCSS.  Although it is anticipated that much further ES&H work will be needed to optimize the costs and operations of a VLHC and satisfy standards to be applicable at the relevant time scales, for the purposes of this study, many of the ES&H requirements of the Superconducting Super Collider Laboratatory [16, 17] were assumed for the specifications and costing exercises.

VLHC design/specification issues with ES&H impact start with the finished diameter of the main tunnel.  A larger diameter will optimize installation, operations, and maintenance of the accelerator systems, and improve emergency egress and response.  However, increasing the tunnel diameter increases the overall project cost.   Personnel access and egress are issues with the number and placement of minor shafts.  After much negotiation, the Department of Energy accepted a minimum egress/ventilation shaft spacing of 2.7 miles for the final operating configuration for the SSC.  The Chicago area deep reservoir project (TARP) construction required a temporary personnel access/egress shaft (serviced by a crane with man-cage, at a maximum of 5000 feet from the dead-headed boring face.  Such temporary egress shafts are filled-in upon completion and final finishing of that nearby tunnel section.

In this study, it is anticipated that there will be minimum fire and smoke hazards in the tunnel.  The main accelerator bus power supplies will be located on the surface.  Power distribution transformers, switch gear, and breakers located locally in the tunnel will be oil-free. Smaller power supplies and electronics will be in special fire and smoke resistive electronics drawers, and interconnecting cables of low toxicity and of low smoke generation.   The special underground enclosures for RF Klystrons and Kicker Power Supplies and the Experimental Caverns could be equipped with local automatic fire suppression systems. The envisioned VLHC cryogenics systems will not use Liquid Nitrogen.  The quench reliefs of the Liquid Helium systems will be through high pressure piping within the cryogenic transfer lines.  What if that proves to be a problem?  There is the possibility of leaks and ruptures at every interconnect.  With reduced fire, smoke, and oxygen deficiency hazards, it is anticipated that during and after installation of the accelerator components, personnel entering the tunnel will carry sufficient oxygen supplies (2 hours?) nearby on their motorized access vehicles, removing the need for safety refuges [17].  The SSCL had refuges, each with two hour fire door and two hour emergency air supply for up to 7 people located not greater than 2500 feet apart, between the emergency egress shafts.

The handling of groundwater issues will be a major environmental concern throughout the VLHC project.  Much of the tunnel, although below the piezometric surface (water table), will be in the Galena-Platteville dolomite, which is classified as an aquitard.  Still, grouting of cracks will be required to reduce the post-construction groundwater influx to workable pumping limits.  Other strata such as the sandstone and dolomitic sandstone, below the water table, of the South Ring configuration will be problematic from structural and water influx rate viewpoints and likely will require fully lined tunnel sections.

During tunnel construction, there will be additional water influx rates before tunnel grouting and lining, especially at the injection/equipment access ramps where the long and shallow-angle traversal of the glacial till-bedrock surface interface may be problematic before tunnel lining.  There will be the issues of dewatering the aquifer both during construction and operations,  prevention of aquifer contamination during construction, and radiological contamination of the soil and aquifer during accelerator operations.  Not only will the volume of water discharged during construction require serious attention, the quality of this discharge, in terms of suspended solids and other environmental limits, will likely be an issue. Channeling, storage, pumping, and disposal of groundwater influx will require an engineered solution.  Are existing creeks nearby capable of accepting the water discharge?  The VLHC operational specification for groundwater seepage is an average discharge of 50 gallons per minute per mile of tunnel corresponds to a total of  7,200 gpm total, to be distributed over 6 pumping sites, each at 1,200 gpm.  Optimization studies will have to be undertaken to balance additional construction costs for water exclusion versus operating costs for dewatering costs over a 40 year (?) lifetime of the VLHC, including environmental impacts.

Special consideration of beam-loss => groundwater contamination – need Mokhov model.

For the Stage 2 – high field ring VLHC, each of the 12 remote cryogenics sites will be consuming approximately 15 MW electrical power, mainly to run the Helium compressors.  This power will have to be dissipated to the environment, either by air-cooling towers, cooling ponds (approximately 15 acres each), or combinations of towers and ponds, depending on the particular environmental needs at each cryogenics site.

The disposal of spoils or muck from the underground construction will be an issue.  The spoils will have various fractions of clay, dolomite, shale, sandstone, etc. The Illinois SSC Proposal [18] evaluated four scenarios, three of which were to refill nearby previous mining operations and the fourth was in landscaping around the shafts and remote sites.  Sale of the dolomite for use as construction material may, or may not, be feasible, depending on market conditions.

Constructing a tunnel will have major surface impact for personnel and equipment access and muck removal.  Some of these surface sites will not be needed, or with reduced footprint, after construction.  It will be important to have a plan to return these lands back to the citizens of Illinois in a useable and environmentally acceptable condition.

References

[1]   Geologicial-Geotechnical Studies for Siting the Superconducting Super Collider in Illinois:  Preliminary Geological Feasibility Report, J.P. Kempton et al., ISGS Environmental Geology Notes, EGN-111 (1985).

[2]  Geotechnical Summary to the Proposal to Site the Superconducting Super Collider in Illinois, Harza Engineering Company and ISGS, (1987).

[3]  Next Linear Collider (NLC) Project, North-South Alignment, Geotechnical Study, Harza Engineering Company (2000).

[4]   Siting Considerations for Future Accelerator Facilities at Fermilab, FCSS, DRAFT 2 (01/17/01), dated XX-XX-XX, Chapter 2.  Geology and Underground Construction Methodologies.

[5]  TARP:  Chicago Tunnel and Reservoir Plan.

[6]  Summary of the NuMI Project, the Fermilab NuMI Project Staff and the MINOS Collaboration, NuMI-678, Version 5.1 (2000).

[7]  Peter J. Conroy, geo-technical consultant, Elmhurst, Illinois.

[8]  TM-2048:  Cost Model for a 3 TeV VLHC Booster Tunnel, J. Lach et al., FERMILAB-TM-2048 (1998).

[9] CNA Consulting Engineers, Charles R. Nelson and Associates, 2800 University Avenue S.E., Minneapolis, Minnesota 55414.

[10]  Superconducting Super Collider Laboratory, SSCL-SR-1056, Site Specific Conceptual Design, July, 1990.

[11]   Superconducting Super Collider, A Retrospective Summary, 1989-1993, SSCL-SR-1235, April, 1994,  Chapter 14.  Experimental Areas.

[12]   How the Tevatron was Aligned, C.T. Murphy, MI-note 0089.

[13]  Geodesy and Alignment Concepts for the Fermi Main Injector, Virgil Bocean, MI-note 0093.

[14]  www.smithengineering.com

[15]  Siting Considerations for Future Accelerator Facilities at Fermilab, FCSS, DRAFT 2 (01/17/01), dated XX-XX-XX, Chapter 4, Potential Environmental, Safety, and Health Issues.

[16]   Superconducting Super Collider, A Retrospective Summary, 1989-1993, SSCL-SR-1235, April, 1994, Chapter 28, Environment, Safety, and Health, and Quality Assurance.

[17]   SSC Egress Provisions and Features for Evaluation of Equivalency as per Chapter 7 of NFPA 101 M,  L. Coulson and T. Toohig, 5/29/00.

[18]  Disposal of Material to be Excavated from the Illinois SSC,  L.M. Curran, S. B. Bhadwat, ISGS, (1987).

Figures:

7.1	General geologic features of Northeastern Illinois. (in prep – see sketch)

7.2	Schematic of VLHC 232 km racetrack.

  - Lampshade diagram for North Ring orientation for flat and inclined tunnels.

  - Lampshade diagram for South Ring orientation for inclined tunnel.

  - Vertical siting of the experimental halls/caverns (and therefore VLHC).

  - Main Tunnel cross section.			Prelim sketch - WHAT’S THE DIAMETER

7.7	Extraction from Tevatron to North Ring and location of Experimental Halls/Caverns

(in prep - Jeff Sims prelim)

7.8.a	Straight Section Geometry adjacent to Tevatron

7.8.b	Schematic (distorted scale) geometry of straight sections and Stage 2 Bypass line.

7.8.c	Schematic geometry of clustered straight sections (in prep – see sketch)

  - Arc showing 1/12 of ring with underground caverns and shafts.

  - Schematic for injection ramps for tilted North Ring configurations.

  - Mid-site underground caverns.			(in prep – see sketch)

  - A-site and B-site underground caverns.		(in prep – see sketch)

  - Experimental Hall/Cavern.				(in prep – see sketch)

  - Experimental Areas – isometric.			(in prep – see sketch)

  - Experimental Areas – surface structures.		(in prep – see sketch)

  - Cryogenics and Utilities Plants at A-sites and B-Sites for Stage 1 and Stage 2

(in prep – see sketch)

  - Alignment schematic for technical components.