Project Number: AW-2225

Contract Number:  TW-0839

December 1996

SPECIAL SPECIFICATION

SECTION 03301

CAST-IN-PLACE CONCRETE SUPPLEMENT

PART	1	- GENERAL                                                                                                            Page

1.01	Description of Work

1.02	References

1.03	Definitions	3

1.04	Quality Assurance

1.05	Submittals

PART 2 - PRODUCTS

2.01	Form Materials

2.02	Shielding Concrete

2.03	Pool Liner Bedding Grout

2.04	Grout Under Movable Wall Sill Plate

PART 3 - EXECUTION

3.01	Placing Embeds

3.02	Joints in Shielding Concrete

3.03	Working Within Wall Forms

3.04	Placing Shielding Concrete

3.05	Finishes

3.06	Curing Shielding Concrete

3.07	Shielding Concrete Surface Repairs

3.08	Test Cell Ceiling Plugs

3.09	Movable Shield Wall

3.10	Bedding Of Stainless Steel Pool Liner

SPECIAL SPECIFICATION

SECTION 03301

CAST-IN-PLACE CONCRETE SUPPLEMENT

PART 1 - GENERAL

1.01	DESCRIPTION OF WORK

Section Includes:  Additional requirements for cast-in-place concrete materials to be used for the construction of radiation shielding, for grouting beneath the stainless steel pool liner and beneath the movable shield wall sill plate and for concrete slabs to support trucks.

Products Installed but not Specified Under this Section:

Serpentine access tubes, ceiling plug frames, elevator ceiling embeds, and embedded steel shielding are specified in Division 5, Section “Metal Fabrications.”

Pool liner is specified in Division 5 Section “Stainless Steel Pool Liner.”

Hollow metal frames in openings are specified in Division 8, Section “Steel Doors and Frames.”

Movable shield wall shell, its jamb and head liners and its sill plate are specified in Division 13, “Movable Shield Wall.”

Manipulator arm wall tubes, and shielded window frames will be Sandia Furnished Equipment (SFE).

Refer to the following sections for related work:

1. 	Division 1, Section “Environment, Safety, and Health Requirements.”

2.	Division 3, Section “Cast-in-Place Concrete.”

1.02	REFERENCES

A.	American Concrete Institute (ACI)

301	Specifications for Structural Concrete for Buildings

308	Standard Practice for Curing Concrete

309 	Standard Practice for Consolidation of Concrete (Attached hereto).

B.	American Society for Testing and Materials (ASTM)

A36	Standard Specification for Structural Steel

A525	Specification for General Requirements for Steel Sheet, Zinc-coated 	(Galvanized) by the Hot-Dip Process

C78	Flexural Strength of Concrete (Using Simple Beam with Third-Point 	Loading)

C138	Standard Test Method for Unit Weight, Yield, and Air Content 	(Gravimetric) of Concrete

C150	Specification for Portland Cement

C494	Specification for Chemical Admixtures for Concrete

C618	Specification for Fly Ash and Raw or Calcined Natural Pozzolan for use as 	a Mineral Admixture in Portland Cement Concrete

C847	Specification for Metal Lath

C1017	Specification for Chemical Admixtures for Use in Producing Flowing 	Concrete

C1107	Specification for Packaged Dry, Hydraulic-Cement Grout (non-shrink)

1.03	DEFINITIONS

Shielding:  Any material or assembly that encloses a nuclear source in order to reduce the amount of radiation that escapes into the surrounding area.

Shielding Concrete:  Shielding concrete is defined as all Portland cement concrete around the Test Cells and above elevation 95’-10” where adjacent to the pool or above elevation 99’-0” where not adjacent to the pool.

1.04 	QUALITY ASSURANCE

General:  In addition to the following provisions, comply with the requirements of Division 3, Section “Cast-in-Place Concrete.”

Quality Control:

Complete and thorough quality control, including documentation is mandatory for every placement of shielding concrete, pool concrete, embedded steel shielding and other items embedded in shielding concrete.  Towards that end, the contractor shall coordinated with the SDR to provide for complete inspection of all reinforcement, embeds and forms for shielding concrete before its placement; to provide for complete inspection of the assembled pool liner and pool reinforcement before pool concrete placement; to provide for complete inspection of the movable wall shell, reinforcement, jamb and head liners, sill plate and bearings before their grouting and concrete placement; and to provide for thorough inspection during grout and concrete placement for all these items. The Contractor shall provide a minimum of 48 hours notice prior to any concrete placement.  He shall provide complete access to the work during concrete placement. The satisfactory construction of these items and complete documentation that it has occurred is critical to the success of this project.

Contractor shall arrange for a concrete pre-placement conference to take place at least two weeks prior to the first placement of shielding concrete or of pool liner bedding grout (whichever comes first).  Representatives of the general contractor, the concrete subcontractor(s), the concrete producer and the form designer will attend.  The foremen of the crews responsible for placement of shielding concrete, its reinforcement and forming; placement of shield window frames, serpentine access tubes, manipulator wall tubes; placement of pool liner bedding grout and pool wall concrete; placement of concrete within and adjacent to the movable shield wall and of grout below the movable shield wall sill plate; and placement and removal of forms shall also attend.  Sandia’s project manager, structural engineer, inspectors, testing laboratory representatives and shielding specialists will also attend.  The subjects of discussion will include approved designs, coordination with inspectors, concrete sampling and testing requirements, authority to accept or reject fresh concrete, authority to add water to concrete at the site, distribution of test reports, basic radiation shielding construction requirements, concrete consolidation, thick concrete wall placement and curing practices, shield wall bulkhead and cold joint requirements, concrete finishing, and concrete placement rates and delivery schedules.  The contractor shall take minutes of the meeting and distribute copies to all participants.

The density of shielding concrete test specimens shall be measured in accordance with ASTM C138 at the time of placement and at 28 days.  The concrete supplier’s documented correlation between newly placed plastic concrete (“wet” concrete) density will form the basis for accepting the “wet” concrete for inclusion in shielding based on its measured wet density.  Concrete not acceptable for shielding shall be used in other applications or shall be removed from the site for disposal off base.  For further information about shielding concrete density, refer to Section 2.02 B.

The elapsed time from batching until the concrete mix is no longer of sufficient plasticity for vibratory consolidation shall be determined by the concrete supplier for all shielding concrete mix designs.  This will establish the time limit for placing additional concrete lifts on previously placed concrete with consolidation of the concrete layers without resorting to use of a cold joint.

Concrete shall be tested for modulus of rupture for concrete slabs to support trucks as noted on drawings in accordance with ASTM C78; one set of four (4) standard beams will be taken for each day of concrete placement; two (2) specimens shall be tested at 14 days and two (2) specimens shall be tested at 28 days.

If the average strength of two (2) consecutive beams tested at 28 days falls below the required tensile strength by more than 50 psi (350 kPa) below the specified strength, the in-place concrete represented by the low-strength beams shall be tested at the contractor’s expense in accordance with ASTM C42.  If the concrete still does not meet these requirements, it shall be replaced at the contractor’s expense.

1.05	SUBMITTALS

A.	General:  In addition to submittals required in Division 3, Section “Cast-in-Place Concrete,” provide the following submittals.

B.	Concrete Placement Plan:  The contractor shall submit a plan for placement of concrete on this project.  This plan shall consider required placement rates, timing of consolidation of upper and lower lifts of concrete, crane and pump placement at the site, the number of workers and equipment required, staging of delivery trucks, possible equipment and truck breakdowns, bulkhead locations and resultant placement volumes, coordination with convoys that can close roadways providing access to the site and the characteristics of the concrete mixes.

Shielding Concrete Forming Plan:  Submit shop drawings and calculations showing details of forming and tie locations for review and acceptance of the concept and joint and tie locations.  Design forms and shoring to resist hydrostatic and gravitational forces due to the concrete placement.  The shop drawings shall be stamped and signed by a Professional Engineer registered in the State of jurisdiction.

Concrete Batch Tickets shall be submitted to the SDR at the end of each day’s placement.  The tickets shall include the date and time of batching, the mix design code, time of departure from plant, admixtures, temperature of concrete at departure from plant, and time of discharge.

Safety Plan:  Submit a safety plan for working within wall forms with the general site safety plan.

PART 2 - PRODUCTS

2.01	FORM MATERIALS

General:  In addition to the following provisions, comply with the requirements of Division 3, “Cast-in-Place Concrete.”

Forms for Exposed Finish Shielding Concrete:

Construct all form work for exposed concrete surfaces with plywood, metal, metal framed plywood facing or other acceptable panel type materials to provide continuous, straight, smooth, exposed surfaces.  Furnish in largest practicable sizes to minimize number of joints.  Provide form material with sufficient thickness to withstand pressure of newly place concrete without bow or deflection.

Use A-B permanently sealed plyform, sanded, Class 1, EXT grade trademark of the American Plywood Association, PSI-83.  Only new material will be accepted for concrete formwork and may be used only twice for this project.  Any material with deformed or marred finish will be rejected.

Forms for Movable Shield Wall:  The forms for the movable shield wall, its jambs and head liner will be steel sheet as specified in Division 13, “Movable Shield Wall.”

Forms for Test Cell Ceiling Plugs:  The forms for the test cell ceiling plugs and their socket liners will consist of ASTM A36 plate continuously welded to frames of ASTM A36 shapes and will be cast integrally with the concrete.

Shielding Concrete Bulkhead Forms:

Construct all formwork for bulkheads in shielding concrete of stay-in-place expanded metal mesh with cut lumber and/or reinforcing steel supports.  Provide supports of adequate strength and spacing to withstand pressure of newly placed concrete without bow or deflection of the metal mesh or its supports.

Stay-in-place form shall be of a ribbed expanded metal fabricated in accordance with ASTM C847 from galvanized sheet steel complying with ASTM A525.  It shall be formed by lancing and expanding 26 gage or 25 gage sheet in such a manner as to form solid V-ribs of ¾” depth and spaced 3 7/8” apart with 15/64” x 3/8” parallelogram shaped mesh openings between ribs.

F.	Form Ties for Shielding Concrete:  Only solid metal form ties that remain in the concrete and snap off just below or are cut at the surface are allowed.

2.02	SHIELDING CONCRETE

General:  Shielding concrete shall comply with the requirements of Division 3, Section “Cast-in-Place Concrete” in addition to the following provisions.

Density:  The minimum cured density of shielding concrete shall be 144 pcf.  The concrete supplier shall provide documentation for each shielding concrete mix design showing the relationship for the density of the plastic concrete and the density of the 28-day old concrete.  The concrete supplier shall analyze his data to determine the standard deviation of the relationship between plastic concrete density and 28-day old concrete density.  If based on less than 30 tests, use the modified formula or modification factor, as appropriate, from ACI 318 section 5.3.1.  Based on this data and 1.5 times the standard deviation, the acceptable minimum plastic concrete density to satisfy the requirements for the minimum 28-day concrete density for each shielding concrete mix design will be established.

Concrete Materials:

Use only ASTM C150 Type V Portland cement.

Coarse aggregate shall have an absorption of less than 3%, a specific gravity greater than 2.5 and a sulfates and sulfites content less than 0.5% by weight and a maximum aggregate dimension as shown on the plans.

Mixed concrete shall have a temperature of at least 50( F  (10( C) and not more than 75( F  (24( C) at the time of placing.

2.03	POOL LINER BEDDING GROUT

General:  Special bedding grout shall comply with the requirements of Division 3, Section “Cast-in-Place Concrete” in addition to the following provisions.

Materials:

Coarse aggregate shall be 100% passing the 3/8 inch (0.95 cm) sieve.

Admixtures to improve flowability shall comply with ASTM C1017.

The non-shrink admixture shall impart the properties of low water content, good flowability, minimum of bleed and expansion properties.  The admixture shall not contain chloride ions in excess of 0.25 percent by weight.

Mix Design:  Design and document a mix design with good flowability and expansion properties such that the expansion of the grout does not exceed 0.4 percent and shrinkage is 0.0 percent.

Minimum Compressive Strength at 28 days shall be 4000 psi (27.6 MPa).

2.04	GROUT UNDER MOVABLE WALL SILL PLATE

A.	General:  The grout to be used under the sill plate shall be non-metallic, non-shrink high-strength grout complying with ASTM C1107 with a minimum compressive strength of 28 days of 4000 psi (27.6 MPa).

PART 3 - EXECUTION

3.01	PLACING EMBEDS

General:  Coordinate carefully with SDR to provide accurate, correct and documented placement of all embeds within the tolerances shown on the drawings.

Shielding Window Frames:  Employ the manufacturer of the shield window frames to coordinate installation of the frames within the forms.  Frame, shim, and weld frames in place to hold them in correct positions during concrete placement.

3.02	JOINTS IN SHIELDING CONCRETE

A.	Bulkhead Joints:   Bulkhead joints must occur only at accepted locations and in the correct geometry.  Bulkhead locations will effect the requirements for the rate of concrete placement and thus have a direct effect on the contractor’s plan for placing concrete.

Cold Joints:  Cold joint locations are not shown on the drawings.  The contractor shall be prepared, however, to place cold joints at all times during the placement of shielding concrete in the case of emergency shutdown.  All cold joints, whether planned or emergency, shall meet the requirements shown on the drawings.  In no case will joints with straight, unbroken planes be allowed.

Alternate Joint Locations:  If the contractor desires to use alternate bulkhead or cold joint locations from those shown on the drawings, he must submit a drawn plan of the new proposed joint locations at least ten working days prior to placement and have it accepted prior to implementation.

3.03	WORKING WITHIN WALL FORMS

A.	Safety:  Work within wall forms qualifies as a confined  space and require special measures to conform to Division 1, Section “Environment, Safety, and Health Requirements”

B.	Cleanliness:  Do not transport soil and trash into forms when entering.  Clean out all soil and trash before placing concrete within forms.

3.04	PLACING SHIELDING CONCRETE

A.	General:  In addition to the requirements of Division 3, Section “Cast-in-Place Concrete”, comply with the following provisions.

B.	Consolidation:  Proper consolidation is absolutely essential.  Compliance with the requirements of ACI 309 will be strictly enforced.  Provide access to inspectors for visual observation of concrete placement and consolidation at all times including, if necessary, construction of elevated and safety-railed observation platforms.  Demonstrate that the vibration techniques and equipment to be used are more than adequate for the purpose with the mix, reinforcement and volumes of concrete to be used.  Provide at least two additional vibrators on site for emergency use or replacement.

C.	Forms:  Forms and their joints must be mortar and paste tight and capably of resisting pressures from high lift placements.

3.05	FINISHES

General:  Comply with the provisions of Division 3, Section “Cast-in-Place Concrete.”

Provide Trowel Finish for all interior slabs-on-grade and for the tops of test cell ceilings.

Provide Nonslip Broom Finish to exterior concrete aprons.

Provide Grout-Cleaned Finish to exposed walls and bottoms of ceilings of test cells within 24 hours of stripping forms and completion of the wet curing process.

3.06	CURING SHIELDING CONCRETE

General:  Unless noted otherwise in the following provisions, comply with the requirements of Division 3, Section “Cast-in-Place Concrete.”

Water Curing:  The internal and external temperatures of the concrete will be monitored on a daily basis by the laboratory.  Should the interior temperature of the concrete exceed the exterior temperature by more than 25 degrees F (13.9 degrees C), watercuring will be required to the concrete.  Cure concrete surfaces by the use of water misting in combination with burlap matting.  In addition to keeping the newly placed concrete damp, the curing will keep the concrete surface cool.  Towards that end, water will not be allowed to pond on the concrete, forming pools that could collect heat; the concrete will be kept moist by misting at a rate that provides cooling by evaporation without collecting in pools.  Apply mist to forms to keep them cool during curing.  When forms are stripped, apply mist and burlap matting to the sides of concrete after stripping forms.  Cure all shielding concrete for at least fourteen (14) days after placement.

3.07	SHIELDING CONCRETE SURFACE REPAIRS

General:  Unless noted otherwise, comply with the provisions of Division 3, “Cast-in-Place Concrete.”

Patching Defective Areas:  Cut out honeycomb rock pockets and voids only after the SDR has reviewed each location.  If necessary, use a bush hammer at the edges of cut outs to insure that the edges are rough in texture.  Do not begin patching the cut out holes until the SDR has reviewed the areas and approved the holes for patching.  Proprietary bonding agents are acceptable only if they do not contain organic chemicals (hydrocarbons).

3.08	TEST CELL CEILING PLUGS

Frames:  Shop assemble the inner and outer form frames for each plug and its socket to  the tolerance as shown on the drawings.  Fit the two frames for each set of plug and socket forms together and check that the gap between the two frames does not exceed 1/4 inch (6.4 mm) at any location along the top and bottom and that the two frames fit easily together.  Correct any deficiencies and matchmark each set of fitted frames showing which frames go together and which is the north side of each frame.  Set the socket frames in the proper locations, true and square.  Insert the plug frames into the sockets and shim all around to center.  Tightly fill the gap all around with cord or other removable plug to exclude entry of concrete paste between the frames.

Reinforcement and Concrete Placement:  Install and secure reinforcement for the ceiling around and within each plug.  Accurately locate and secure lifting inserts in each plug.  Place shielding concrete in the ceiling around and within each plug in accordance with specifications.

Markings:  Mark the top of each completed plug in 1 ½” high letters with two coats of red exterior acrylic with the following captions:

An arrow pointing toward the north next to the inscription, “NORTH,”

An inscription, “TEST CELL #X” where “X” is the number, “1,” “2,” or “3” as applicable, and

The inscription, Centered between the lifting coils, “MINIMUM LIFTING BOLT PENETRATION: 2 ½ INCHES.”

Operability:  After concrete in the ceilings and in the plugs has cured for at least 28 days, verify the operability of each plug by lifting each plug out of its socket and replacing it in the presence of the SDR.

Deliverables:  At the project close out, deliver to SNL four (4) Dayton 1” T-26 double swivel lifting plates and four (4) Dayton 1” B-14 coil bolts, or approved equal, to match coil inserts used in plugs, new or used only to lift these plugs, and in good condition.

3.09	MOVABLE SHIELD WALL

General:  Coordinate placement of shielding concrete with the movable shield wall liner and from bulkheads to jamb and head liners with the movable shield wall manufacturer and the SDR.  Coordinate sill plate placement and grouting with the movable shield wall manufacturer and the SDR.  Coordinate placement of movable shield wall electrical and compressed air utilities and trolley beam and equipment anchorages with movable shield wall manufacturer and the SDR.

3.10	BEDDING OF STAINLESS STEEL POOL LINER

A.	General:  Grout below the pool liner using a flowable, non-shrink, non-ferrous mix expressly designed for this purpose and in careful coordination with the pool liner fabricator and the SDR.  Refer to the suggested methods and procedures for Field Assembly and Installation in Division 5, Section “Stainless Steel Pool Liner.”

END OF SECTION