November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 16002-S

SEISMIC RESTRAINT OF ELECTRICAL SYSTEMS AND EQUIPMENT

Page

PART 1 - GENERAL

1.01 	Scope	2

1.02	Submittal Data Requirements	3

1.03	Code and Standards Requirements	4

1.04	Manufacturer’s Responsibility	4

1.05	Related Work	5

1.06 	Seismic Force Levels	5

PART 2 - PRODUCTS

2.01	Intent	6

2.02 	Acceptable Manufacturers	6

2.03 	Anchorage	6

PART 3 - EXECUTION

3.01 	General	6

3.02 	Seismic Restraint of Electrical Services	7

3.03 	Seismic Restraint Exclusions	7

SPECIAL SPECIFICATION

SECTION 16002-S

SEISMIC RESTRAINT OF ELECTRICAL SYSTEMS AND EQUIPMENT

PART 1 - GENERAL

l.0l 	SCOPE

A.		Intent

1.	It is the intent of this specification to keep all electrical building system components in place during a seismic event.

2.	All such systems must be installed in strict accordance with seismic codes, component manufacturer's and building construction standards.  Whenever a conflict occurs between the manufacturer's or construction standards, the most stringent shall apply.

3.	Any variance or non-compliance with these specification requirements shall be corrected by the contractor in an approved manner.

4.	Seismic restraints shall be designed in accordance with seismic force levels as detailed in section 1.0.6.

B.	 	The work in this section includes, but is not limited to the following:

1.	Seismic restraint for electrical systems and equipment.

2.	Equipment buried underground is excluded but entry of services through the foundation wall is included.

3.	Typical equipment to be restrained is as follows (Equipment listed is still included in this specification):

Battery Racks		Generators

Bus Ducts		Light Fixtures

Cable Trays		Motor Control Centers

Conduit		Switching Gear

Electrical Panels	Transformers

Unit Substations

C.	Definitions

1.	Positive Attachment:

a.	A positive attachment is defined as a concrete anchor, a double sided beam clamp loaded perpendicular to a beam, or bolted connection to structure. Single sided "C" type beam clamps for support rods of electrical conduit, bus duct, or cable trays  or any other equipment are not acceptable on this project as seismic anchor points.

2.	Transverse Bracing:

a.	Restraint(s) applied to limit motion perpendicular to the centerline of conduit or cable tray.

3.	Longitudinal Bracing:

Restraint(s) applied to limit motion parallel to the centerline of the 
conduit or cable tray.

1.02  	SUBMITTAL DATA REQUIREMENTS

A. 		The manufacturer of seismic restraints shall provide submittals per 1300-S for products as follows:

1.	Descriptive Data:

a.	Catalog cuts or data sheets on and specific restraints detailing compliance with the specification.

b.	Detailed schedules of flexible and rigidly mounted equipment, indicating types and configuration of seismic restraints.

2.		Shop Drawings:

Submit fabrication details for equipment bases including dimensions, structural member sizes and support point locations.

b.	Provide all details of suspension and support for ceiling hung equipment.

c. 	Where walls, floors, slabs or supplementary steel work are used for seismic restraint locations, details of acceptable attachment methods for conduit must be included and approved before the condition is accepted for installation.  Restraint manufacturers' submittals must include spacing, static loads and seismic loads at all attachment and support points.

d.	Provide specific details of seismic restraints and anchors; include number, size and locations for each piece of equipment.

3.	Seismic Certification and Analysis:

a.	Seismic restraint calculations must be provided for all connections of equipment to the structure.  Calculations must be stamped by a registered professional engineer with at least five years of seismic design experience, licensed in New Mexico.

b.	All restraining devices shall have a preapproval number from California OSHPD or some other recognized government agency showing maximum restraint ratings.  Preapprovals based on independent testing are preferred to preapprovals based on calculations.  Where preapproved devices are not available, submittals based on independent testing are preferred.  Calculations (including the combining of tensile and shear loadings) to support seismic restraint designs must be stamped by a registered professional engineer with at least five years of seismic design experience and licensed in the state of the job location.  Testing and calculations must include both shear and tensile loads as well as one test or analysis at 45E to the weakest mode.

c.	Analysis must indicate calculated dead loads, static seismic loads and capacity of materials utilized for connections to equipment and structure.  Analysis must detail anchoring methods, bolt diameter, embedment and/or welded length.  All seismic restraint devices shall be designed to accept, without failure, the forces detailed in section 1.06 acting through the equipment center of gravity.  Overturning moments may exceed forces at ground level.

1.03	CODE AND STANDARDS REQUIREMENTS

A. 		Applicable codes and Standards

1.	SMACNA, Seismic Restraint Manual: Guidelines for Mechanical Systems,  1991

2.	Uniform Building Code, 1994

1.04	MANUFACTURER’S RESPONSIBILITY

A.		Manufacturer of seismic restraint shall have the following responsibilities:

1.	Determine seismic restraint sizes and locations.

Provide seismic restraints as scheduled or specified.

Provide calculations and materials as required for seismic restraint of  isolated and unisolated equipment.

4.	Provide installation instructions, drawings and trained field supervision to insure proper installation and performance.

1.05 	RELATED WORK

A.		Supplementary Support Steel

1.	Contractor shall supply supplementary support steel for all equipment, cabletray, conduit, etc. including roof mounted equipment, as required or specified.

B.		Attachments

1.	Contractor shall supply restraint attachment plates cast into housekeeping pads, concrete inserts, double sided beam clamps, etc. in accordance with the requirements of the seismic restraint vendor's calculations.

2.	Capacity, as indicated on Structural drawings, for concrete inserts used for support attachment shall not be exceeded for the combination of gravity and seismic loads on the support.

C.	Contractor shall design restraints to permit design installation as shown on the Drawings and shall coordinate installation to aid, not hinder other contractors.Gravity support requirements specified in other sections and/or shown on drawings must be considered in combination with seismic restraint requirement in this section.  Whenever, conflicting requirements occur between this section and other section or drawing, the  most stringent shall apply.

1.06	SEISMIC FORCE  LEVELS

A. 		Seismic loads are to be based on the 1994 Uniform Building Code using the following:

Z=0.22

I=1.25

Cp (for all systems and equipment except non-rigid and flexibly supported 	equipment)=0.75

Cp (for non-rigid and flexibly supported equipment)=1.5

PART 2 - PRODUCTS

2.01 	INTENT

A. 	For the purposes of this project, failure is defined as the discontinuance of any attachment point between equipment or structure, vertical permanent deformation greater than 1/8 inch and/or horizontal permanent deformation greater than 1/4 inch.

2.02 	ACCEPTABLE MANUFACTURERS

A.  	Subject to compliance with requirements, provide seismic restraint products from any of the following:

Mason Industries, Inc.

B-Line Systems, Inc.

3.	Unistrut Corporation

4.	Grinnell Corporation

B.	Substitutions: only under provisions of Section 1600-S.

2.03	ANCHORAGE

A. 	Seismic restraints anchored to concrete shall use embedded anchor bolts, adhesive anchors, or undercut anchors.  Expansion anchors shall not be used.  Anchorage to the structural waffle slabs shall be to cold-formed embedments as shown on drawings.

PART 3 - EXECUTION

3.0l 	GENERAL

A. 	All seismic restraint systems must be installed in  strict accordance with the manufacturers written instructions and all certified submittal data.

B. 	Installation of seismic restraints must not cause any change of position of equipment,  conduit or cable trays resulting in stresses or misalignment.

C.		Coordinate work with other trades to avoid rigid contact with the building.

D. 	Any conflicts with other trades which will result in rigid contact with equipment or piping due to inadequate space or other unforeseen conditions should be brought to the architects/engineers attention prior to installation.  Corrective work necessitated by conflicts after installation shall be at the responsible contractors expense.

Bring to the architects/engineers attention any discrepancies between the specifications and the field conditions or changes required due to specific equipment selection, prior to installation.  Corrective work necessitated by discrepancies after installation shall be at the responsible contractors expense.

Correct, at no additional cost, all installations which are deemed defective in workmanship and materials at the contractors expense.

Attach hangers to joist panel points unless approved calculations indicate the attached loads are less than 150 pounds.

H. 	Provide supplementary steel where required to bridge between joists or to transmit loads to panel points.  Submit for approval Supplementary Steel Shop Drawings or sketches indicating member sizes and method of attachment.  Do not begin fabrication of the supplementary steel until approval is received.

I.		Overstressing of the building structure must not occur because of overhead support of equipment.  Contractor must submit loads to the structural engineer of record for approval.  Generally bracing may occur from:

1.		Flanges of structural beams.

2.	Upper truss cords in bar joist construction.

3.	Cast in place inserts or concrete anchors.

3.02	SEISMIC RESTRAINT OF ELECTRICAL SERVICE

A.	Transverse restraints shall occur at 30’ intervals or both ends if the electrical run is less than the specified interval.  Transverse restraints shall be installed at each electrical services turn and at each end of the electric run.

B.	Longitudinal restraints shall occur at  60’ intervals with at least one restraint per electric run.  Transverse restraints for one electric section may also as a longitudinal restraint for a duct for an electric section connected perpendicular to it if the restraints are installed within 4’ of the intersection of the electric run and if the restraints are sized for the larger electric run.

C.	All rigid floor mounted equipment must have a resilient media between the equipment mounting hole and the anchor bolt.  Anchor bolts shall be designed in accordance with Section 1.06 seismic forces.  Neoprene bushings shall be specification type 4 and anchor bolts shall be specification type 18 or 19.

3.03	SEISMIC RESTRAINT EXCLUSIONS

All conduit less than 2 1/2” diameter suspended by individual hanger rods.

B.	All clevis or trapeze supported conduits suspended by hanger rods where the point of attachment is less than 12” in length from the structure to the structural connection of the clevis or trapeze.

C.		Equipment

1.	Equipment weighing less than 50 lbs.

END OF SECTION