## Summary
Emission Factors from RICE Emissions Database 1/10/02
Assumptions:
remove not detected (<<) and not reported
all loads
greater than 500 HP
"No HAP control" selected for all pollutants excepts NOx. For NOx, "No control" selected.
| 4SRB | 4SLB | 2SLB | CI
acetaldehyde | 0.00514 | 0.0787 | 0.0934 | 0.016422
acrolein | 0.000552 | 0.0751 | 0.0923 | 2.37e-05
formaldehyde | 0.0524 | 0.688 | 0.738 | 0.019454
methanol | 0.0126 | 0.0453 | 0.0381
HAP | 0.070692 | 0.8871 | 0.9618 | 0.035901
CO | 25.1 | 5.57 | 5.19 | 0.69608
NOx | 15.5

## 4SRB-acetaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
25 | 25.4 | Naval Petroleum Reserve #1 | CARB 430 | Elk Hills, CA | Naval Petroleum Reserve #1/Elk Hills, CA | Petro Chem Environmental Services Inc. | 1992-02-06 | 1500 | HP | 70 | Waukesha | L7042 GSIU | Waukesha/L7042 GSIU/1500 MW / 70% | Natural Gas | NR | Acetaldehyde | ND | 276 | ND | 98.6666666666667 | 98.7 | 20.0 | 3 | 10 | 276 | 10 | .000175 | .00482 | .000175 | .00172 | .0000187 | .000521 | .0000191 | .000186 | .000000167 | .00000459 | .000000167 | .00000164 | ppb | PCC | Test reported 1/2 DL as concentrations. Corrected to ND with full DL | 9.8 | 9.9 | 10 | NR | Engine Type Information Updated. Glen Slitor, San Joaquin Valley Air Pollution Control | 68 | F | NR | Btu/dscf | 2553 | 2553 | 2553 | 44 |  |  |  | 3 | 2 | 3 | 70 | 4SRB | Turbo Charged | 12 | 8710 | 2 | 1500 | ND | 148 | ND | 56
29 | 29.29x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-24 | 896 | HP | 52 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 52% | Natural Gas | Gas Transmission | Acetaldehyde | 2650 | NR | NR | 2650 | 2650 | 7180 | 3 | 2650 | NR | NR | .00856 | NR | NR | .00856 | .00261 | NR | NR | .00261 | .0000184 | NR | NR | .0000184 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1013 | Btu/scf | 472 | NR | NR | 44 | .205 | NR | NR | 1 | 0 | 1 | 52 | 4SRB | NR | 12 | 8470 | 1 | 896 | 763 | NR | NR | 763

## 4SRB-acrolein
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
25 | 25.4 | Naval Petroleum Reserve #1 | CARB 430 | Elk Hills, CA | Naval Petroleum Reserve #1/Elk Hills, CA | Petro Chem Environmental Services Inc. | 1992-02-06 | 1500 | HP | 70 | Waukesha | L7042 GSIU | Waukesha/L7042 GSIU/1500 MW / 70% | Natural Gas | NR | Acrolein | ND | 57.9 | ND | 24.7933333333333 | 24.8 | 16.48 | 3 | 8.24 | 57.9 | 8.24 | .000183 | .00129 | .000183 | .000552 | .0000196 | .000139 | .00002 | .0000595 | .000000174 | .00000123 | .000000174 | .000000526 | ppb | PCC | Test reported 1/2 DL as concentrations. Corrected to ND with full DL | 9.8 | 9.9 | 10 | NR | Engine Type Information Updated. Glen Slitor, San Joaquin Valley Air Pollution Control | 68 | F | NR | Btu/dscf | 2553 | 2553 | 2553 | 56 |  |  |  | 3 | 2 | 3 | 70 | 4SRB | Turbo Charged | 12 | 8710 | 2 | 1500 | ND | 31.1 | ND | 15.86

## 4SRB-formaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
25 | 25.3 | Naval Petroleum Reserve #1 | CARB 430 | Elk Hills, CA | Naval Petroleum Reserve #1/Elk Hills, CA | Petro Chem Environmental Services Inc. | 1992-02-13 | 1000 | HP | 95 | Waukesha | L7042 GS1 | Waukesha/L7042 GS1/1000 MW / 95% | Natural Gas | NR | Formaldehyde | ND | 58.7 | 37.0 | 35.4666666666667 | 35.5 | 21.4 | 3 | 10.7 | 58.7 | 37.0 | .000116 | .000634 | .000399 | .000383 | .0000118 | .0000655 | .0000406 | .0000393 | .000000122 | .000000667 | .00000042 | .000000403 | ppb | PSC | Test reported 1/2 DL as concentrations. Corrected to ND with full DL | 8.0 | 8.2 | 8.0 | NR |  | 68 | F | NR | Btu/dscf | 2313 | 2313 | 2313 | 30 |  |  |  | 3 | 1 | 7 | 95 | 4SRB | Turbo Intercooled | 12 | 8710 | 2 | 1000 | ND | 27.3 | 16.9 | 18.3
25 | 25.4 | Naval Petroleum Reserve #1 | CARB 430 | Elk Hills, CA | Naval Petroleum Reserve #1/Elk Hills, CA | Petro Chem Environmental Services Inc. | 1992-02-06 | 1500 | HP | 70 | Waukesha | L7042 GSIU | Waukesha/L7042 GSIU/1500 MW / 70% | Natural Gas | NR | Formaldehyde | ND | 117.6 | 56.7 | 60.6333333333333 | 60.6 | 15.2 | 3 | 7.6 | 117.6 | 56.7 | .0000906 | .0014 | .000676 | .000722 | .0000097 | .000151 | .0000737 | .0000781 | .0000000863 | .00000133 | .000000644 | .000000687 | ppb | PCC | Test reported 1/2 DL as concentrations. Corrected to ND with full DL | 9.8 | 9.9 | 10 | NR | Engine Type Information Updated. Glen Slitor, San Joaquin Valley Air Pollution Control | 68 | F | NR | Btu/dscf | 2553 | 2553 | 2553 | 30 |  |  |  | 3 | 1 | 3 | 70 | 4SRB | Turbo Charged | 12 | 8710 | 2 | 1500 | ND | 63.1 | 30.7 | 33.8
29 | 29.28x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-23 | 896 | HP | 88 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 88% | Natural Gas | Gas Transmission | Formaldehyde | 22900 | NR | NR | 22900 | 22900 | 1460 | 3 | 22900 | NR | NR | .0765 | NR | NR | .0765 | .0154 | NR | NR | .0154 | .000097 | NR | NR | .000097 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 716 | NR | NR | 30 | .207 | NR | NR | 1 | 0 | 1 | 88 | 4SRB | NR | 12 | 8499 | 1 | 896 | 6590 | NR | NR | 6590
29 | 29.29x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-24 | 896 | HP | 52 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 52% | Natural Gas | Gas Transmission | Formaldehyde | 24300 | NR | NR | 24300 | 24300 | 1460 | 3 | 24300 | NR | NR | .0535 | NR | NR | .0535 | .0163 | NR | NR | .0163 | .000115 | NR | NR | .000115 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1013 | Btu/scf | 472 | NR | NR | 30 | .205 | NR | NR | 1 | 0 | 1 | 52 | 4SRB | NR | 12 | 8470 | 1 | 896 | 6990 | NR | NR | 6990
3 | 3.16 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 650 | HP | 100 | Dresser-Rand | LVG-8 | Dresser-Rand/LVG-8/650 MW / 100% | Natural Gas | NR | Formaldehyde | 7200 | 7200 | 7200 | 7200 | 7200 | NA | 3 | 7200 | 7200 | 7200 | .131 | .131 | .131 | .131 | .00495 | .00495 | .00495 | .00495 | .000202 | .000202 | .000202 | .000202 | ppb | NR | #E | 0.3 | 0.3 | 0.3 | NR | #E. Tested @ NSCR inlet | 68 | F | NR | Btu/dscf | 3884.165 | 3884.165 | 3884.165 | 30 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8710 | 2 | 650 | 2060 | 2060 | 2060 | 2060

## 4SRB-methanol
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
29 | 29.28x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-23 | 896 | HP | 88 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 88% | Natural Gas | Gas Transmission | Methanol | 4250 | NR | NR | 4250 | 4250 | NA | 3 | 4250 | NR | NR | .0151 | NR | NR | .0151 | .00306 | NR | NR | .00306 | .0000192 | NR | NR | .0000192 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 716 | NR | NR | 32 | .207 | NR | NR | 1 | 0 | 1 | 88 | 4SRB | NR | 12 | 8499 | 1 | 896 | 1220 | NR | NR | 1220
29 | 29.29x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-24 | 896 | HP | 52 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 52% | Natural Gas | Gas Transmission | Methanol | 4260 | NR | NR | 4260 | 4260 | NA | 3 | 4260 | NR | NR | .01 | NR | NR | .01 | .00305 | NR | NR | .00305 | .0000215 | NR | NR | .0000215 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1013 | Btu/scf | 472 | NR | NR | 32 | .205 | NR | NR | 1 | 0 | 1 | 52 | 4SRB | NR | 12 | 8470 | 1 | 896 | 1230 | NR | NR | 1230

## 4SRB-CO
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
101 | 101 | Philips Petroleum Company, Lake Washington Central Battery | EPA 3A | Portsulphur, P.O. Box 51107, Lafayette, LA 70505 | Philips Petroleum Company, Lake Washington Central Battery/Portsulphur, P.O. Box 51107, Lafayette, LA 70505 | Environmental Science & Engineering Inc. | 1992-10-27 | 550 | HP | 100 | Waukesha | L5108G | Waukesha/L5108G/550 MW / 100% | Natural Gas | NR | CO | 584290 | 577060 | 575160 | 578836.666666667 | 579000 | NA | 3 | 584290 | 577060 | 575160 | 1.67 | 1.83 | 1.64 | 1.71 | .54 | .541 | .594 | .558 | .00304 | .00333 | .00298 | .00312 | ppb | PCC |  | 6.6 | 6.8 | 8.1 | NR | PCC assumed because NOx are one order of magnitude lower than the rest of the gathered data 3/99 | 68 | F | 1175.9 | Btu/dscf | 656.7 | 726.6 | 654.0 | 28 |  |  |  | 3 | 0 | 3 | 100 | 4SRB | NR | 12 | 8710 | 0 | 550 | 241000 | 241000 | 265000 | 249000
102 | 102.1 | Becktel Petroleum Operations Inc. - Elk Hills Naval Petroleum Reserve No. 1 | EPA method 10 | Tupman, CA | Becktel Petroleum Operations Inc. - Elk Hills Naval Petroleum Reserve No. 1/Tupman, CA | Petro Chem Environmental Services Inc. | 1993-05-25 | 1500 | HP | 66 | Waukesha | L7042 GSIU | Waukesha/L7042 GSIU/1500 MW / 66% | Natural Gas | NR | CO | 482000 | 463000 | 472000 | 472333.333333333 | 472000 | NA | 3 | 482000 | 463000 | 472000 | 5.64 | 5.29 | 5.47 | 5.47 | .628 | .59 | .619 | .612 | .0057 | .00534 | .00553 | .00552 | ppb | PCC for NOx control | Report has SO2 emissions calculated based on values for H2S | 10.81 | 10.58 | 10.87 | NR | Report has SO2 emissions calculated based on values for H2S | 60 | F | 1100 | Btu/dscf | 2644 | 2585 | 2619 | 28 |  |  |  | 3 | 0 | 3 | 66 | 4SRB | NR | NR | 8527 | 0 | 1500 | 282000 | 265000 | 278000 | 275000
102 | 102.2 | Becktel Petroleum Operations Inc. - Elk Hills Naval Petroleum Reserve No. 1 | EPA method 10 | Tupman, Ca | Becktel Petroleum Operations Inc. - Elk Hills Naval Petroleum Reserve No. 1/Tupman, Ca | Petro Chem Environmental Services Inc. | 1993-07-22 | 1500 | HP | 63 | Waukesha | L7042 GSIU | Waukesha/L7042 GSIU/1500 MW / 63% | Natural Gas | NR | CO | 585000 | 591000 | 602000 | 592666.666666667 | 593000 | NA | 3 | 585000 | 591000 | 602000 | 6.11 | 6.48 | 6.41 | 6.33 | .745 | .753 | .772 | .757 | .00647 | .00686 | .00678 | .0067 | ppb | PCC for NOx control | Report has SO2 emissions calculated based on values for H2S | 10.51 | 10.52 | 10.59 | NR | Report has SO2 emissions calculated based on values for H2S | 68 | F | 1101 | Btu/dscf | 2398 | 2518 | 2443 | 28 |  |  |  | 3 | 0 | 3 | 63 | 4SRB | NR | NR | 8710 | 0 | 1500 | 332000 | 336000 | 345000 | 337666.666666667
120 | 120 | UNOCAL - Coalinga Station Pipeline Facility | CARB 1-100 | P.O. Box 661, San Luis Obispo, CA 93406 | UNOCAL - Coalinga Station Pipeline Facility/P.O. Box 661, San Luis Obispo, CA 93406 | BTC Environmental Inc. | 1991-06-21 | 765 | HP | 88 | Enterprise | GSG-8 | Enterprise/GSG-8/765 MW / 88% | Natural Gas | NR | CO | 10491000 | 10543000 | 10161000 | 10398333.3333333 | 10400000 | NA | 3 | 10491000 | 10543000 | 10161000 | 66.6 | 67 | 64.5 | 66 | 6.54 | 6.58 | 6.34 | 6.49 | .0989 | .0995 | .0958 | .0981 | ppb | NR | Engine # 1 | 0.2 | 0.2 | 0.2 | NR | Engine # 1 | 68 | F | 999 | Btu/dscf | 1458 | 1458 | 1458 | 28 |  |  |  | 3 | 0 | 1 | 88 | 4SRB | NR | NR | 8503 | 0 | 765 | 2990000 | 3010000 | 2900000 | 2966666.66666667
133 | 133 | Becktel Petroleum Operations Inc - Elk Hills Naval Petroleum Reserve No. 1 | EPA 10 | 28590 Highway 119, Tupman, CA 93276 | Becktel Petroleum Operations Inc - Elk Hills Naval Petroleum Reserve No. 1/28590 Highway 119, Tupman, CA 93276 | Petro Chem Environmental Services Inc. | 1993-05-26 | 1500 | HP | 67 | Waukesha | L7042 GSIU | Waukesha/L7042 GSIU/1500 MW / 67% | Natural Gas | NR | CO | 24300 | 25500 | 24200 | 24666.6666666667 | 24700 | NA | 3 | 24300 | 25500 | 24200 | .198 | .211 | .202 | .204 | .0289 | .031 | .0295 | .0298 | .000197 | .00021 | .000201 | .000203 | ppb | PCC |  | 9.77 | 10.03 | 10.06 | NR |  | 68 | F | 1108 | Btu/dscf | 1871 | 1903 | 1921 | 28 |  |  |  | 3 | 0 | 3 | 67 | 4SRB | NR | NR | 8710 | 0 | 1500 | 12900 | 13800 | 13200 | 13300
141 | 141 | CNG Transmission Corporation, State Line Station | EPA 3A | Genesse Township, PA | CNG Transmission Corporation, State Line Station/Genesse Township, PA | Emission Testing Services Inc. | 1990-06-13 | 1100 | HP | 94.98 | Ingersoll Rand | KVG-104 | Ingersoll Rand/KVG-104/1100 MW / 94.98% | Natural Gas | NR | CO | 191580 | 192980 | 19526 | 134695.333333333 | 135000 | NA | 3 | 191580 | 192980 | 19526 | 2.01 | 1.96 | .197 | 1.39 | .176 | .176 | .0178 | .123 | .00192 | .00188 | .000189 | .00133 | ppb | PCC |  | 6.47 | 6.42 | 6.36 | 1044.74 | PCC assumed because NOx emissions are one order ofmagnitue lower than the remaining data. | 68 | F | NR | NR | 2406.6 | 2325.8 | 2315.7 | 28 |  |  |  | 3 | 0 | 3 | 94.98 | 4SRB | NR | NR | 8710 | 0 | 1100 | 78300 | 78600 | 7920 | 54940
146 | 146 | City of Tulare Sewage Treatment Plant | CARB 1-100 | 411 East Kern Avenue, Tulare, CA 93274 | City of Tulare Sewage Treatment Plant/411 East Kern Avenue, Tulare, CA 93274 | Steiner Environmental Inc. | 1993-08-06 | 670 | HP | 96 | Waukesha | L5108GC | Waukesha/L5108GC/670 MW / 96% | Process Gas | NR | CO | 249730 | 279610 | NR | 264670 | 265000 | NA | 3 | 249730 | 279610 | NR | 1.17 | 1.32 | NR | 1.25 | NR | NR | NR | NR | .00182 | .00205 | NR | .00194 | ppb | NR |  | 7.94 | 8.03 | NR | NR |  | 60 | F | 759 | Btu/dscf | 1060.87 | 1068.29 | NR | 28 |  |  |  | 2 | 0 | 1 | 96 | 4SRB | NR | NR | NR | 0 | 670 | 114000 | 128000 | NR | 121000
151 | 151.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 5323760 | 5276230 | 5257950 | 5285980 | 5290000 | NA | 3 | 5323760 | 5276230 | 5257950 | 22.9 | 22.3 | 22.2 | 22.5 | 3.28 | 3.25 | 3.24 | 3.26 | .0347 | .0338 | .0336 | .034 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in automatic mode | 0.03 | 0.05 | 0.07 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1044 | Btu/dscf | 987.07 | 969.56 | 968.3 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.16 | 0 | 660 | 1510000 | 1490000 | 1490000 | 1496666.66666667
151 | 151.11.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 5431070 | NR | NR | 5431070 | 5430000 | NA | 3 | 5431070 | NR | NR | 22.4 | NR | NR | 22.4 | 3.36 | NR | NR | 3.36 | .0339 | NR | NR | .0339 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.06 | 0.05 | 0.05 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1073 | Btu/dscf | 945.25 | 944.8 | 944.8 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 1540000 | NR | NR | 1540000
151 | 151.11.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 13162350 | NR | NR | 13162350 | 13200000 | NA | 3 | 13162350 | NR | NR | 54.2 | NR | NR | 54.2 | 8.14 | NR | NR | 8.14 | .0821 | NR | NR | .0821 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.06 | 0.05 | 0.05 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1073 | Btu/dscf | 945.25 | 944.8 | 944.8 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 3730000 | NR | NR | 3730000
151 | 151.11.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 9337250 | NR | NR | 9337250 | 9340000 | NA | 3 | 9337250 | NR | NR | 38.4 | NR | NR | 38.4 | 5.78 | NR | NR | 5.78 | .0582 | NR | NR | .0582 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.06 | 0.05 | 0.05 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1073 | Btu/dscf | 945.25 | 944.8 | 944.8 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 2640000 | NR | NR | 2640000
151 | 151.13 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 6361720 | 6136230 | 6036240 | 6178063.33333333 | 6180000 | NA | 3 | 6361720 | 6136230 | 6036240 | 28.4 | 27 | 25.6 | 27 | 3.96 | 3.82 | 3.76 | 3.85 | .0437 | .0415 | .0394 | .0415 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in automatic mode | 0.23 | 0.23 | 0.23 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1048 | Btu/dscf | 1024.72 | 1011.12 | 972.16 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 1820000 | 1750000 | 1720000 | 1763333.33333333
151 | 151.15.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 5141620 | NR | NR | 5141620 | 5140000 | NA | 3 | 5141620 | NR | NR | 21.8 | NR | NR | 21.8 | 3.21 | NR | NR | 3.21 | .0335 | NR | NR | .0335 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.3 | 0.09 | 0.16 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1048 | Btu/dscf | 975.46 | 965.62 | 968.88 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 1470000 | NR | NR | 1470000
151 | 151.15.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 13894230 | NR | NR | 13894230 | 13900000 | NA | 3 | 13894230 | NR | NR | 59 | NR | NR | 59 | 8.68 | NR | NR | 8.68 | .0908 | NR | NR | .0908 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.3 | 0.09 | 0.16 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1048 | Btu/dscf | 975.46 | 965.62 | 968.88 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 3980000 | NR | NR | 3980000
151 | 151.15.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 6463050 | NR | NR | 6463050 | 6460000 | NA | 3 | 6463050 | NR | NR | 27.5 | NR | NR | 27.5 | 4.04 | NR | NR | 4.04 | .0423 | NR | NR | .0423 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.3 | 0.09 | 0.16 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1048 | Btu/dscf | 975.46 | 965.62 | 968.88 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 1850000 | NR | NR | 1850000
151 | 151.17 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 8325050 | 8326520 | 9001240 | 8550936.66666667 | 8550000 | NA | 3 | 8325050 | 8326520 | 9001240 | 34.1 | 34.4 | 37.1 | 35.2 | 5.2 | 5.2 | 5.63 | 5.34 | .0525 | .0529 | .0571 | .0542 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in automatic mode | 0.29 | 0.3 | 0.34 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1048 | Btu/dscf | 941.45 | 948.68 | 945.16 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 2380000 | 2380000 | 2580000 | 2446666.66666667
151 | 151.19.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 8120000 | NR | NR | 8120000 | 8120000 | NA | 3 | 8120000 | NR | NR | 33.5 | NR | NR | 33.5 | 5.1 | NR | NR | 5.1 | .0515 | NR | NR | .0515 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.4 | 0.26 | 0.33 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1048 | Btu/dscf | 947.93 | 941.5 | 944.7 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 2340000 | NR | NR | 2340000
151 | 151.19.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 11000000 | NR | NR | 11000000 | 11000000 | NA | 3 | 11000000 | NR | NR | 45.4 | NR | NR | 45.4 | 6.9 | NR | NR | 6.9 | .0698 | NR | NR | .0698 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.4 | 0.26 | 0.33 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1048 | Btu/dscf | 947.93 | 941.5 | 944.7 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 3170000 | NR | NR | 3170000
151 | 151.19.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 9750000 | NR | NR | 9750000 | 9750000 | NA | 3 | 9750000 | NR | NR | 40.3 | NR | NR | 40.3 | 6.12 | NR | NR | 6.12 | .062 | NR | NR | .062 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.4 | 0.26 | 0.33 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1048 | Btu/dscf | 947.93 | 941.5 | 944.7 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 2810000 | NR | NR | 2810000
151 | 151.21 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 4864480 | 4848770 | 4722500 | 4811916.66666667 | 4810000 | NA | 3 | 4864480 | 4848770 | 4722500 | 20.6 | 20.1 | 19.7 | 20.1 | 3.02 | 3.01 | 2.93 | 2.99 | .0317 | .0309 | .0303 | .031 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in automatic mode | 0.21 | 0.2 | 0.18 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1042 | Btu/dscf | 971.01 | 951.55 | 956.73 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 1390000 | 1380000 | 1340000 | 1370000
151 | 151.23.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 4150850 | NR | NR | 4150850 | 4150000 | NA | 3 | 4150850 | NR | NR | 17.3 | NR | NR | 17.3 | 2.57 | NR | NR | 2.57 | .0266 | NR | NR | .0266 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.17 | 0.09 | 0.14 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1042 | Btu/dscf | 956.27 | 952.59 | 954.89 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 1180000 | NR | NR | 1180000
151 | 151.23.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 9135630 | NR | NR | 9135630 | 9140000 | NA | 3 | 9135630 | NR | NR | 38.1 | NR | NR | 38.1 | 5.67 | NR | NR | 5.67 | .0586 | NR | NR | .0586 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.17 | 0.09 | 0.14 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1042 | Btu/dscf | 956.27 | 952.59 | 954.89 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 2600000 | NR | NR | 2600000
151 | 151.23.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 5455610 | NR | NR | 5455610 | 5460000 | NA | 3 | 5455610 | NR | NR | 22.7 | NR | NR | 22.7 | 3.38 | NR | NR | 3.38 | .0349 | NR | NR | .0349 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.17 | 0.09 | 0.14 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1042 | Btu/dscf | 956.27 | 952.59 | 954.89 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 1550000 | NR | NR | 1550000
151 | 151.25 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 7015040 | 6978670 | 6820000 | 6937903.33333333 | 6940000 | NA | 3 | 7015040 | 6978670 | 6820000 | 30.9 | 30.9 | 29.4 | 30.4 | 4.43 | 4.4 | 4.31 | 4.38 | .0475 | .0475 | .0452 | .0467 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in automatic mode | 0.55 | 0.52 | 0.54 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1042 | Btu/dscf | 1012.16 | 1017.26 | 988.35 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 2030000 | 2020000 | 1980000 | 2010000
151 | 151.27.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 6300000 | NR | NR | 6300000 | 6300000 | NA | 3 | 6300000 | NR | NR | 27.1 | NR | NR | 27.1 | 3.98 | NR | NR | 3.98 | .0417 | NR | NR | .0417 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.52 | 0.45 | 0.52 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1042 | Btu/dscf | 987.38 | 984.00 | 987.38 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 1820000 | NR | NR | 1820000
151 | 151.27.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 10000000 | NR | NR | 10000000 | 10000000 | NA | 3 | 10000000 | NR | NR | 43 | NR | NR | 43 | 6.31 | NR | NR | 6.31 | .0662 | NR | NR | .0662 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.52 | 0.45 | 0.52 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1042 | Btu/dscf | 987.38 | 984.00 | 987.38 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 2890000 | NR | NR | 2890000
151 | 151.27.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | CO | 6770000 | NR | NR | 6770000 | 6770000 | NA | 3 | 6770000 | NR | NR | 29.1 | NR | NR | 29.1 | 4.27 | NR | NR | 4.27 | .0448 | NR | NR | .0448 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.52 | 0.45 | 0.52 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1042 | Btu/dscf | 987.38 | 984.00 | 987.38 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 1960000 | NR | NR | 1960000
151 | 151.3.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 4900370 | NR | NR | 4900370 | 4900000 | NA | 3 | 4900370 | NR | NR | 20.7 | NR | NR | 20.7 | 3.02 | NR | NR | 3.02 | .0314 | NR | NR | .0314 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.08 | 0.06 | 0.06 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1044 | Btu/dscf | 969.23 | 968.3 | 968.3 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.18 | 0 | 660 | 1390000 | NR | NR | 1390000
151 | 151.3.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 6102600 | NR | NR | 6102600 | 6100000 | NA | 3 | 6102600 | NR | NR | 25.8 | NR | NR | 25.8 | 3.77 | NR | NR | 3.77 | .0391 | NR | NR | .0391 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.08 | 0.06 | 0.06 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1044 | Btu/dscf | 969.23 | 968.3 | 968.3 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.18 | 0 | 660 | 1730000 | NR | NR | 1730000
151 | 151.3.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 5252590 | NR | NR | 5252590 | 5250000 | NA | 3 | 5252590 | NR | NR | 22.2 | NR | NR | 22.2 | 3.24 | NR | NR | 3.24 | .0336 | NR | NR | .0336 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.08 | 0.06 | 0.06 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1044 | Btu/dscf | 969.23 | 968.3 | 968.3 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.18 | 0 | 660 | 1490000 | NR | NR | 1490000
151 | 151.5 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 3675000 | 3720000 | 3872090 | 3755696.66666667 | 3760000 | NA | 3 | 3675000 | 3720000 | 3872090 | 15.7 | 15.4 | 15.6 | 15.6 | 2.27 | 2.3 | 2.4 | 2.32 | .0238 | .0233 | .0236 | .0236 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in automatic mode | 0.03 | 0.08 | 0.07 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1073 | Btu/dscf | 982.55 | 947.99 | 927.49 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 1040000 | 1050000 | 1100000 | 1063333.33333333
151 | 151.7.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 3696110 | NR | NR | 3696110 | 3700000 | NA | 3 | 3696110 | NR | NR | 14.9 | NR | NR | 14.9 | 2.29 | NR | NR | 2.29 | .0226 | NR | NR | .0226 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.06 | 0.05 | 0.06 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1073 | Btu/dscf | 927.05 | 926.6 | 927.05 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 1050000 | NR | NR | 1050000
151 | 151.7.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 2208910 | NR | NR | 2208910 | 2210000 | NA | 3 | 2208910 | NR | NR | 8.92 | NR | NR | 8.92 | 1.37 | NR | NR | 1.37 | .0135 | NR | NR | .0135 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.06 | 0.05 | 0.06 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, maxiumum | 68 | F | 1073 | Btu/dscf | 927.05 | 926.6 | 927.05 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 625000 | NR | NR | 625000
151 | 151.7.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 4558420 | NR | NR | 4558420 | 4560000 | NA | 3 | 4558420 | NR | NR | 18.4 | NR | NR | 18.4 | 2.82 | NR | NR | 2.82 | .0279 | NR | NR | .0279 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.06 | 0.05 | 0.06 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1073 | Btu/dscf | 927.05 | 926.6 | 927.05 | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 1290000 | NR | NR | 1290000
151 | 151.9 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | CO | 5644990 | 5507300 | 5655400 | 5602563.33333333 | 5600000 | NA | 3 | 5644990 | 5507300 | 5655400 | 23.2 | 22.8 | 23.3 | 23.1 | 3.49 | 3.41 | 3.5 | 3.47 | .0352 | .0345 | .0353 | .035 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in automatic mode | 0.05 | 0.06 | 0.07 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1073 | Btu/dscf | 945.36 | 950.45 | 945.7 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 1600000 | 1560000 | 1600000 | 1586666.66666667
160 | 160.1.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | CO | 3897000 | 3869000 | 3863000 | 3876333.33333333 | 3880000 | NA | 3 | 3897000 | 3869000 | 3863000 | 31.1 | 30.9 | 30.9 | 31 | 2.47 | 2.45 | 2.45 | 2.46 | .0232 | .023 | .023 | .0231 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | North Site, Engine # 2, Inlet to converter | 0.01 | 0.01 | 0.01 | NR | North Site, Engine # 2, Inlet to converter | 68 | F | NR | NR | 1834 | 1834 | 1834 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 1100000 | 1090000 | 1090000 | 1093333.33333333
160 | 160.2.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | CO | 4174000 | 4218000 | 4422000 | 4271333.33333333 | 4270000 | NA | 3 | 4174000 | 4218000 | 4422000 | 32.2 | 32.5 | 34.1 | 32.9 | 2.67 | 2.7 | 2.83 | 2.73 | .024 | .0242 | .0254 | .0245 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | Inlet Concentration | 0.21 | 0.22 | 0.23 | NR | South Site, Engine # 1, Inlet to converter | 68 | F | NR | NR | 1770 | 1770 | 1770 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 1190000 | 1200000 | 1260000 | 1216666.66666667
160 | 160.3.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | CO | 3985000 | 3986000 | 4000000 | 3990333.33333333 | 3990000 | NA | 3 | 3985000 | 3986000 | 4000000 | 31.2 | 31.2 | 31.3 | 31.2 | 2.54 | 2.54 | 2.55 | 2.54 | .0233 | .0233 | .0233 | .0233 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | Inlet Concentration | 0.17 | 0.18 | 0.17 | NR | South Site, Engine # 2, Inlet to converter | 68 | F | NR | NR | 1797 | 1797 | 1797 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 1130000 | 1140000 | 1140000 | 1136666.66666667
160 | 160.4.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | CO | 3594000 | 3547000 | 3558000 | 3566333.33333333 | 3570000 | NA | 3 | 3594000 | 3547000 | 3558000 | 28.2 | 27.8 | 27.9 | 28 | 2.28 | 2.25 | 2.25 | 2.26 | .021 | .0207 | .0208 | .0208 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | Inlet Concentration | 0.01 | 0.01 | 0.01 | NR | North Site, Engine # 1, Inlet to converter | 68 | F | NR | NR | 1802 | 1802 | 1802 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 1020000 | 1000000 | 1000000 | 1006666.66666667
29 | 29.28x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-23 | 896 | HP | 88 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 88% | Natural Gas | Gas Transmission | CO | 3714000 | NR | NR | 3714000 | 3710000 | NA | 3 | 3714000 | NR | NR | 11.6 | NR | NR | 11.6 | 2.34 | NR | NR | 2.34 | .0147 | NR | NR | .0147 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 716 | NR | NR | 28 | .207 | NR | NR | 1 | 0 | 1 | 88 | 4SRB | NR | 12 | 8499 | 1 | 896 | 1070000 | NR | NR | 1070000
29 | 29.29x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-24 | 896 | HP | 52 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 52% | Natural Gas | Gas Transmission | CO | 2690000 | NR | NR | 2690000 | 2690000 | NA | 3 | 2690000 | NR | NR | 5.53 | NR | NR | 5.53 | 1.69 | NR | NR | 1.69 | .0119 | NR | NR | .0119 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1013 | Btu/scf | 472 | NR | NR | 28 | .205 | NR | NR | 1 | 0 | 1 | 52 | 4SRB | NR | 12 | 8470 | 1 | 896 | 774000 | NR | NR | 774000

## 4SRB-NOx
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
151 | 151.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1715050 | 1905130 | 1949440 | 1856540 | 1860000 | NA | 3 | 1715050 | 1905130 | 1949440 | 12.1 | 13.2 | 13.5 | 12.9 | 1.73 | 1.93 | 1.98 | 1.88 | .0183 | .02 | .0205 | .0196 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in automatic mode | 0.03 | 0.05 | 0.07 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1044 | Btu/dscf | 987.07 | 969.56 | 968.3 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.16 | 0 | 660 | 485000 | 539000 | 552000 | 525333.333333333
151 | 151.11.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1852240 | NR | NR | 1852240 | 1850000 | NA | 3 | 1852240 | NR | NR | 12.5 | NR | NR | 12.5 | 1.88 | NR | NR | 1.88 | .0189 | NR | NR | .0189 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.06 | 0.05 | 0.05 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1073 | Btu/dscf | 945.25 | 944.8 | 944.8 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 524000 | NR | NR | 524000
108 | 108.1.1 | Southern California Gas Company - Goleta Station | CARB method 1-100 | California | Southern California Gas Company - Goleta Station/California | Pape & Steiner Environmental Services | 1990-08-28 | 650 | HP | 87 | Ingersoll Rand | LVG-8 | Ingersoll Rand/LVG-8/650 MW / 87% | Natural Gas | NR | NOx | 1613000 | 1672000 | 1735000 | 1673333.33333333 | 1670000 | NA | 3 | 1613000 | 1672000 | 1735000 | 13.7 | 12.5 | 14.6 | 13.6 | 1.68 | 1.74 | 1.81 | 1.74 | .0242 | .0221 | .0258 | .024 | ppb | Inlet of Englehard Catalytic Converter for NOx control | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 0.24 | 0.19 | 0.24 | NR | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 68 | F | 1113 | Btu/dscf | 1182.73 | 1043.79 | 1177.01 | 46 |  |  |  | 3 | 0 | 1 | 87 | 4SRB | NR | 8 | 8640.44 | 0 | 650 | 461000 | 476000 | 495000 | 477333.333333333
108 | 108.2.1 | Southern California Gas Company - Goleta Station | CARB method 1-100 | California | Southern California Gas Company - Goleta Station/California | Pape & Steiner Environmental Services | 1990-08-20 | 650 | HP | 86 | Ingersoll Rand | LVG-8 | Ingersoll Rand/LVG-8/650 MW / 86% | Natural Gas | NR | NOx | 2184000 | 2190000 | 2261000 | 2211666.66666667 | 2210000 | NA | 3 | 2184000 | 2190000 | 2261000 | 17.1 | 16.8 | 17.2 | 17 | 2.28 | 2.29 | 2.36 | 2.31 | .0306 | .0301 | .0308 | .0305 | ppb | Inlet of Englehard Catalytic Converter for NOx control | NOx is Inlet ConcentrationFuel Type deducted from given fuel factor and heating value | 0.31 | 0.34 | 0.30 | NR | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 68 | F | 1149 | Btu/dscf | 1093.2 | 1075.09 | 1060.59 | 46 |  |  |  | 3 | 0 | 1 | 86 | 4SRB | NR | 8 | 8626.17 | 0 | 650 | 626000 | 628000 | 648000 | 634000
108 | 108.3.1 | Southern California Gas Company - Goleta Station | CARB method 1-100 | California | Southern California Gas Company - Goleta Station/California | Pape & Steiner Environmental Services | 1990-08-21 | 650 | HP | 86 | Ingersoll Rand | LVG-8 | Ingersoll Rand/LVG-8/650 MW / 86% | Natural Gas | NR | NOx | 1996000 | 2014000 | 2084000 | 2031333.33333333 | 2030000 | NA | 3 | 1996000 | 2014000 | 2084000 | 16 | 16.1 | 17 | 16.4 | 2.11 | 2.13 | 2.2 | 2.15 | .0286 | .0288 | .0304 | .0293 | ppb | Inlet of Englehard Catalytic Converter for NOx control | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 0.46 | .42 | 0.42 | NR | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 68 | F | 1180 | Btu/dscf | 1117.21 | 1115.37 | 1141.65 | 46 |  |  |  | 3 | 0 | 1 | 86 | 4SRB | NR | 8 | 8664.5 | 0 | 650 | 576000 | 580000 | 600000 | 585333.333333333
108 | 108.4.1 | Southern California Gas Company - Goleta Station | CARB method 1-100 | California | Southern California Gas Company - Goleta Station/California | Pape & Steiner Environmental Services | 1990-08-22 | 650 | HP | 86 | Ingersoll Rand | LVG-8 | Ingersoll Rand/LVG-8/650 MW / 86% | Natural Gas | NR | NOx | 2264000 | 2296000 | 2295000 | 2285000 | 2280000 | NA | 3 | 2264000 | 2296000 | 2295000 | 16.6 | 16.8 | 16.6 | 16.7 | 2.37 | 2.41 | 2.4 | 2.39 | .0297 | .0301 | .0297 | .0298 | ppb | Inlet of Englehard Catalytic Converter for NOx control | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 0.4 | 0.4 | 0.38 | NR | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 68 | F | 1072 | Btu/dscf | 1022.79 | 1022.54 | 1009.19 | 46 |  |  |  | 3 | 0 | 1 | 86 | 4SRB | NR | 8 | 8615.9 | 0 | 650 | 652000 | 661000 | 660000 | 657666.666666667
108 | 108.5.1 | Southern California Gas Company - Goleta Station | CARB method 1-100 | California | Southern California Gas Company - Goleta Station/California | Pape & Steiner Environmental Services | 1990-08-23 | 600 | HP | 96 | Ingersoll Rand | KVG-6 | Ingersoll Rand/KVG-6/600 MW / 96% | Natural Gas | NR | NOx | 2246000 | 2274000 | 2302000 | 2274000 | 2270000 | NA | 3 | 2246000 | 2274000 | 2302000 | 17.7 | 16.7 | 16.5 | 17 | 2.34 | 2.37 | 2.4 | 2.37 | .0307 | .029 | .0286 | .0294 | ppb | Inlet of Englehard Catalytic Converter for NOx control | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 0.23 | 0.21 | 0.24 | NR | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 68 | F | 1137 | Btu/dscf | 1100.64 | 1025.43 | 999.76 | 46 |  |  |  | 3 | 0 | 1 | 96 | 4SRB | NR | 6 | 8628.51 | 0 | 600 | 641000 | 648000 | 657000 | 648666.666666667
108 | 108.6.1 | Southern California Gas Company - Goleta Station | CARB method 1-100 | California | Southern California Gas Company - Goleta Station/California | Pape & Steiner Environmental Services | 1990-08-24 | 600 | HP | 90 | Ingersoll Rand | KVG-6 | Ingersoll Rand/KVG-6/600 MW / 90% | Natural Gas | NR | NOx | 1479000 | 1537000 | 1537000 | 1517666.66666667 | 1520000 | NA | 3 | 1479000 | 1537000 | 1537000 | 11 | 11.2 | 11.3 | 11.2 | 1.54 | 1.6 | 1.6 | 1.58 | .0204 | .0207 | .0209 | .0207 | ppb | Inlet of Englehard Catalytic Converter for NOx control | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 0.2 | 0.23 | 0.22 | NR | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 68 | F | 1086 | Btu/dscf | 1034.68 | 1020.20 | 1030.77 | 46 |  |  |  | 3 | 0 | 1 | 90 | 4SRB | NR | 6 | 8641.16 | 0 | 600 | 422000 | 439000 | 439000 | 433333.333333333
108 | 108.7.1 | Southern California Gas Company - Goleta Station | CARB method 1-100 | California | Southern California Gas Company - Goleta Station/California | Pape & Steiner Environmental Services | 1990-08-27 | 600 | HP | 92.5 | Ingersoll Rand | KVG-6 | Ingersoll Rand/KVG-6/600 MW / 92.5% | Natural Gas | NR | NOx | 2490000 | 2496000 | 2548000 | 2511333.33333333 | 2510000 | NA | 3 | 2490000 | 2496000 | 2548000 | 17.6 | 16.9 | 16.9 | 17.1 | 2.58 | 2.59 | 2.64 | 2.6 | .0317 | .0305 | .0305 | .0309 | ppb | Inlet of Englehard Catalytic Converter for NOx control | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 0.17 | 0.17 | 0.2 | NR | NOx is Inlet Concentration. Fuel Type deducted from given fuel factor and heating value | 68 | F | 1026 | Btu/dscf | 987.58 | 945.36 | 925.01 | 46 |  |  |  | 3 | 0 | 1 | 92.5 | 4SRB | NR | 6 | 8612.39 | 0 | 600 | 709000 | 710000 | 726000 | 715000
120 | 120 | UNOCAL - Coalinga Station Pipeline Facility | CARB 1-100 | P.O. Box 661, San Luis Obispo, CA 93406 | UNOCAL - Coalinga Station Pipeline Facility/P.O. Box 661, San Luis Obispo, CA 93406 | BTC Environmental Inc. | 1991-06-21 | 765 | HP | 88 | Enterprise | GSG-8 | Enterprise/GSG-8/765 MW / 88% | Natural Gas | NR | NOx | 1646000 | 1621000 | 1748000 | 1671666.66666667 | 1670000 | NA | 3 | 1646000 | 1621000 | 1748000 | 17.2 | 16.9 | 18.2 | 17.4 | 1.69 | 1.66 | 1.79 | 1.71 | .0255 | .0251 | .027 | .0259 | ppb | NR | Engine # 1 | 0.2 | 0.2 | 0.2 | NR | Engine # 1 | 68 | F | 999 | Btu/dscf | 1458 | 1458 | 1458 | 46 |  |  |  | 3 | 0 | 1 | 88 | 4SRB | NR | NR | 8503 | 0 | 765 | 469000 | 462000 | 498000 | 476333.333333333
146 | 146 | City of Tulare Sewage Treatment Plant | CARB 1-100 | 411 East Kern Avenue, Tulare, CA 93274 | City of Tulare Sewage Treatment Plant/411 East Kern Avenue, Tulare, CA 93274 | Steiner Environmental Inc. | 1993-08-06 | 670 | HP | 96 | Waukesha | L5108GC | Waukesha/L5108GC/670 MW / 96% | Process Gas | NR | NOx | 86180 | 82100 | NR | 84140 | 84100 | NA | 3 | 86180 | 82100 | NR | .664 | .637 | NR | .651 | NR | NR | NR | NR | .00103 | .00099 | NR | .00101 | ppb | NR |  | 7.94 | 8.03 | NR | NR |  | 60 | F | 759 | Btu/dscf | 1060.87 | 1068.29 | NR | 46 |  |  |  | 2 | 0 | 1 | 96 | 4SRB | NR | NR | NR | 0 | 670 | 39200 | 37600 | NR | 38400
151 | 151.11.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1189320 | NR | NR | 1189320 | 1190000 | NA | 3 | 1189320 | NR | NR | 8.04 | NR | NR | 8.04 | 1.21 | NR | NR | 1.21 | .0122 | NR | NR | .0122 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.06 | 0.05 | 0.05 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1073 | Btu/dscf | 945.25 | 944.8 | 944.8 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 337000 | NR | NR | 337000
151 | 151.11.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1494040 | NR | NR | 1494040 | 1490000 | NA | 3 | 1494040 | NR | NR | 10.1 | NR | NR | 10.1 | 1.52 | NR | NR | 1.52 | .0153 | NR | NR | .0153 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.06 | 0.05 | 0.05 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1073 | Btu/dscf | 945.25 | 944.8 | 944.8 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 423000 | NR | NR | 423000
151 | 151.13 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1987420 | 2023580 | 2037470 | 2016156.66666667 | 2020000 | NA | 3 | 1987420 | 2023580 | 2037470 | 14.6 | 14.6 | 14.2 | 14.5 | 2.03 | 2.07 | 2.08 | 2.06 | .0225 | .0225 | .0218 | .0223 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in authomatic mode | 0.23 | 0.23 | 0.23 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1048 | Btu/dscf | 1024.72 | 1011.12 | 972.16 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 567000 | 578000 | 582000 | 575666.666666667
151 | 151.15.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 2194690 | NR | NR | 2194690 | 2190000 | NA | 3 | 2194690 | NR | NR | 15.3 | NR | NR | 15.3 | 2.25 | NR | NR | 2.25 | .0235 | NR | NR | .0235 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.3 | 0.09 | 0.16 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1048 | Btu/dscf | 975.46 | 965.62 | 968.88 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 629000 | NR | NR | 629000
151 | 151.15.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1240990 | NR | NR | 1240990 | 1240000 | NA | 3 | 1240990 | NR | NR | 8.66 | NR | NR | 8.66 | 1.27 | NR | NR | 1.27 | .0133 | NR | NR | .0133 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.3 | 0.09 | 0.16 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1048 | Btu/dscf | 975.46 | 965.62 | 968.88 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 355000 | NR | NR | 355000
151 | 151.15.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1956320 | NR | NR | 1956320 | 1960000 | NA | 3 | 1956320 | NR | NR | 13.7 | NR | NR | 13.7 | 2.01 | NR | NR | 2.01 | .0211 | NR | NR | .0211 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.3 | 0.09 | 0.16 | NR | Engine # 2 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1048 | Btu/dscf | 975.46 | 965.62 | 968.88 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 560000 | NR | NR | 560000
151 | 151.17 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1906610 | 1965480 | 1963310 | 1945133.33333333 | 1950000 | NA | 3 | 1906610 | 1965480 | 1963310 | 12.8 | 13.3 | 13.3 | 13.1 | 1.96 | 2.02 | 2.02 | 2 | .0197 | .0205 | .0205 | .0202 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in automatic mode | 0.29 | 0.3 | 0.34 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1048 | Btu/dscf | 941.45 | 948.68 | 945.16 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 546000 | 563000 | 563000 | 557333.333333333
151 | 151.19.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 2064170 | NR | NR | 2064170 | 2060000 | NA | 3 | 2064170 | NR | NR | 14 | NR | NR | 14 | 2.13 | NR | NR | 2.13 | .0215 | NR | NR | .0215 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.4 | 0.26 | 0.33 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1048 | Btu/dscf | 947.93 | 941.5 | 944.7 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 594000 | NR | NR | 594000
151 | 151.19.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1682960 | NR | NR | 1682960 | 1680000 | NA | 3 | 1682960 | NR | NR | 11.4 | NR | NR | 11.4 | 1.74 | NR | NR | 1.74 | .0175 | NR | NR | .0175 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.4 | 0.26 | 0.33 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1048 | Btu/dscf | 947.93 | 941.5 | 944.7 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 484000 | NR | NR | 484000
151 | 151.19.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1876210 | NR | NR | 1876210 | 1880000 | NA | 3 | 1876210 | NR | NR | 12.7 | NR | NR | 12.7 | 1.93 | NR | NR | 1.93 | .0195 | NR | NR | .0195 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.4 | 0.26 | 0.33 | NR | Engine # 4 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1048 | Btu/dscf | 947.93 | 941.5 | 944.7 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8474.22 | 0 | 650 | 540000 | NR | NR | 540000
151 | 151.21 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 2058920 | 2212540 | 2137660 | 2136373.33333333 | 2140000 | NA | 3 | 2058920 | 2212540 | 2137660 | 14.3 | 15.1 | 14.6 | 14.7 | 2.1 | 2.26 | 2.18 | 2.18 | .022 | .0232 | .0225 | .0226 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in automatic mode | 0.21 | 0.2 | 0.18 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1042 | Btu/dscf | 971.01 | 951.55 | 956.73 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 587000 | 631000 | 609000 | 609000
151 | 151.23.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 2231800 | NR | NR | 2231800 | 2230000 | NA | 3 | 2231800 | NR | NR | 15.3 | NR | NR | 15.3 | 2.27 | NR | NR | 2.27 | .0235 | NR | NR | .0235 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.17 | 0.09 | 0.14 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1042 | Btu/dscf | 956.27 | 952.59 | 954.89 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 635000 | NR | NR | 635000
151 | 151.23.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1623930 | NR | NR | 1623930 | 1620000 | NA | 3 | 1623930 | NR | NR | 11.1 | NR | NR | 11.1 | 1.66 | NR | NR | 1.66 | .0171 | NR | NR | .0171 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.17 | 0.09 | 0.14 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1042 | Btu/dscf | 956.27 | 952.59 | 954.89 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 462000 | NR | NR | 462000
151 | 151.23.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-26 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 2063330 | NR | NR | 2063330 | 2060000 | NA | 3 | 2063330 | NR | NR | 14.1 | NR | NR | 14.1 | 2.1 | NR | NR | 2.1 | .0217 | NR | NR | .0217 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.17 | 0.09 | 0.14 | NR | Engine # 3 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1042 | Btu/dscf | 956.27 | 952.59 | 954.89 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 587000 | NR | NR | 587000
151 | 151.25 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1736670 | 1718750 | 1744220 | 1733213.33333333 | 1730000 | NA | 3 | 1736670 | 1718750 | 1744220 | 12.6 | 12.5 | 12.3 | 12.5 | 1.8 | 1.78 | 1.81 | 1.8 | .0194 | .0192 | .0189 | .0192 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in automatic mode | 0.55 | 0.52 | 0.54 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1042 | Btu/dscf | 1012.16 | 1017.26 | 988.35 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 504000 | 498000 | 505000 | 502333.333333333
151 | 151.27.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1800730 | NR | NR | 1800730 | 1800000 | NA | 3 | 1800730 | NR | NR | 12.7 | NR | NR | 12.7 | 1.87 | NR | NR | 1.87 | .0195 | NR | NR | .0195 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.52 | 0.45 | 0.52 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1042 | Btu/dscf | 987.38 | 984.00 | 987.38 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 521000 | NR | NR | 521000
151 | 151.27.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1411710 | NR | NR | 1411710 | 1410000 | NA | 3 | 1411710 | NR | NR | 9.97 | NR | NR | 9.97 | 1.46 | NR | NR | 1.46 | .0153 | NR | NR | .0153 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.52 | 0.45 | 0.52 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1042 | Btu/dscf | 987.38 | 984.00 | 987.38 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 409000 | NR | NR | 409000
151 | 151.27.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-25 | 650 | HP | 100 | Ingersoll Rand | LVG-82 | Ingersoll Rand/LVG-82/650 MW / 100% | Natural Gas | NR | NOx | 1703440 | NR | NR | 1703440 | 1700000 | NA | 3 | 1703440 | NR | NR | 12 | NR | NR | 12 | 1.77 | NR | NR | 1.77 | .0185 | NR | NR | .0185 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.52 | 0.45 | 0.52 | NR | Engine # 5 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1042 | Btu/dscf | 987.38 | 984.00 | 987.38 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 8 | 8469.22 | 0 | 650 | 493000 | NR | NR | 493000
151 | 151.3.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1999190 | NR | NR | 1999190 | 2000000 | NA | 3 | 1999190 | NR | NR | 13.9 | NR | NR | 13.9 | 2.03 | NR | NR | 2.03 | .0211 | NR | NR | .0211 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.08 | 0.06 | 0.06 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1044 | Btu/dscf | 969.23 | 968.3 | 968.3 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.18 | 0 | 660 | 567000 | NR | NR | 567000
151 | 151.3.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1907690 | NR | NR | 1907690 | 1910000 | NA | 3 | 1907690 | NR | NR | 13.2 | NR | NR | 13.2 | 1.93 | NR | NR | 1.93 | .02 | NR | NR | .02 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.08 | 0.06 | 0.06 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 68 | F | 1044 | Btu/dscf | 969.23 | 968.3 | 968.3 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.18 | 0 | 660 | 541000 | NR | NR | 541000
151 | 151.3.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-23 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1876210 | NR | NR | 1876210 | 1880000 | NA | 3 | 1876210 | NR | NR | 13 | NR | NR | 13 | 1.9 | NR | NR | 1.9 | .0197 | NR | NR | .0197 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.08 | 0.06 | 0.06 | NR | Engine # 7 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1044 | Btu/dscf | 969.23 | 968.3 | 968.3 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8460.18 | 0 | 660 | 532000 | NR | NR | 532000
151 | 151.5 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 2377050 | 2280450 | 2275750 | 2311083.33333333 | 2310000 | NA | 3 | 2377050 | 2280450 | 2275750 | 16.7 | 15.5 | 15.1 | 15.8 | 2.41 | 2.32 | 2.31 | 2.35 | .0253 | .0235 | .0229 | .0239 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in automatic mode | 0.03 | 0.08 | 0.07 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1073 | Btu/dscf | 982.55 | 947.99 | 927.49 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 672000 | 646000 | 645000 | 654333.333333333
151 | 151.7.1 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 2351900 | NR | NR | 2351900 | 2350000 | NA | 3 | 2351900 | NR | NR | 15.6 | NR | NR | 15.6 | 2.39 | NR | NR | 2.39 | .0236 | NR | NR | .0236 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 0.06 | 0.05 | 0.06 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, minimum | 68 | F | 1073 | Btu/dscf | 927.05 | 926.6 | 927.05 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 666000 | NR | NR | 666000
151 | 151.7.2 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1989820 | NR | NR | 1989820 | 1990000 | NA | 3 | 1989820 | NR | NR | 13.2 | NR | NR | 13.2 | 2.02 | NR | NR | 2.02 | .02 | NR | NR | .02 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, maximum | 0.06 | 0.05 | 0.06 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, maxiumum | 68 | F | 1073 | Btu/dscf | 927.05 | 926.6 | 927.05 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 563000 | NR | NR | 563000
151 | 151.7.3 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 2208910 | NR | NR | 2208910 | 2210000 | NA | 3 | 2208910 | NR | NR | 14.7 | NR | NR | 14.7 | 2.24 | NR | NR | 2.24 | .0223 | NR | NR | .0223 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (manual control) controllers for NOx control | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, set point | 0.06 | 0.05 | 0.06 | NR | Engine # 8 Inlet, Air-to-Fuel Ratio in manual mode, set point | 68 | F | 1073 | Btu/dscf | 927.05 | 926.6 | 927.05 | 46 |  |  |  | 1 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 625000 | NR | NR | 625000
151 | 151.9 | Southern California Gas Company - Goleta Station | CARB 1-100 | P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Southern California Gas Company - Goleta Station/P.O. Box 3249, Terminal Ammex, Los Angeles, CA 90051 | Steiner Environmental Inc. | 1991-09-24 | 660 | HP | 100 | Ingersoll Rand | KVG-62 | Ingersoll Rand/KVG-62/660 MW / 100% | Natural Gas | NR | NOx | 1909480 | 1923600 | 1896250 | 1909776.66666667 | 1910000 | NA | 3 | 1909480 | 1923600 | 1896250 | 12.9 | 13.1 | 12.8 | 12.9 | 1.94 | 1.95 | 1.93 | 1.94 | .0195 | .0198 | .0194 | .0196 | ppb | Inlet of Englehard NOx Control Catalysts and Air-to-Fuel ratio (automatic control) controllers for NOx control | Engine # 6 Inlet, Air-to-Fuel Ratio in automatic mode | 0.05 | 0.06 | 0.07 | NR | Engine # 6 Inlet, Air-to-Fuel Ratio in authomatic mode | 68 | F | 1073 | Btu/dscf | 945.36 | 950.45 | 945.7 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | 6 | 8489.1 | 0 | 660 | 540000 | 545000 | 537000 | 540666.666666667
160 | 160.1.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | NOx | 3206000 | 2936000 | 3001000 | 3047666.66666667 | 3050000 | NA | 3 | 3206000 | 2936000 | 3001000 | 42.1 | 38.5 | 39.4 | 40 | 3.33 | 3.05 | 3.12 | 3.17 | .0314 | .0287 | .0294 | .0298 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | North Site, Engine # 2, Inlet to converter | 0.01 | 0.01 | 0.01 | NR | North Site, Engine # 2, Inlet to converter | 68 | F | NR | NR | 1834 | 1834 | 1834 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 905000 | 829000 | 848000 | 860666.666666667
160 | 160.2.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | NOx | 2957000 | 2904000 | 2928000 | 2929666.66666667 | 2930000 | NA | 3 | 2957000 | 2904000 | 2928000 | 37.5 | 36.8 | 37.1 | 37.1 | 3.11 | 3.05 | 3.08 | 3.08 | .028 | .0274 | .0277 | .0277 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | Inlet Concentration | 0.21 | 0.22 | 0.23 | NR | South Site, Engine # 1, Inlet to converter | 68 | F | NR | NR | 1770 | 1770 | 1770 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 843000 | 829000 | 836000 | 836000
160 | 160.3.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | NOx | 2991000 | 2956000 | 2934000 | 2960333.33333333 | 2960000 | NA | 3 | 2991000 | 2956000 | 2934000 | 38.5 | 38 | 37.7 | 38.1 | 3.13 | 3.1 | 3.08 | 3.1 | .0287 | .0283 | .0281 | .0284 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | Inlet Concentration | 0.17 | 0.18 | 0.17 | NR | South Site, Engine # 2, Inlet to converter | 68 | F | NR | NR | 1797 | 1797 | 1797 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 851000 | 842000 | 835000 | 842666.666666667
160 | 160.4.1 | TCC Inc. | CARB 100 | 5201 California Ave., Suite 290, Bakersfield, CA 93309 | TCC Inc./5201 California Ave., Suite 290, Bakersfield, CA 93309 | Western Environmental Services | 1993-08-24 | 1341 | HP | 100 | Waukesha | L7042 | Waukesha/L7042/1341 MW / 100% | Natural Gas | NR | NOx | 3053000 | 2916000 | 3240000 | 3069666.66666667 | 3070000 | NA | 3 | 3053000 | 2916000 | 3240000 | 39.4 | 37.6 | 41.8 | 39.6 | 3.18 | 3.03 | 3.37 | 3.19 | .0294 | .028 | .0312 | .0295 | ppb | Fuel Air Controller + Inlet of Catalytic Converter for NOx and CO control | Inlet Concentration | 0.01 | 0.01 | 0.01 | NR | North Site, Engine # 1, Inlet to converter | 68 | F | NR | NR | 1802 | 1802 | 1802 | 46 |  |  |  | 3 | 0 | 1 | 100 | 4SRB | NR | NR | 8710 | 0 | 1341 | 862000 | 824000 | 915000 | 867000
29 | 29.28x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-23 | 896 | HP | 88 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 88% | Natural Gas | Gas Transmission | NOx | 2843000 | NR | NR | 2843000 | 2840000 | NA | 3 | 2843000 | NR | NR | 14.6 | NR | NR | 14.6 | 2.94 | NR | NR | 2.94 | .0185 | NR | NR | .0185 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 716 | NR | NR | 46 | .207 | NR | NR | 1 | 0 | 1 | 88 | 4SRB | NR | 12 | 8499 | 1 | 896 | 818000 | NR | NR | 818000
29 | 29.29x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-24 | 896 | HP | 52 | Waukesha | L7042GU | Waukesha/L7042GU/896 MW / 52% | Natural Gas | Gas Transmission | NOx | 2542000 | NR | NR | 2542000 | 2540000 | NA | 3 | 2542000 | NR | NR | 8.59 | NR | NR | 8.59 | 2.62 | NR | NR | 2.62 | .0184 | NR | NR | .0184 | ppb | NR |  | .4 | NR | NR |  |  | 68 | F | 1013 | Btu/scf | 472 | NR | NR | 46 | .205 | NR | NR | 1 | 0 | 1 | 52 | 4SRB | NR | 12 | 8470 | 1 | 896 | 732000 | NR | NR | 732000

## 2SLB-acetaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
29 | 29.10x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | Acetaldehyde | 1540 | NR | NR | 1540 | 1540 | 4100 | 3 | 1540 | NR | NR | .0817 | NR | NR | .0817 | .00508 | NR | NR | .00508 | .0000445 | NR | NR | .0000445 | ppb | NR |  | 14.8 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7749 | NR | NR | 44 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 1490 | NR | NR | 1490
29 | 29.14x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 86 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 86% | Natural Gas | Gas Transmission | Acetaldehyde | 1710 | NR | NR | 1710 | 1710 | 2750 | 3 | 1710 | NR | NR | .0731 | NR | NR | .0731 | .00614 | NR | NR | .00614 | .0000472 | NR | NR | .0000472 | ppb | NR |  | 15.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6243 | NR | NR | 44 | .065 | NR | NR | 1 | 0 | 1 | 86 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 1800 | NR | NR | 1800
29 | 29.15x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 101 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 101% | Natural Gas | Gas Transmission | Acetaldehyde | 1920 | NR | NR | 1920 | 1920 | 2750 | 3 | 1920 | NR | NR | .083 | NR | NR | .083 | .00613 | NR | NR | .00613 | .0000457 | NR | NR | .0000457 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6312 | NR | NR | 44 | .07 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 1800 | NR | NR | 1800
29 | 29.16x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 95% | Natural Gas | Gas Transmission | Acetaldehyde | 1950 | NR | NR | 1950 | 1950 | 2750 | 3 | 1950 | NR | NR | .0871 | NR | NR | .0871 | .00654 | NR | NR | .00654 | .0000509 | NR | NR | .0000509 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6528 | NR | NR | 44 | .068 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 1920 | NR | NR | 1920
29 | 29.23x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-26 | 1800 | HP | 93 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 93% | Natural Gas | Gas Transmission | Acetaldehyde | 1640 | NR | NR | 1640 | 1640 | 6130 | 3 | 1640 | NR | NR | .0771 | NR | NR | .0771 | .00603 | NR | NR | .00603 | .0000461 | NR | NR | .0000461 | ppb | PCC Clean burn |  | 15.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6866 | NR | NR | 44 | .073 | NR | NR | 1 | 0 | 3 | 93 | 2SLB | Turbo Charged | 10 | 8471 | 1 | 1800 | 1760 | NR | NR | 1760
29 | 29.2x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 911 | HP | 100 | Clark | BA-5 | Clark/BA-5/911 MW / 100% | Natural Gas | Gas Transmission | Acetaldehyde | 2200 | NR | NR | 2200 | 2200 | 1760 | 3 | 2200 | NR | NR | .0705 | NR | NR | .0705 | .00672 | NR | NR | .00672 | .0000774 | NR | NR | .0000774 | ppb | NR |  | 14.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4679 | NR | NR | 44 | .08 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 911 | 1970 | NR | NR | 1970
29 | 29.5x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 1000 | HP | 84 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 84% | Natural Gas | Gas Transmission | Acetaldehyde | 3340 | NR | NR | 3340 | 3340 | 4810 | 3 | 3340 | NR | NR | .106 | NR | NR | .106 | .0116 | NR | NR | .0116 | .000126 | NR | NR | .000126 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4617 | NR | NR | 44 | .069 | NR | NR | 1 | 0 | 1 | 84 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 1000 | 3400 | NR | NR | 3400
29 | 29.9x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | Acetaldehyde | 1820 | NR | NR | 1820 | 1820 | 4100 | 3 | 1820 | NR | NR | .0993 | NR | NR | .0993 | .00621 | NR | NR | .00621 | .0000541 | NR | NR | .0000541 | ppb | NR |  | 15 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7972 | NR | NR | 44 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 1820 | NR | NR | 1820
3 | 3.1 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 80 | Dresser-Rand | TLA-6 | Dresser-Rand/TLA-6/2000 MW / 80% | Natural Gas | NR | Acetaldehyde | 3100 | 1300 | NR | 2200 | 2200 | NA | 3 | 3100 | 1300 | NR | .152 | .0641 | NR | .108 | .00913 | .00378 | NR | .00646 | .000095 | .0000401 | NR | .0000676 | ppb | PCC | #A | 13.84 | 13.76 | 13.72 | NR | #A | 68 | F | 1024 | Btu/dscf | 7143.83 | 7198.57 | 7226.27 | 44 |  |  |  | 2 | 0 | 3 | 80 | 2SLB | NR | 6 | 8710 | 2 | 2000 | 2590 | 1070 | NR | 1830
3 | 3.2 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 90 | Dresser-Rand | TLA-6 | Dresser-Rand/TLA-6/2000 MW / 90% | Natural Gas | NR | Acetaldehyde | 810 | NR | NR | 810 | 810 | NA | 3 | 810 | NR | NR | .0422 | NR | NR | .0422 | .00303 | NR | NR | .00303 | .0000234 | NR | NR | .0000234 | ppb | PCC | #A | 15.34 | 15.31 | 15.39 | NR | #A | 68 | F | 1022 | Btu/dscf | 7617.43 | 7617.43 | 7617.43 | 44 |  |  |  | 1 | 0 | 3 | 90 | 2SLB | NR | 8 | 8710 | 2 | 2000 | 860 | NR | NR | 860
3 | 3.3 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 100 | Dresser-Rand | TLA-6 | Dresser-Rand/TLA-6/2000 MW / 100% | Natural Gas | NR | Acetaldehyde | 2100 | 460 | 1000 | 1186.66666666667 | 1190 | NA | 3 | 2100 | 460 | 1000 | .117 | .0256 | .0565 | .0664 | .00801 | .00171 | .00373 | .00448 | .0000585 | .0000128 | .0000282 | .0000332 | ppb | PCC | #A | 15.45 | 15.32 | 15.33 | NR | #A | 68 | F | 1023 | Btu/dscf | 8152.53 | 8144.75 | 8252.47 | 44 |  |  |  | 3 | 0 | 3 | 100 | 2SLB | NR | 6 | 8710 | 2 | 2000 | 2270 | 486 | 1060 | 1272
31 | 31.12x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-16 | 796 | HP | 101 | Clark | HRA-8 | Clark/HRA-8/796 MW / 101% | Natural Gas | Compressor | Acetaldehyde | 2999 | NR | NR | 2999 | 3000 | 2214 | 3 | 2999 | NR | NR | .0677 | NR | NR | .0677 | .00881 | NR | NR | .00881 | .0000842 | NR | NR | .0000842 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14 | NR | NR | 848 | Engine 23 - Test 17. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3296 | NR | NR | 44 | 8.3 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 2560 | NR | NR | 2560
31 | 31.13x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 88 | Clark | HRA-8 | Clark/HRA-8/796 MW / 88% | Natural Gas | Compressor | Acetaldehyde | 4770 | NR | NR | 4770 | 4770 | 1762 | 3 | 4770 | NR | NR | .0993 | NR | NR | .0993 | .0126 | NR | NR | .0126 | .000142 | NR | NR | .000142 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 704 | Engine 24 - Test 10. Pre-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 3040 | NR | NR | 44 | 8.6 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 3650 | NR | NR | 3650
31 | 31.14x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 89 | Clark | HRA-8 | Clark/HRA-8/796 MW / 89% | Natural Gas | Compressor | Acetaldehyde | 5802 | NR | NR | 5802 | 5800 | 1843 | 3 | 5802 | NR | NR | .125 | NR | NR | .125 | .0153 | NR | NR | .0153 | .000176 | NR | NR | .000176 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 708 | Engine 24 - Test 11. Pre-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3151 | NR | NR | 44 | 8.3 | NR | NR | 1 | 0 | 1 | 89 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 4450 | NR | NR | 4450
31 | 31.9x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 105 | Clark | HRA-8 | Clark/HRA-8/796 MW / 105% | Natural Gas | Compressor | Acetaldehyde | 12992 | NR | NR | 12992 | 13000 | 2420 | 3 | 12992 | NR | NR | .251 | NR | NR | .251 | .0314 | NR | NR | .0314 | .0003 | NR | NR | .0003 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.5 | NR | NR | 813 | Engine 23 - Test 12. Pre-maintenance and pre-balance. | 68 | F | 1011 | Btu/scf | 2826 | NR | NR | 44 | 9.1 | NR | NR | 1 | 0 | 1 | 105 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 9130 | NR | NR | 9130
7 | 7.13 | ARCO Oil and Gas Co | CARB 430 | Bakersfield CA 93309 | ARCO Oil and Gas Co/Bakersfield CA 93309 | ENSR Consulting | 1990-07-01 | 660 | HP | 100 | Cooper Bessemer | NR | Cooper Bessemer/NR/660 MW / 100% | Natural Gas | Compressor | Acetaldehyde | 3620 | 1760 | 1500 | 2293.33333333333 | 2290 | NA | 3 | 3620 | 1760 | 1500 | .0901 | .0438 | .0374 | .0571 | .0109 | .00532 | .00453 | .00692 | .000137 | .0000664 | .0000567 | .0000867 | ppb | NR |  | 14.0 | 14.0 | 14.0 | NR |  | 68 | F | NR | Btu/dscf | 3637.7 | 3637.7 | 3637.7 | 44 |  |  |  | 3 | 0 | 1 | 100 | 2SLB | NR | NR | 8740 | 2 | 660 | 3100 | 1500 | 1280 | 1960

## 2SLB-acrolein
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
29 | 29.23x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-26 | 1800 | HP | 93 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 93% | Natural Gas | Gas Transmission | Acrolein | 1870 | NR | NR | 1870 | 1870 | 4630 | 3 | 1870 | NR | NR | .112 | NR | NR | .112 | .00875 | NR | NR | .00875 | .0000669 | NR | NR | .0000669 | ppb | PCC Clean burn |  | 15.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6866 | NR | NR | 56 | .073 | NR | NR | 1 | 0 | 3 | 93 | 2SLB | Turbo Charged | 10 | 8471 | 1 | 1800 | 2010 | NR | NR | 2010
29 | 29.24x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 95% | Natural Gas | Gas Transmission | Acrolein | 1640 | NR | NR | 1640 | 1640 | 4630 | 3 | 1640 | NR | NR | .0948 | NR | NR | .0948 | .00758 | NR | NR | .00758 | .0000554 | NR | NR | .0000554 | ppb | PCC Clean burn |  | 15.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6633 | NR | NR | 56 | .082 | NR | NR | 1 | 0 | 3 | 95 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 1730 | NR | NR | 1730
29 | 29.25x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 79 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 79% | Natural Gas | Gas Transmission | Acrolein | 2530 | NR | NR | 2530 | 2530 | 4630 | 3 | 2530 | NR | NR | .133 | NR | NR | .133 | .0121 | NR | NR | .0121 | .0000935 | NR | NR | .0000935 | ppb | PCC Clean burn |  | 15.5 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6039 | NR | NR | 56 | .08 | NR | NR | 1 | 0 | 3 | 79 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 2760 | NR | NR | 2760
29 | 29.4x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 1000 | HP | 75 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 75% | Natural Gas | Gas Transmission | Acrolein | 2250 | NR | NR | 2250 | 2250 | 3800 | 3 | 2250 | NR | NR | .0933 | NR | NR | .0933 | .0111 | NR | NR | .0111 | .000124 | NR | NR | .000124 | ppb | NR |  | 15.7 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4759 | NR | NR | 56 | .068 | NR | NR | 1 | 0 | 1 | 75 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 1000 | 2550 | NR | NR | 2550
29 | 29.5x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 1000 | HP | 84 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 84% | Natural Gas | Gas Transmission | Acrolein | 2550 | NR | NR | 2550 | 2550 | 3800 | 3 | 2550 | NR | NR | .103 | NR | NR | .103 | .0113 | NR | NR | .0113 | .000123 | NR | NR | .000123 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4617 | NR | NR | 56 | .069 | NR | NR | 1 | 0 | 1 | 84 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 1000 | 2590 | NR | NR | 2590
7 | 7.13 | ARCO Oil and Gas Co | CARB 430 | Bakersfield CA 93309 | ARCO Oil and Gas Co/Bakersfield CA 93309 | ENSR Consulting | 1990-07-01 | 660 | HP | 100 | Cooper Bessemer | NR | Cooper Bessemer/NR/660 MW / 100% | Natural Gas | Compressor | Acrolein | 1090 | 50 | 550 | 563.333333333333 | 563 | NA | 3 | 1090 | 50 | 550 | .0345 | .00158 | .0174 | .0178 | .00419 | .000192 | .00212 | .00217 | .0000523 | .00000239 | .0000264 | .000027 | ppb | NR |  | 14.0 | 14.0 | 14.0 | NR |  | 68 | F | NR | Btu/dscf | 3637.7 | 3637.7 | 3637.7 | 56 |  |  |  | 3 | 0 | 1 | 100 | 2SLB | NR | NR | 8740 | 2 | 660 | 932 | 42.8 | 470 | 481.6

## 2SLB-formaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
11 | 11.1 | Chevron USA | CARB 430 | Carpinteria, CA | Chevron USA/Carpinteria, CA | Engineering Science Inc. | 1990-04-23 | 1800 | HP | 100 | Cooper Bessemer | GMWA-10 | Cooper Bessemer/GMWA-10/1800 MW / 100% | Natural Gas | NR | Formaldehyde | 2870 | 8530 | 2830 | 4743.33333333333 | 4740 | NA | 3 | 2870 | 8530 | 2830 | .0119 | .0353 | .0117 | .0196 | .00333 | .00988 | .00328 | .0055 | .00000661 | .0000196 | .0000065 | .0000109 | ppb | NR |  | 8.9 | 8.9 | 8.9 | NR | Process parameters for individual runs not provided. | 68 | F | 1128.48 | Btu/dscf | 887 | 887 | 887 | 30 |  |  |  | 3 | 0 | 1 | 100 | 2SLB | Blower Scavenged | 10 | 8546.256 | 2 | 1800 | 1410 | 4190 | 1390 | 2330
29 | 29.10x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | Formaldehyde | 18300 | NR | NR | 18300 | 18300 | 830 | 3 | 18300 | NR | NR | .662 | NR | NR | .662 | .0412 | NR | NR | .0412 | .000361 | NR | NR | .000361 | ppb | NR |  | 14.8 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7749 | NR | NR | 30 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 17700 | NR | NR | 17700
29 | 29.11x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-11 | 1800 | HP | 85 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 85% | Natural Gas | Gas Transmission | Formaldehyde | 22400 | NR | NR | 22400 | 22400 | 830 | 3 | 22400 | NR | NR | .917 | NR | NR | .917 | .0569 | NR | NR | .0569 | .000599 | NR | NR | .000599 | ppb | NR |  | 15.5 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 8769 | NR | NR | 30 | .069 | NR | NR | 1 | 0 | 1 | 85 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 24500 | NR | NR | 24500
29 | 29.12x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 100 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 100% | Natural Gas | Gas Transmission | Formaldehyde | 16500 | NR | NR | 16500 | 16500 | 560 | 3 | 16500 | NR | NR | .538 | NR | NR | .538 | .0377 | NR | NR | .0377 | .000299 | NR | NR | .000299 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6983 | NR | NR | 30 | .067 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 16200 | NR | NR | 16200
29 | 29.13x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 87 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 87% | Natural Gas | Gas Transmission | Formaldehyde | 18900 | NR | NR | 18900 | 18900 | 560 | 3 | 18900 | NR | NR | .607 | NR | NR | .607 | .0463 | NR | NR | .0463 | .000388 | NR | NR | .000388 | ppb | NR |  | 15.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6880 | NR | NR | 30 | .065 | NR | NR | 1 | 0 | 1 | 87 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 19900 | NR | NR | 19900
29 | 29.14x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 86 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 86% | Natural Gas | Gas Transmission | Formaldehyde | 16700 | NR | NR | 16700 | 16700 | 560 | 3 | 16700 | NR | NR | .487 | NR | NR | .487 | .0409 | NR | NR | .0409 | .000315 | NR | NR | .000315 | ppb | NR |  | 15.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6243 | NR | NR | 30 | .065 | NR | NR | 1 | 0 | 1 | 86 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 17600 | NR | NR | 17600
29 | 29.15x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 101 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 101% | Natural Gas | Gas Transmission | Formaldehyde | 14400 | NR | NR | 14400 | 14400 | 560 | 3 | 14400 | NR | NR | .424 | NR | NR | .424 | .0314 | NR | NR | .0314 | .000233 | NR | NR | .000233 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6312 | NR | NR | 30 | .07 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 13500 | NR | NR | 13500
29 | 29.16x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 95% | Natural Gas | Gas Transmission | Formaldehyde | 15400 | NR | NR | 15400 | 15400 | 560 | 3 | 15400 | NR | NR | .469 | NR | NR | .469 | .0352 | NR | NR | .0352 | .000274 | NR | NR | .000274 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6528 | NR | NR | 30 | .068 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 15100 | NR | NR | 15100
29 | 29.17x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 96 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 96% | Natural Gas | Gas Transmission | Formaldehyde | 29800 | NR | NR | 29800 | 29800 | 800 | 3 | 29800 | NR | NR | 1.82 | NR | NR | 1.82 | .0659 | NR | NR | .0659 | .000542 | NR | NR | .000542 | ppb | NR |  | 14.7 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 13104 | NR | NR | 30 | .069 | NR | NR | 1 | 0 | 1 | 96 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 28400 | NR | NR | 28400
29 | 29.18x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 95 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 95% | Natural Gas | Gas Transmission | Formaldehyde | 30700 | NR | NR | 30700 | 30700 | 800 | 3 | 30700 | NR | NR | 1.7 | NR | NR | 1.7 | .0668 | NR | NR | .0668 | .000511 | NR | NR | .000511 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 11888 | NR | NR | 30 | .071 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 28800 | NR | NR | 28800
29 | 29.19x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 88 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 88% | Natural Gas | Gas Transmission | Formaldehyde | 26500 | NR | NR | 26500 | 26500 | 800 | 3 | 26500 | NR | NR | 1.46 | NR | NR | 1.46 | .0616 | NR | NR | .0616 | .000474 | NR | NR | .000474 | ppb | NR |  | 15 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 11794 | NR | NR | 30 | .067 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 26500 | NR | NR | 26500
29 | 29.1x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 911 | HP | 94 | Clark | BA-5 | Clark/BA-5/911 MW / 94% | Natural Gas | Gas Transmission | Formaldehyde | 18600 | NR | NR | 18600 | 18600 | 360 | 3 | 18600 | NR | NR | .371 | NR | NR | .371 | .0381 | NR | NR | .0381 | .000433 | NR | NR | .000433 | ppb | NR |  | 14.2 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4272 | NR | NR | 30 | .104 | NR | NR | 1 | 0 | 1 | 94 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 911 | 16400 | NR | NR | 16400
29 | 29.20x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 91 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 91% | Natural Gas | Gas Transmission | Formaldehyde | 28200 | NR | NR | 28200 | 28200 | 800 | 3 | 28200 | NR | NR | 1.78 | NR | NR | 1.78 | .0667 | NR | NR | .0667 | .000559 | NR | NR | .000559 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 13514 | NR | NR | 30 | .068 | NR | NR | 1 | 0 | 1 | 91 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 28700 | NR | NR | 28700
29 | 29.21x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 92 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 92% | Natural Gas | Gas Transmission | Formaldehyde | 27900 | NR | NR | 27900 | 27900 | 800 | 3 | 27900 | NR | NR | 1.69 | NR | NR | 1.69 | .066 | NR | NR | .066 | .000525 | NR | NR | .000525 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 12978 | NR | NR | 30 | .069 | NR | NR | 1 | 0 | 1 | 92 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 28400 | NR | NR | 28400
29 | 29.22x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-25 | 1800 | HP | 97 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 97% | Natural Gas | Gas Transmission | Formaldehyde | 20300 | NR | NR | 20300 | 20300 | 1250 | 3 | 20300 | NR | NR | .656 | NR | NR | .656 | .0518 | NR | NR | .0518 | .000376 | NR | NR | .000376 | ppb | PCC Clean burn |  | 15.5 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6920 | NR | NR | 30 | .073 | NR | NR | 1 | 0 | 3 | 97 | 2SLB | Turbo Charged | 10 | 8470 | 1 | 1800 | 22200 | NR | NR | 22200
29 | 29.23x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-26 | 1800 | HP | 93 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 93% | Natural Gas | Gas Transmission | Formaldehyde | 22000 | NR | NR | 22000 | 22000 | 1250 | 3 | 22000 | NR | NR | .705 | NR | NR | .705 | .0551 | NR | NR | .0551 | .000421 | NR | NR | .000421 | ppb | PCC Clean burn |  | 15.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6866 | NR | NR | 30 | .073 | NR | NR | 1 | 0 | 3 | 93 | 2SLB | Turbo Charged | 10 | 8471 | 1 | 1800 | 23600 | NR | NR | 23600
29 | 29.24x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 95% | Natural Gas | Gas Transmission | Formaldehyde | 15200 | NR | NR | 15200 | 15200 | 1250 | 3 | 15200 | NR | NR | .471 | NR | NR | .471 | .0376 | NR | NR | .0376 | .000275 | NR | NR | .000275 | ppb | PCC Clean burn |  | 15.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6633 | NR | NR | 30 | .082 | NR | NR | 1 | 0 | 3 | 95 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 16000 | NR | NR | 16000
29 | 29.25x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 79 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 79% | Natural Gas | Gas Transmission | Formaldehyde | 25500 | NR | NR | 25500 | 25500 | 1250 | 3 | 25500 | NR | NR | .719 | NR | NR | .719 | .0654 | NR | NR | .0654 | .000506 | NR | NR | .000506 | ppb | PCC Clean burn |  | 15.5 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6039 | NR | NR | 30 | .08 | NR | NR | 1 | 0 | 3 | 79 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 27900 | NR | NR | 27900
29 | 29.2x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 911 | HP | 100 | Clark | BA-5 | Clark/BA-5/911 MW / 100% | Natural Gas | Gas Transmission | Formaldehyde | 17900 | NR | NR | 17900 | 17900 | 360 | 3 | 17900 | NR | NR | .391 | NR | NR | .391 | .0373 | NR | NR | .0373 | .000429 | NR | NR | .000429 | ppb | NR |  | 14.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4679 | NR | NR | 30 | .08 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 911 | 16000 | NR | NR | 16000
29 | 29.3x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 911 | HP | 80 | Clark | BA-5 | Clark/BA-5/911 MW / 80% | Natural Gas | Gas Transmission | Formaldehyde | 23000 | NR | NR | 23000 | 23000 | 360 | 3 | 23000 | NR | NR | .468 | NR | NR | .468 | .0526 | NR | NR | .0526 | .000642 | NR | NR | .000642 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4356 | NR | NR | 30 | .088 | NR | NR | 1 | 0 | 1 | 80 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 911 | 22600 | NR | NR | 22600
29 | 29.4x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 1000 | HP | 75 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 75% | Natural Gas | Gas Transmission | Formaldehyde | 33300 | NR | NR | 33300 | 33300 | 970 | 3 | 33300 | NR | NR | .74 | NR | NR | .74 | .0878 | NR | NR | .0878 | .000987 | NR | NR | .000987 | ppb | NR |  | 15.7 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4759 | NR | NR | 30 | .068 | NR | NR | 1 | 0 | 1 | 75 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 1000 | 37800 | NR | NR | 37800
29 | 29.5x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 1000 | HP | 84 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 84% | Natural Gas | Gas Transmission | Formaldehyde | 26600 | NR | NR | 26600 | 26600 | 970 | 3 | 26600 | NR | NR | .573 | NR | NR | .573 | .0631 | NR | NR | .0631 | .000682 | NR | NR | .000682 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4617 | NR | NR | 30 | .069 | NR | NR | 1 | 0 | 1 | 84 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 1000 | 27100 | NR | NR | 27100
29 | 29.6x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-11 | 1235 | HP | 88 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 88% | Natural Gas | Gas Transmission | Formaldehyde | 18800 | NR | NR | 18800 | 18800 | 990 | 3 | 18800 | NR | NR | .446 | NR | NR | .446 | .0445 | NR | NR | .0445 | .00041 | NR | NR | .00041 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 5079 | NR | NR | 30 | .072 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 19100 | NR | NR | 19100
29 | 29.7x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-12 | 1235 | HP | 100 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 100% | Natural Gas | Gas Transmission | Formaldehyde | 17800 | NR | NR | 17800 | 17800 | 990 | 3 | 17800 | NR | NR | .402 | NR | NR | .402 | .0388 | NR | NR | .0388 | .000326 | NR | NR | .000326 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 4845 | NR | NR | 30 | .083 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 16700 | NR | NR | 16700
29 | 29.8x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-12 | 1235 | HP | 100 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 100% | Natural Gas | Gas Transmission | Formaldehyde | 18000 | NR | NR | 18000 | 18000 | 990 | 3 | 18000 | NR | NR | .4 | NR | NR | .4 | .0386 | NR | NR | .0386 | .000324 | NR | NR | .000324 | ppb | NR |  | 14.5 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 4756 | NR | NR | 30 | .084 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 16600 | NR | NR | 16600
29 | 29.9x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | Formaldehyde | 18100 | NR | NR | 18100 | 18100 | 830 | 3 | 18100 | NR | NR | .673 | NR | NR | .673 | .0421 | NR | NR | .0421 | .000367 | NR | NR | .000367 | ppb | NR |  | 15 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7972 | NR | NR | 30 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 18100 | NR | NR | 18100
3 | 3.1 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 80 | Dresser-Rand | TLA-6 | Dresser-Rand/TLA-6/2000 MW / 80% | Natural Gas | NR | Formaldehyde | 66000 | 17000 | NR | 41500 | 41500 | NA | 3 | 66000 | 17000 | NR | 2.2 | .571 | NR | 1.39 | .132 | .0337 | NR | .0829 | .00138 | .000357 | NR | .000868 | ppb | PCC | #A | 13.84 | 13.76 | 13.72 | NR | #A | 68 | F | 1024 | Btu/dscf | 7143.83 | 7198.57 | 7226.27 | 30 |  |  |  | 2 | 0 | 3 | 80 | 2SLB | NR | 6 | 8710 | 2 | 2000 | 55200 | 14000 | NR | 34600
3 | 3.2 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 90 | Dresser-Rand | TLA-6 | Dresser-Rand/TLA-6/2000 MW / 90% | Natural Gas | NR | Formaldehyde | 26000 | NR | NR | 26000 | 26000 | NA | 3 | 26000 | NR | NR | .924 | NR | NR | .924 | .0663 | NR | NR | .0663 | .000513 | NR | NR | .000513 | ppb | PCC | #A | 15.34 | 15.31 | 15.39 | NR | #A | 68 | F | 1022 | Btu/dscf | 7617.43 | 7617.43 | 7617.43 | 30 |  |  |  | 1 | 0 | 3 | 90 | 2SLB | NR | 8 | 8710 | 2 | 2000 | 27600 | NR | NR | 27600
3 | 3.3 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 100 | Dresser-Rand | TLA-6 | Dresser-Rand/TLA-6/2000 MW / 100% | Natural Gas | NR | Formaldehyde | 22000 | 7600 | 15000 | 14866.6666666667 | 14900 | NA | 3 | 22000 | 7600 | 15000 | .837 | .289 | .578 | .568 | .0572 | .0193 | .0382 | .0382 | .000418 | .000144 | .000289 | .000284 | ppb | PCC | #A | 15.45 | 15.32 | 15.33 | NR | #A | 68 | F | 1023 | Btu/dscf | 8152.53 | 8144.75 | 8252.47 | 30 |  |  |  | 3 | 0 | 3 | 100 | 2SLB | NR | 6 | 8710 | 2 | 2000 | 23800 | 8040 | 15900 | 15913.3333333333
31 | 31.11x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 104 | Clark | HRA-8 | Clark/HRA-8/796 MW / 104% | Natural Gas | Compressor | Formaldehyde | 50754 | NR | NR | 50754 | 50800 | 1724 | 3 | 50754 | NR | NR | .805 | NR | NR | .805 | .105 | NR | NR | .105 | .000972 | NR | NR | .000972 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14.2 | NR | NR | 848 | Engine 23 - Test 6. Post-maintenance, bad cam timing. | 68 | F | 1011 | Btu/scf | 3399 | NR | NR | 30 | 7.2 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 44700 | NR | NR | 44700
31 | 31.12x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-16 | 796 | HP | 101 | Clark | HRA-8 | Clark/HRA-8/796 MW / 101% | Natural Gas | Compressor | Formaldehyde | 39477 | NR | NR | 39477 | 39500 | 502 | 3 | 39477 | NR | NR | .607 | NR | NR | .607 | .0791 | NR | NR | .0791 | .000755 | NR | NR | .000755 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14 | NR | NR | 848 | Engine 23 - Test 17. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3296 | NR | NR | 30 | 8.3 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 33800 | NR | NR | 33800
31 | 31.13x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 88 | Clark | HRA-8 | Clark/HRA-8/796 MW / 88% | Natural Gas | Compressor | Formaldehyde | 36214 | NR | NR | 36214 | 36200 | 449 | 3 | 36214 | NR | NR | .514 | NR | NR | .514 | .065 | NR | NR | .065 | .000734 | NR | NR | .000734 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 704 | Engine 24 - Test 10. Pre-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 3040 | NR | NR | 30 | 8.6 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 27700 | NR | NR | 27700
31 | 31.14x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 89 | Clark | HRA-8 | Clark/HRA-8/796 MW / 89% | Natural Gas | Compressor | Formaldehyde | 37405 | NR | NR | 37405 | 37400 | 469 | 3 | 37405 | NR | NR | .55 | NR | NR | .55 | .0672 | NR | NR | .0672 | .000776 | NR | NR | .000776 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 708 | Engine 24 - Test 11. Pre-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3151 | NR | NR | 30 | 8.3 | NR | NR | 1 | 0 | 1 | 89 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 28700 | NR | NR | 28700
31 | 31.15x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 91 | Clark | HRA-8 | Clark/HRA-8/796 MW / 91% | Natural Gas | Compressor | Formaldehyde | 36184 | NR | NR | 36184 | 36200 | 856 | 3 | 36184 | NR | NR | .538 | NR | NR | .538 | .0695 | NR | NR | .0695 | .000743 | NR | NR | .000743 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.7 | NR | NR | 726 | Engine 24 - Test 3. Post-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 3188 | NR | NR | 30 | 7.7 | NR | NR | 1 | 0 | 1 | 91 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 29700 | NR | NR | 29700
31 | 31.16x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 89 | Clark | HRA-8 | Clark/HRA-8/796 MW / 89% | Natural Gas | Compressor | Formaldehyde | 32792 | NR | NR | 32792 | 32800 | 823 | 3 | 32792 | NR | NR | .486 | NR | NR | .486 | .0648 | NR | NR | .0648 | .000686 | NR | NR | .000686 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.9 | NR | NR | 715 | Engine 24 - Test 4. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3176 | NR | NR | 30 | 7.6 | NR | NR | 1 | 0 | 1 | 89 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 27600 | NR | NR | 27600
31 | 31.17x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 2050 | HP | 99 | Clark | HBAT-8 | Clark/HBAT-8/2050 MW / 99% | Natural Gas | Compressor | Formaldehyde | 108307 | NR | NR | 108307 | 108000 | 1788 | 3 | 108307 | NR | NR | 2.87 | NR | NR | 2.87 | .163 | NR | NR | .163 | .00141 | NR | NR | .00141 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 11.7 | NR | NR | 1929 | Engine 25 - Test 9. Pre-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 5684 | NR | NR | 30 | 4.9 | NR | NR | 1 | 0 | 1 | 99 | 2SLB | Turbo Charged |  | 8498 | 1 | 2050 | 69500 | NR | NR | 69500
31 | 31.18x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 2050 | HP | 95 | Clark | HBAT-8 | Clark/HBAT-8/2050 MW / 95% | Natural Gas | Compressor | Formaldehyde | 52017 | NR | NR | 52017 | 52000 | 1025 | 3 | 52017 | NR | NR | 1.37 | NR | NR | 1.37 | .0877 | NR | NR | .0877 | .000703 | NR | NR | .000703 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.7 | NR | NR | 1836 | Engine 25 - Test 1. Post-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 5642 | NR | NR | 30 | 8.3 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged |  | 8498 | 1 | 2050 | 37400 | NR | NR | 37400
31 | 31.19x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 2050 | HP | 94 | Clark | HBAT-8 | Clark/HBAT-8/2050 MW / 94% | Natural Gas | Compressor | Formaldehyde | 53377 | NR | NR | 53377 | 53400 | 1089 | 3 | 53377 | NR | NR | 1.43 | NR | NR | 1.43 | .09 | NR | NR | .09 | .000742 | NR | NR | .000742 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.7 | NR | NR | 1819 | Engine 25 - Test 2. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 5750 | NR | NR | 30 | 8.2 | NR | NR | 1 | 0 | 1 | 94 | 2SLB | Turbo Charged |  | 8498 | 1 | 2050 | 38400 | NR | NR | 38400
31 | 31.1x | GRI - Campaign 2 | FTIR | None | GRI - Campaign 2/None | Radian Corporation | 1994-03-12 | 1350 | HP | 73 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1350 MW / 73% | Natural Gas | Drives Refrigeration Compressor | Formaldehyde | 27100 | NR | NR | 27100 | 27100 | 1251 | 3 | 27100 | NR | NR | .765 | NR | NR | .765 | .0681 | NR | NR | .0681 | .000776 | NR | NR | .000776 | ppb | NR | Fuel factor is default given in calculations section of report | 15.4 | NR | NR | 984 | Cooper - Test 7 | 68 | F | 1012 | Btu/scf | 6050 | NR | NR | 30 | 5.7 | NR | NR | 1 | 0 | 1 | 73 | 2SLB | Blower Scavenged |  | 8498 | 1 | 1350 | 29100 | NR | NR | 29100
31 | 31.2x | GRI - Campaign 2 | FTIR | None | GRI - Campaign 2/None | Radian Corporation | 1994-03-13 | 1140 | HP | 87 | Clark | BA-6 | Clark/BA-6/1140 MW / 87% | Natural Gas | Gas Compression | Formaldehyde | 2600 | NR | NR | 2600 | 2600 | 517 | 3 | 2600 | NR | NR | .0642 | NR | NR | .0642 | .00378 | NR | NR | .00378 | .0000647 | NR | NR | .0000647 | ppb | NR | Fuel factor is default given in calculations section of report | 11.4 | NR | NR | 994 | Clark - Test 8 | 68 | F | 1012 | Btu/scf | 5291 | NR | NR | 30 | 9.0 | NR | NR | 1 | 0 | 1 | 87 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1140 | 1610 | NR | NR | 1610
31 | 31.3x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-18 | 2000 | HP | 98 | Cooper Bessemer | GMWA-8 | Cooper Bessemer/GMWA-8/2000 MW / 98% | Natural Gas | Compressor | Formaldehyde | 12128 | NR | NR | 12128 | 12100 | 772 | 3 | 12128 | NR | NR | .469 | NR | NR | .469 | .027 | NR | NR | .027 | .000239 | NR | NR | .000239 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14.7 | NR | NR | 1958 | Engine 4 - Test 1 | 68 | F | 1206 | Btu/scf | 8290 | NR | NR | 30 | 9.3 | NR | NR | 1 | 0 | 1 | 98 | 2SLB | Blower Scavenged |  | 8498 | 1 | 2000 | 11500 | NR | NR | 11500
31 | 31.4x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-18 | 2000 | HP | 83 | Cooper Bessemer | GMWA-8 | Cooper Bessemer/GMWA-8/2000 MW / 83% | Natural Gas | Compressor | Formaldehyde | 11714 | NR | NR | 11714 | 11700 | 976 | 3 | 11714 | NR | NR | .463 | NR | NR | .463 | .0294 | NR | NR | .0294 | .000279 | NR | NR | .000279 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 15.4 | NR | NR | 1655 | Engine 4 - Test 2 | 68 | F | 1206 | Btu/scf | 8462 | NR | NR | 30 | 7.8 | NR | NR | 1 | 0 | 1 | 83 | 2SLB | Blower Scavenged |  | 8498 | 1 | 2000 | 12600 | NR | NR | 12600
31 | 31.5x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-18 | 1100 | HP | 81 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 81% | Natural Gas | Compressor | Formaldehyde | 16000 | NR | NR | 16000 | 16000 | 1946 | 3 | 16000 | NR | NR | .322 | NR | NR | .322 | .0381 | NR | NR | .0381 | .000361 | NR | NR | .000361 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 15.1 | NR | NR | 894 | Engine 2 - Test 1 | 68 | F | 1206 | Btu/scf | 4311 | NR | NR | 30 | 7.5 | NR | NR | 1 | 0 | 1 | 81 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 16300 | NR | NR | 16300
31 | 31.6x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-19 | 1100 | HP | 104 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 104% | Natural Gas | Compressor | Formaldehyde | 15273 | NR | NR | 15273 | 15300 | 780 | 3 | 15273 | NR | NR | .277 | NR | NR | .277 | .0267 | NR | NR | .0267 | .000242 | NR | NR | .000242 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.0 | NR | NR | 1145 | Engine 2 - Test 2 | 68 | F | 1204 | Btu/scf | 3885 | NR | NR | 30 | 10.3 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 11400 | NR | NR | 11400
31 | 31.7x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-19 | 1100 | HP | 104 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 104% | Natural Gas | Compressor | Formaldehyde | 13451 | NR | NR | 13451 | 13500 | 662 | 3 | 13451 | NR | NR | .244 | NR | NR | .244 | .0235 | NR | NR | .0235 | .000213 | NR | NR | .000213 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.0 | NR | NR | 1142 | Engine 2 - Test 3 | 68 | F | 1204 | Btu/scf | 3890 | NR | NR | 30 | 9.3 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 10000 | NR | NR | 10000
31 | 31.8x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-20 | 1100 | HP | 104 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 104% | Natural Gas | Compressor | Formaldehyde | 12690 | NR | NR | 12690 | 12700 | 651 | 3 | 12690 | NR | NR | .229 | NR | NR | .229 | .0228 | NR | NR | .0228 | .0002 | NR | NR | .0002 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 1146 | Engine 2 - Test 4 | 68 | F | 1205 | Btu/scf | 3868 | NR | NR | 30 | 7.8 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 9720 | NR | NR | 9720
31 | 31.9x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 105 | Clark | HRA-8 | Clark/HRA-8/796 MW / 105% | Natural Gas | Compressor | Formaldehyde | 52805 | NR | NR | 52805 | 52800 | 660 | 3 | 52805 | NR | NR | .696 | NR | NR | .696 | .0869 | NR | NR | .0869 | .000833 | NR | NR | .000833 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.5 | NR | NR | 813 | Engine 23 - Test 12. Pre-maintenance and pre-balance. | 68 | F | 1011 | Btu/scf | 2826 | NR | NR | 30 | 9.1 | NR | NR | 1 | 0 | 1 | 105 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 37100 | NR | NR | 37100
7 | 7.13 | ARCO Oil and Gas Co | CARB 430 | Bakersfield CA 93309 | ARCO Oil and Gas Co/Bakersfield CA 93309 | ENSR Consulting | 1990-07-01 | 660 | HP | 100 | Cooper Bessemer | NR | Cooper Bessemer/NR/660 MW / 100% | Natural Gas | Compressor | Formaldehyde | 30380 | 3450 | 14740 | 16190 | 16200 | NA | 3 | 30380 | 3450 | 14740 | .516 | .0586 | .25 | .275 | .0626 | .00711 | .0304 | .0334 | .000782 | .0000888 | .000379 | .000417 | ppb | NR |  | 14.0 | 14.0 | 14.0 | NR |  | 68 | F | NR | Btu/dscf | 3637.7 | 3637.7 | 3637.7 | 30 |  |  |  | 3 | 0 | 1 | 100 | 2SLB | NR | NR | 8740 | 2 | 660 | 26000 | 2950 | 12600 | 13850

## 2SLB-methanol
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
29 | 29.10x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | Methanol | 690 | NR | NR | 690 | 690 | NA | 3 | 690 | NR | NR | .0266 | NR | NR | .0266 | .00166 | NR | NR | .00166 | .0000145 | NR | NR | .0000145 | ppb | NR |  | 14.8 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7749 | NR | NR | 32 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 667 | NR | NR | 667
29 | 29.11x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-11 | 1800 | HP | 85 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 85% | Natural Gas | Gas Transmission | Methanol | 740 | NR | NR | 740 | 740 | NA | 3 | 740 | NR | NR | .0323 | NR | NR | .0323 | .00201 | NR | NR | .00201 | .0000211 | NR | NR | .0000211 | ppb | NR |  | 15.5 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 8769 | NR | NR | 32 | .069 | NR | NR | 1 | 0 | 1 | 85 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 809 | NR | NR | 809
29 | 29.12x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 100 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 100% | Natural Gas | Gas Transmission | Methanol | 750 | NR | NR | 750 | 750 | NA | 3 | 750 | NR | NR | .0261 | NR | NR | .0261 | .00183 | NR | NR | .00183 | .0000145 | NR | NR | .0000145 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6983 | NR | NR | 32 | .067 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 738 | NR | NR | 738
29 | 29.13x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 87 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 87% | Natural Gas | Gas Transmission | Methanol | 850 | NR | NR | 850 | 850 | NA | 3 | 850 | NR | NR | .0291 | NR | NR | .0291 | .00222 | NR | NR | .00222 | .0000186 | NR | NR | .0000186 | ppb | NR |  | 15.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6880 | NR | NR | 32 | .065 | NR | NR | 1 | 0 | 1 | 87 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 896 | NR | NR | 896
29 | 29.14x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 86 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 86% | Natural Gas | Gas Transmission | Methanol | 770 | NR | NR | 770 | 770 | NA | 3 | 770 | NR | NR | .0239 | NR | NR | .0239 | .00201 | NR | NR | .00201 | .0000154 | NR | NR | .0000154 | ppb | NR |  | 15.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6243 | NR | NR | 32 | .065 | NR | NR | 1 | 0 | 1 | 86 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 811 | NR | NR | 811
29 | 29.15x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 101 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 101% | Natural Gas | Gas Transmission | Methanol | 760 | NR | NR | 760 | 760 | NA | 3 | 760 | NR | NR | .0239 | NR | NR | .0239 | .00176 | NR | NR | .00176 | .0000131 | NR | NR | .0000131 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6312 | NR | NR | 32 | .07 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 712 | NR | NR | 712
29 | 29.16x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 95% | Natural Gas | Gas Transmission | Methanol | 750 | NR | NR | 750 | 750 | NA | 3 | 750 | NR | NR | .0244 | NR | NR | .0244 | .00183 | NR | NR | .00183 | .0000143 | NR | NR | .0000143 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6528 | NR | NR | 32 | .068 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 738 | NR | NR | 738
29 | 29.17x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 96 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 96% | Natural Gas | Gas Transmission | Methanol | 1590 | NR | NR | 1590 | 1590 | NA | 3 | 1590 | NR | NR | .104 | NR | NR | .104 | .00375 | NR | NR | .00375 | .000031 | NR | NR | .000031 | ppb | NR |  | 14.7 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 13104 | NR | NR | 32 | .069 | NR | NR | 1 | 0 | 1 | 96 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 1510 | NR | NR | 1510
29 | 29.18x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 95 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 95% | Natural Gas | Gas Transmission | Methanol | 1680 | NR | NR | 1680 | 1680 | NA | 3 | 1680 | NR | NR | .0994 | NR | NR | .0994 | .0039 | NR | NR | .0039 | .0000299 | NR | NR | .0000299 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 11888 | NR | NR | 32 | .071 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 1570 | NR | NR | 1570
29 | 29.19x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 88 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 88% | Natural Gas | Gas Transmission | Methanol | 1390 | NR | NR | 1390 | 1390 | NA | 3 | 1390 | NR | NR | .0816 | NR | NR | .0816 | .00345 | NR | NR | .00345 | .0000265 | NR | NR | .0000265 | ppb | NR |  | 15 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 11794 | NR | NR | 32 | .067 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 1390 | NR | NR | 1390
29 | 29.1x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 911 | HP | 94 | Clark | BA-5 | Clark/BA-5/911 MW / 94% | Natural Gas | Gas Transmission | Methanol | 1390 | NR | NR | 1390 | 1390 | NA | 3 | 1390 | NR | NR | .0296 | NR | NR | .0296 | .00303 | NR | NR | .00303 | .0000346 | NR | NR | .0000346 | ppb | NR |  | 14.2 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4272 | NR | NR | 32 | .104 | NR | NR | 1 | 0 | 1 | 94 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 911 | 1220 | NR | NR | 1220
29 | 29.20x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 91 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 91% | Natural Gas | Gas Transmission | Methanol | 1470 | NR | NR | 1470 | 1470 | NA | 3 | 1470 | NR | NR | .0989 | NR | NR | .0989 | .00371 | NR | NR | .00371 | .0000311 | NR | NR | .0000311 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 13514 | NR | NR | 32 | .068 | NR | NR | 1 | 0 | 1 | 91 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 1500 | NR | NR | 1500
29 | 29.21x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 92 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 92% | Natural Gas | Gas Transmission | Methanol | 1420 | NR | NR | 1420 | 1420 | NA | 3 | 1420 | NR | NR | .0917 | NR | NR | .0917 | .00358 | NR | NR | .00358 | .0000285 | NR | NR | .0000285 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 12978 | NR | NR | 32 | .069 | NR | NR | 1 | 0 | 1 | 92 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 1440 | NR | NR | 1440
29 | 29.22x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-25 | 1800 | HP | 97 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 97% | Natural Gas | Gas Transmission | Methanol | 880 | NR | NR | 880 | 880 | NA | 3 | 880 | NR | NR | .0303 | NR | NR | .0303 | .0024 | NR | NR | .0024 | .0000174 | NR | NR | .0000174 | ppb | PCC Clean burn |  | 15.5 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6920 | NR | NR | 32 | .073 | NR | NR | 1 | 0 | 3 | 97 | 2SLB | Turbo Charged | 10 | 8470 | 1 | 1800 | 961 | NR | NR | 961
29 | 29.23x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-26 | 1800 | HP | 93 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 93% | Natural Gas | Gas Transmission | Methanol | 350 | NR | NR | 350 | 350 | NA | 3 | 350 | NR | NR | .012 | NR | NR | .012 | .000935 | NR | NR | .000935 | .00000717 | NR | NR | .00000717 | ppb | PCC Clean burn |  | 15.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6866 | NR | NR | 32 | .073 | NR | NR | 1 | 0 | 3 | 93 | 2SLB | Turbo Charged | 10 | 8471 | 1 | 1800 | 375 | NR | NR | 375
29 | 29.24x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 95% | Natural Gas | Gas Transmission | Methanol | 690 | NR | NR | 690 | 690 | NA | 3 | 690 | NR | NR | .0228 | NR | NR | .0228 | .00182 | NR | NR | .00182 | .0000133 | NR | NR | .0000133 | ppb | PCC Clean burn |  | 15.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6633 | NR | NR | 32 | .082 | NR | NR | 1 | 0 | 3 | 95 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 727 | NR | NR | 727
29 | 29.25x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 79 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 79% | Natural Gas | Gas Transmission | Methanol | 990 | NR | NR | 990 | 990 | NA | 3 | 990 | NR | NR | .0298 | NR | NR | .0298 | .00271 | NR | NR | .00271 | .000021 | NR | NR | .000021 | ppb | PCC Clean burn |  | 15.5 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6039 | NR | NR | 32 | .08 | NR | NR | 1 | 0 | 3 | 79 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 1080 | NR | NR | 1080
29 | 29.2x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 911 | HP | 100 | Clark | BA-5 | Clark/BA-5/911 MW / 100% | Natural Gas | Gas Transmission | Methanol | 1610 | NR | NR | 1610 | 1610 | NA | 3 | 1610 | NR | NR | .0375 | NR | NR | .0375 | .00358 | NR | NR | .00358 | .0000412 | NR | NR | .0000412 | ppb | NR |  | 14.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4679 | NR | NR | 32 | .08 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 911 | 1440 | NR | NR | 1440
29 | 29.3x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 911 | HP | 80 | Clark | BA-5 | Clark/BA-5/911 MW / 80% | Natural Gas | Gas Transmission | Methanol | 1350 | NR | NR | 1350 | 1350 | NA | 3 | 1350 | NR | NR | .0293 | NR | NR | .0293 | .00329 | NR | NR | .00329 | .0000402 | NR | NR | .0000402 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4356 | NR | NR | 32 | .088 | NR | NR | 1 | 0 | 1 | 80 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 911 | 1330 | NR | NR | 1330
29 | 29.4x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 1000 | HP | 75 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 75% | Natural Gas | Gas Transmission | Methanol | 1530 | NR | NR | 1530 | 1530 | NA | 3 | 1530 | NR | NR | .0362 | NR | NR | .0362 | .0043 | NR | NR | .0043 | .0000483 | NR | NR | .0000483 | ppb | NR |  | 15.7 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4759 | NR | NR | 32 | .068 | NR | NR | 1 | 0 | 1 | 75 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 1000 | 1740 | NR | NR | 1740
29 | 29.5x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 1000 | HP | 84 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 84% | Natural Gas | Gas Transmission | Methanol | 1440 | NR | NR | 1440 | 1440 | NA | 3 | 1440 | NR | NR | .0331 | NR | NR | .0331 | .00364 | NR | NR | .00364 | .0000394 | NR | NR | .0000394 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4617 | NR | NR | 32 | .069 | NR | NR | 1 | 0 | 1 | 84 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 1000 | 1460 | NR | NR | 1460
29 | 29.6x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-11 | 1235 | HP | 88 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 88% | Natural Gas | Gas Transmission | Methanol | 670 | NR | NR | 670 | 670 | NA | 3 | 670 | NR | NR | .0169 | NR | NR | .0169 | .00169 | NR | NR | .00169 | .0000156 | NR | NR | .0000156 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 5079 | NR | NR | 32 | .072 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 682 | NR | NR | 682
29 | 29.7x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-12 | 1235 | HP | 100 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 100% | Natural Gas | Gas Transmission | Methanol | 920 | NR | NR | 920 | 920 | NA | 3 | 920 | NR | NR | .0222 | NR | NR | .0222 | .00214 | NR | NR | .00214 | .000018 | NR | NR | .000018 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 4845 | NR | NR | 32 | .083 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 862 | NR | NR | 862
29 | 29.8x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-12 | 1235 | HP | 100 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 100% | Natural Gas | Gas Transmission | Methanol | 970 | NR | NR | 970 | 970 | NA | 3 | 970 | NR | NR | .023 | NR | NR | .023 | .00222 | NR | NR | .00222 | .0000186 | NR | NR | .0000186 | ppb | NR |  | 14.5 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 4756 | NR | NR | 32 | .084 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 894 | NR | NR | 894
29 | 29.9x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | Methanol | 700 | NR | NR | 700 | 700 | NA | 3 | 700 | NR | NR | .0278 | NR | NR | .0278 | .00174 | NR | NR | .00174 | .0000151 | NR | NR | .0000151 | ppb | NR |  | 15 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7972 | NR | NR | 32 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 700 | NR | NR | 700
31 | 31.11x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 104 | Clark | HRA-8 | Clark/HRA-8/796 MW / 104% | Natural Gas | Compressor | Methanol | 1552 | NR | NR | 1552 | 1550 | 1110 | 3 | 1552 | NR | NR | .0263 | NR | NR | .0263 | .00342 | NR | NR | .00342 | .0000318 | NR | NR | .0000318 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14.2 | NR | NR | 848 | Engine 23 - Test 6. Post-maintenance, bad cam timing. | 68 | F | 1011 | Btu/scf | 3399 | NR | NR | 32 | 7.2 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 1370 | NR | NR | 1370
31 | 31.12x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-16 | 796 | HP | 101 | Clark | HRA-8 | Clark/HRA-8/796 MW / 101% | Natural Gas | Compressor | Methanol | 2421 | NR | NR | 2421 | 2420 | 982 | 3 | 2421 | NR | NR | .0397 | NR | NR | .0397 | .00517 | NR | NR | .00517 | .0000494 | NR | NR | .0000494 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14 | NR | NR | 848 | Engine 23 - Test 17. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3296 | NR | NR | 32 | 8.3 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 2070 | NR | NR | 2070
31 | 31.13x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 88 | Clark | HRA-8 | Clark/HRA-8/796 MW / 88% | Natural Gas | Compressor | Methanol | 1849 | NR | NR | 1849 | 1850 | 952 | 3 | 1849 | NR | NR | .028 | NR | NR | .028 | .00354 | NR | NR | .00354 | .00004 | NR | NR | .00004 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 704 | Engine 24 - Test 10. Pre-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 3040 | NR | NR | 32 | 8.6 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 1420 | NR | NR | 1420
31 | 31.14x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 89 | Clark | HRA-8 | Clark/HRA-8/796 MW / 89% | Natural Gas | Compressor | Methanol | 1799 | NR | NR | 1799 | 1800 | 960 | 3 | 1799 | NR | NR | .0282 | NR | NR | .0282 | .00345 | NR | NR | .00345 | .0000398 | NR | NR | .0000398 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 708 | Engine 24 - Test 11. Pre-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3151 | NR | NR | 32 | 8.3 | NR | NR | 1 | 0 | 1 | 89 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 1380 | NR | NR | 1380
31 | 31.15x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 91 | Clark | HRA-8 | Clark/HRA-8/796 MW / 91% | Natural Gas | Compressor | Methanol | 2048 | NR | NR | 2048 | 2050 | 953 | 3 | 2048 | NR | NR | .0325 | NR | NR | .0325 | .00419 | NR | NR | .00419 | .0000449 | NR | NR | .0000449 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.7 | NR | NR | 726 | Engine 24 - Test 3. Post-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 3188 | NR | NR | 32 | 7.7 | NR | NR | 1 | 0 | 1 | 91 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 1680 | NR | NR | 1680
31 | 31.16x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 89 | Clark | HRA-8 | Clark/HRA-8/796 MW / 89% | Natural Gas | Compressor | Methanol | 1753 | NR | NR | 1753 | 1750 | 931 | 3 | 1753 | NR | NR | .0277 | NR | NR | .0277 | .00369 | NR | NR | .00369 | .0000391 | NR | NR | .0000391 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.9 | NR | NR | 715 | Engine 24 - Test 4. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3176 | NR | NR | 32 | 7.6 | NR | NR | 1 | 0 | 1 | 89 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 1480 | NR | NR | 1480
31 | 31.17x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 2050 | HP | 99 | Clark | HBAT-8 | Clark/HBAT-8/2050 MW / 99% | Natural Gas | Compressor | Methanol | 1882 | NR | NR | 1882 | 1880 | 1420 | 3 | 1882 | NR | NR | .0533 | NR | NR | .0533 | .00302 | NR | NR | .00302 | .0000263 | NR | NR | .0000263 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 11.7 | NR | NR | 1929 | Engine 25 - Test 9. Pre-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 5684 | NR | NR | 32 | 4.9 | NR | NR | 1 | 0 | 1 | 99 | 2SLB | Turbo Charged |  | 8498 | 1 | 2050 | 1210 | NR | NR | 1210
31 | 31.5x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-18 | 1100 | HP | 81 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 81% | Natural Gas | Compressor | Methanol | 832 | NR | NR | 832 | 832 | 649 | 3 | 832 | NR | NR | .0179 | NR | NR | .0179 | .00212 | NR | NR | .00212 | .0000201 | NR | NR | .0000201 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 15.1 | NR | NR | 894 | Engine 2 - Test 1 | 68 | F | 1206 | Btu/scf | 4311 | NR | NR | 32 | 7.5 | NR | NR | 1 | 0 | 1 | 81 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 846 | NR | NR | 846
31 | 31.9x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 105 | Clark | HRA-8 | Clark/HRA-8/796 MW / 105% | Natural Gas | Compressor | Methanol | 2178 | NR | NR | 2178 | 2180 | 1089 | 3 | 2178 | NR | NR | .0306 | NR | NR | .0306 | .00382 | NR | NR | .00382 | .0000366 | NR | NR | .0000366 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.5 | NR | NR | 813 | Engine 23 - Test 12. Pre-maintenance and pre-balance. | 68 | F | 1011 | Btu/scf | 2826 | NR | NR | 32 | 9.1 | NR | NR | 1 | 0 | 1 | 105 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 1530 | NR | NR | 1530

## 2SLB-CO
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
105 | 105.1 | Exxon Company - Avery Island Field Wide Unit and Compressor Station No. 1 | EPA 10 | Iberia Parish, LA | Exxon Company - Avery Island Field Wide Unit and Compressor Station No. 1/Iberia Parish, LA | Emission Testing Services Inc. | 1992-12-09 | 880 | HP | 90 | Cooper Bessemer | GMV8TF | Cooper Bessemer/GMV8TF/880 MW / 90% | Natural Gas | NR | CO | 100900 | 102000 | 101800 | 101566.666666667 | 102000 | NA | 3 | 100900 | 102000 | 101800 | 1.36 | 1.36 | 1.35 | 1.36 | .185 | .187 | .184 | .185 | .00172 | .00172 | .0017 | .00171 | ppb | PCC | Eng. 003. Load Information in test report says 100%, but permit application shows it was really at 90% load | 13.7 | 13.7 | 13.6 | NR | Eng. 003. Load Information in test report says 100%, but permit application shows it was really at 90% load. PCC assumed because Nox < 100 ppm 3/99. | 68 | F | NR | NR | 3091.9 | 3056 | 3050.9 | 28 |  |  |  | 3 | 0 | 3 | 90 | 2SLB | NR | 8 | 8710 | 0 | 880 | 82700 | 83600 | 82300 | 82866.6666666667
109 | 109 | Texaco Pipeline Inc. - Lake Barre Crude Oil Pressure Boosting Station | EPA 10 | Cocodrie, LA | Texaco Pipeline Inc. - Lake Barre Crude Oil Pressure Boosting Station/Cocodrie, LA | Emission Testing Services Inc. | 1992-03-19 | 2200 | HP | 90 | MEP | 8GTX | MEP/8GTX/2200 MW / 90% | Natural Gas | NR | CO | 338400 | 346140 | 351500 | 345346.666666667 | 345000 | NA | 3 | 338400 | 346140 | 351500 | 9.38 | 9.34 | 9.79 | 9.5 | .506 | .525 | .536 | .522 | .00474 | .00472 | .00494 | .0048 | ppb | PCC | Fairbanks Morse TPLI Unit # 2 | 12.06 | 12.18 | 12.22 | NR | Fairbanks Morse TPLI Unit # 2. PCC identified 3/99 | 68 | F | 1142 | Btu/dscf | 6362 | 6193 | 6391.4 | 28 |  |  |  | 3 | 0 | 3 | 90 | 2SLB | Turbo Charged | 8 | 8710 | 0 | 2200 | 226000 | 234000 | 239000 | 233000
114 | 114.1 | Natural Fuel Gas Supply Corp. - Ellisburg Station | EPA 10 | Allegheny Township, Potter County, PA | Natural Fuel Gas Supply Corp. - Ellisburg Station/Allegheny Township, Potter County, PA | Engineering Science Inc. | 1991-07-11 | 3000 | HP | NR | Cooper Bessemer | 8Q15JHC2 | Cooper Bessemer/8Q15JHC2/3000 MW / NR% | Natural Gas | NR | CO | 212300 | 205600 | 210000 | 209300 | 209000 | NA | 3 | 212300 | 205600 | 210000 | 11 | 10.2 | 10.2 | 10.5 | .493 | .461 | .471 | .475 | .00367 | .0034 | .0034 | .00349 | ppb | Clean Burn Engine PCC | Eng. # 9. Tested at exhaust upstream of silencer. Designed for 685 Btu/HP.hr | 15.2 | 15 | 15 | NR | Eng. # 9. Tested at exhaust upstream of silencer. Designed for 685 Btu/HP.hr | 68 | F | NR | NR | 11887 | 11407 | 11150 | 28 |  |  |  | 3 | 0 | 3 | 0 | 2SLB | Turbo Charged | NR | 8710 | 0 | 3000 | 220000 | 206000 | 210000 | 212000
114 | 114.2 | Natural Fuel Gas Supply Corp. - Ellisburg Station | EPA 10 | Allegheny Township, Potter County, PA | Natural Fuel Gas Supply Corp. - Ellisburg Station/Allegheny Township, Potter County, PA | Engineering Science Inc. | 1991-07-12 | 3000 | HP | NR | Cooper Bessemer | 8Q15JHC2 | Cooper Bessemer/8Q15JHC2/3000 MW / NR% | Natural Gas | NR | CO | 246300 | 254200 | 241600 | 247366.666666667 | 247000 | NA | 3 | 246300 | 254200 | 241600 | 12.7 | 12.8 | 12.4 | 12.6 | .562 | .59 | .561 | .571 | .00423 | .00427 | .00413 | .00421 | ppb | Clean Burn Engine PCC | Eng. # 10. Tested at exhaust upstream of silencer. Designed for 685 Btu/HP.hr | 15.1 | 15.2 | 15.2 | NR | Eng. # 10. Tested at exhaust upstream of silencer. Designed for 685 Btu/HP.hr | 68 | F | NR | NR | 11817 | 11566 | 11765 | 28 |  |  |  | 3 | 0 | 3 | 0 | 2SLB | Turbo Charged | NR | 8710 | 0 | 3000 | 251000 | 263000 | 250000 | 254666.666666667
117 | 117 | Mobil Oil Corp. | EPA 10 | Chalmette, LA | Mobil Oil Corp./Chalmette, LA | Emission Testing Services Inc. | 1990-03-28 | 800 | HP | 100 | Cooper Bessemer | GMVA | Cooper Bessemer/GMVA/800 MW / 100% | Natural Gas | NR | CO | 159600 | 163800 | 236000 | 186466.666666667 | 186000 | NA | 3 | 159600 | 163800 | 236000 | 2.43 | 2.48 | 3.6 | 2.84 | .469 | .481 | .734 | .561 | .00304 | .0031 | .0045 | .00355 | ppb | PCC | FCC Compressor # 3 | 16.4 | 16.4 | 16.65 | NR | FCC Compressor # 3. PCC assumed due to low exhaust temps < 450F & O2 > 16% Assumed 3/99. | 68 | F | NR | NR | 3500.1 | 3476.5 | 3499.5 | 28 |  |  |  | 3 | 0 | 3 | 100 | 2SLB | NR | NR | 8710 | 0 | 800 | 209000 | 215000 | 328000 | 250666.666666667
132 | 132 | Tennessee Gas Pipeline Company | EPA 10 | Coudersport, PA | Tennessee Gas Pipeline Company/Coudersport, PA | Tennessee Gas Pipeline - Mechanical Division | 1986-04-09 | 2250 | HP | 93 | Cooper Bessemer | GMVH-10C | Cooper Bessemer/GMVH-10C/2250 MW / 93% | Natural Gas | NR | CO | 171100 | 179200 | 184300 | 178200 | 178000 | NA | 3 | 171100 | 179200 | 184300 | 6.02 | NR | NR | 6.02 | .388 | .401 | .41 | .4 | .00288 | NR | NR | .00288 | ppb | PCC | Unit 12A. Load based on tested HP/rated HP | 15.07 | 14.99 | 14.96 | NR | Unit 12A. Load based on tested HP/rated HP. PCC identified 3/99 | 68 | F | 1004 | Btu/dscf | 8070.8 | NR | NR | 28 |  |  |  | 3 | 0 | 3 | 93 | 2SLB | NR | NR | 8710 | 0 | 2250 | 173000 | 179000 | 183000 | 178333.333333333
138 | 138 | ARCO Sligo Facility | EPA 10 | Bossier City, LA | ARCO Sligo Facility/Bossier City, LA | CETCON | 1992-04-07 | 1000 | HP | 92 | Cooper Bessemer | GMVC | Cooper Bessemer/GMVC/1000 MW / 92% | Natural Gas | NR | CO | 49600 | 54000 | 48000 | 50533.3333333333 | 50500 | NA | 3 | 49600 | 54000 | 48000 | .946 | 1.03 | .891 | .956 | .117 | .128 | .111 | .119 | .00103 | .00112 | .000968 | .00104 | ppb | NR |  | 15.3 | 15.3 | 15.2 | 920 |  | 68 | F | 1004.5 | Btu/dscf | 4379 | 4367 | 4261 | 28 |  |  |  | 3 | 0 | 1 | 92 | 2SLB | Turbo Charged | NR | 8710 | 0 | 1000 | 52300 | 56900 | 49700 | 52966.6666666667
143 | 143 | Columbia Gulf Transmission Company - Rayne Compressor Station | EPA 10 | Rayne, LA | Columbia Gulf Transmission Company - Rayne Compressor Station/Rayne, LA | Entropy Environmentalists Inc. | 1992-03-17 | 2000 | HP | 100 | NR | GMWA -8 | NR/GMWA -8/2000 MW / 100% | Natural Gas | NR | CO | 52800 | 51200 | 52000 | 52000 | 52000 | NA | 3 | 52800 | 51200 | 52000 | 2.13 | 2.1 | 2.1 | 2.11 | .128 | .125 | .129 | .127 | .00106 | .00105 | .00105 | .00105 | ppb | NR |  | 15.49 | 15.52 | 15.6 | NR |  | 68 | F | NR | NR | 9265 | 9398 | 9268 | 28 |  |  |  | 3 | 0 | 1 | 100 | 2SLB | NR | NR | 8626 | 0 | 2000 | 57600 | 56100 | 57900 | 57200
145 | 145 | Texas Gas Transmission Corporation - Haughton compressor Station | EPA 10 | Haughton, LA | Texas Gas Transmission Corporation - Haughton compressor Station/Haughton, LA | Emission Testing Services Inc. | 1992-12-08 | 1000 | HP | 92 | Cooper Bessemer | GMVR | Cooper Bessemer/GMVR/1000 MW / 92% | Natural Gas | NR | CO | 153600 | 158600 | 162100 | 158100 | 158000 | NA | 3 | 153600 | 158600 | 162100 | 5.66 | 5.95 | 5.97 | 5.86 | .369 | .375 | .376 | .373 | .00615 | .00647 | .00649 | .00637 | ppb | PCC |  | 15.4 | 15.3 | 15.2 | 2002.7 | PCC assumed because NOx emissions < 100 ppm 3/99. | 68 | F | 1038.6 | Btu/dscf | 8456.2 | 8619.4 | 8461.6 | 28 |  |  |  | 3 | 0 | 3 | 92 | 2SLB | NR | NR | 8710 | 0 | 1000 | 165000 | 167000 | 168000 | 166666.666666667
149 | 149.1 | Transcontinental Gas Pipeline Corporation | EPA 10 | Bearcreek, PA | Transcontinental Gas Pipeline Corporation/Bearcreek, PA | Scott Environmental Services | 1992-01-07 | 3400 | HP | 100 | Cooper Bessemer | 10V250 | Cooper Bessemer/10V250/3400 MW / 100% | Natural Gas | NR | CO | 110600 | 107000 | 106800 | 108133.333333333 | 108000 | NA | 3 | 110600 | 107000 | 106800 | 6.8 | 6.49 | 6.38 | 6.56 | .235 | .227 | .229 | .23 | .002 | .00191 | .00188 | .00193 | ppb | PCC | # 5 Engine | 14.67 | 14.67 | 14.73 | NR | Engine # 5, PCC identified 3/99 | 68 | F | NR | NR | 14123 | 13930 | 13715 | 28 |  |  |  | 3 | 0 | 3 | 100 | 2SLB | NR | NR | 8710 | 0 | 3400 | 105000 | 101000 | 102000 | 102666.666666667
149 | 149.2 | Transcontinental Gas Pipeline Corporation | EPA 10 | Bearcreek, PA | Transcontinental Gas Pipeline Corporation/Bearcreek, PA | Scott Environmental Services | 1992-01-07 | 3400 | HP | 100 | Cooper Bessemer | 10V250 | Cooper Bessemer/10V250/3400 MW / 100% | Natural Gas | NR | CO | 117300 | 129700 | 129400 | 125466.666666667 | 125000 | NA | 3 | 117300 | 129700 | 129400 | 9.13 | 9.37 | 8.88 | 9.13 | .293 | .296 | .281 | .29 | .00269 | .00276 | .00261 | .00269 | ppb | PCC | # 5 Engine | 15.6 | 15.1 | 14.8 | NR | Engine # 5, PCC identified 3/99 | 68 | F | NR | NR | 17862 | 16587 | 15746 | 28 |  |  |  | 3 | 0 | 3 | 100 | 2SLB | NR | NR | 8710 | 0 | 3400 | 131000 | 132000 | 125000 | 129333.333333333
29 | 29.10x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | CO | 71100 | NR | NR | 71100 | 71100 | NA | 3 | 71100 | NR | NR | 2.4 | NR | NR | 2.4 | .149 | NR | NR | .149 | .00131 | NR | NR | .00131 | ppb | NR |  | 14.8 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7749 | NR | NR | 28 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 68800 | NR | NR | 68800
29 | 29.11x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-11 | 1800 | HP | 85 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 85% | Natural Gas | Gas Transmission | CO | 76200 | NR | NR | 76200 | 76200 | NA | 3 | 76200 | NR | NR | 2.91 | NR | NR | 2.91 | .181 | NR | NR | .181 | .0019 | NR | NR | .0019 | ppb | NR |  | 15.5 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 8769 | NR | NR | 28 | .069 | NR | NR | 1 | 0 | 1 | 85 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 83300 | NR | NR | 83300
29 | 29.12x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 100 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 100% | Natural Gas | Gas Transmission | CO | 63600 | NR | NR | 63600 | 63600 | NA | 3 | 63600 | NR | NR | 1.93 | NR | NR | 1.93 | .136 | NR | NR | .136 | .00107 | NR | NR | .00107 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6983 | NR | NR | 28 | .067 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 62500 | NR | NR | 62500
29 | 29.13x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 87 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 87% | Natural Gas | Gas Transmission | CO | 77900 | NR | NR | 77900 | 77900 | NA | 3 | 77900 | NR | NR | 2.33 | NR | NR | 2.33 | .178 | NR | NR | .178 | .00149 | NR | NR | .00149 | ppb | NR |  | 15.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6880 | NR | NR | 28 | .065 | NR | NR | 1 | 0 | 1 | 87 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 82100 | NR | NR | 82100
29 | 29.14x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 86 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 86% | Natural Gas | Gas Transmission | CO | 74000 | NR | NR | 74000 | 74000 | NA | 3 | 74000 | NR | NR | 2.01 | NR | NR | 2.01 | .169 | NR | NR | .169 | .0013 | NR | NR | .0013 | ppb | NR |  | 15.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6243 | NR | NR | 28 | .065 | NR | NR | 1 | 0 | 1 | 86 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 78000 | NR | NR | 78000
29 | 29.15x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 101 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 101% | Natural Gas | Gas Transmission | CO | 57000 | NR | NR | 57000 | 57000 | NA | 3 | 57000 | NR | NR | 1.57 | NR | NR | 1.57 | .116 | NR | NR | .116 | .000864 | NR | NR | .000864 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6312 | NR | NR | 28 | .07 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 53400 | NR | NR | 53400
29 | 29.16x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-15 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 95% | Natural Gas | Gas Transmission | CO | 65300 | NR | NR | 65300 | 65300 | NA | 3 | 65300 | NR | NR | 1.86 | NR | NR | 1.86 | .139 | NR | NR | .139 | .00109 | NR | NR | .00109 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 6528 | NR | NR | 28 | .068 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 1800 | 64200 | NR | NR | 64200
29 | 29.17x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 96 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 96% | Natural Gas | Gas Transmission | CO | 114000 | NR | NR | 114000 | 114000 | NA | 3 | 114000 | NR | NR | 6.51 | NR | NR | 6.51 | .235 | NR | NR | .235 | .00194 | NR | NR | .00194 | ppb | NR |  | 14.7 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 13104 | NR | NR | 28 | .069 | NR | NR | 1 | 0 | 1 | 96 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 108000 | NR | NR | 108000
29 | 29.18x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 95 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 95% | Natural Gas | Gas Transmission | CO | 119000 | NR | NR | 119000 | 119000 | NA | 3 | 119000 | NR | NR | 6.16 | NR | NR | 6.16 | .242 | NR | NR | .242 | .00185 | NR | NR | .00185 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 11888 | NR | NR | 28 | .071 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 111000 | NR | NR | 111000
29 | 29.19x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 88 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 88% | Natural Gas | Gas Transmission | CO | 94900 | NR | NR | 94900 | 94900 | NA | 3 | 94900 | NR | NR | 4.88 | NR | NR | 4.88 | .206 | NR | NR | .206 | .00158 | NR | NR | .00158 | ppb | NR |  | 15 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 11794 | NR | NR | 28 | .067 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 94900 | NR | NR | 94900
29 | 29.1x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 911 | HP | 94 | Clark | BA-5 | Clark/BA-5/911 MW / 94% | Natural Gas | Gas Transmission | CO | 86300 | NR | NR | 86300 | 86300 | NA | 3 | 86300 | NR | NR | 1.61 | NR | NR | 1.61 | .165 | NR | NR | .165 | .00188 | NR | NR | .00188 | ppb | NR |  | 14.2 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4272 | NR | NR | 28 | .104 | NR | NR | 1 | 0 | 1 | 94 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 911 | 76000 | NR | NR | 76000
29 | 29.20x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 91 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 91% | Natural Gas | Gas Transmission | CO | 105000 | NR | NR | 105000 | 105000 | NA | 3 | 105000 | NR | NR | 6.18 | NR | NR | 6.18 | .232 | NR | NR | .232 | .00194 | NR | NR | .00194 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 13514 | NR | NR | 28 | .068 | NR | NR | 1 | 0 | 1 | 91 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 107000 | NR | NR | 107000
29 | 29.21x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-14 | 3500 | HP | 92 | Cooper Bessemer | GMWC-10 | Cooper Bessemer/GMWC-10/3500 MW / 92% | Natural Gas | Gas Transmission | CO | 103000 | NR | NR | 103000 | 103000 | NA | 3 | 103000 | NR | NR | 5.82 | NR | NR | 5.82 | .227 | NR | NR | .227 | .00181 | NR | NR | .00181 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 12978 | NR | NR | 28 | .069 | NR | NR | 1 | 0 | 1 | 92 | 2SLB | Turbo Charged | 10 | 8431 | 1 | 3500 | 105000 | NR | NR | 105000
29 | 29.22x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-25 | 1800 | HP | 97 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 97% | Natural Gas | Gas Transmission | CO | 162000 | NR | NR | 162000 | 162000 | NA | 3 | 162000 | NR | NR | 4.88 | NR | NR | 4.88 | .386 | NR | NR | .386 | .00279 | NR | NR | .00279 | ppb | PCC Clean burn |  | 15.5 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6920 | NR | NR | 28 | .073 | NR | NR | 1 | 0 | 3 | 97 | 2SLB | Turbo Charged | 10 | 8470 | 1 | 1800 | 177000 | NR | NR | 177000
29 | 29.23x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-26 | 1800 | HP | 93 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 93% | Natural Gas | Gas Transmission | CO | 181000 | NR | NR | 181000 | 181000 | NA | 3 | 181000 | NR | NR | 5.41 | NR | NR | 5.41 | .423 | NR | NR | .423 | .00323 | NR | NR | .00323 | ppb | PCC Clean burn |  | 15.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 6866 | NR | NR | 28 | .073 | NR | NR | 1 | 0 | 3 | 93 | 2SLB | Turbo Charged | 10 | 8471 | 1 | 1800 | 194000 | NR | NR | 194000
29 | 29.24x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 95 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 95% | Natural Gas | Gas Transmission | CO | 178000 | NR | NR | 178000 | 178000 | NA | 3 | 178000 | NR | NR | 5.14 | NR | NR | 5.14 | .411 | NR | NR | .411 | .00301 | NR | NR | .00301 | ppb | PCC Clean burn |  | 15.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6633 | NR | NR | 28 | .082 | NR | NR | 1 | 0 | 3 | 95 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 188000 | NR | NR | 188000
29 | 29.25x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 1800 | HP | 79 | Cooper Bessemer | GMVC-10C | Cooper Bessemer/GMVC-10C/1800 MW / 79% | Natural Gas | Gas Transmission | CO | 237000 | NR | NR | 237000 | 237000 | NA | 3 | 237000 | NR | NR | 6.23 | NR | NR | 6.23 | .568 | NR | NR | .568 | .00438 | NR | NR | .00438 | ppb | PCC Clean burn |  | 15.5 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 6039 | NR | NR | 28 | .08 | NR | NR | 1 | 0 | 3 | 79 | 2SLB | Turbo Charged | 10 | 8518 | 1 | 1800 | 259000 | NR | NR | 259000
29 | 29.2x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 911 | HP | 100 | Clark | BA-5 | Clark/BA-5/911 MW / 100% | Natural Gas | Gas Transmission | CO | 92600 | NR | NR | 92600 | 92600 | NA | 3 | 92600 | NR | NR | 1.89 | NR | NR | 1.89 | .18 | NR | NR | .18 | .00207 | NR | NR | .00207 | ppb | NR |  | 14.3 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4679 | NR | NR | 28 | .08 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 911 | 82800 | NR | NR | 82800
29 | 29.3x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 911 | HP | 80 | Clark | BA-5 | Clark/BA-5/911 MW / 80% | Natural Gas | Gas Transmission | CO | 95500 | NR | NR | 95500 | 95500 | NA | 3 | 95500 | NR | NR | 1.81 | NR | NR | 1.81 | .204 | NR | NR | .204 | .00248 | NR | NR | .00248 | ppb | NR |  | 14.9 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4356 | NR | NR | 28 | .088 | NR | NR | 1 | 0 | 1 | 80 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 911 | 93900 | NR | NR | 93900
29 | 29.4x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-04 | 1000 | HP | 75 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 75% | Natural Gas | Gas Transmission | CO | 228000 | NR | NR | 228000 | 228000 | NA | 3 | 228000 | NR | NR | 4.73 | NR | NR | 4.73 | .561 | NR | NR | .561 | .00631 | NR | NR | .00631 | ppb | NR |  | 15.7 | NR | NR |  |  | 68 | F | 1025 | Btu/scf | 4759 | NR | NR | 28 | .068 | NR | NR | 1 | 0 | 1 | 75 | 2SLB | Naturally Aspirated | 5 | 8427 | 1 | 1000 | 259000 | NR | NR | 259000
29 | 29.5x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-05 | 1000 | HP | 84 | Clark | HBA-5 | Clark/HBA-5/1000 MW / 84% | Natural Gas | Gas Transmission | CO | 198000 | NR | NR | 198000 | 198000 | NA | 3 | 198000 | NR | NR | 3.98 | NR | NR | 3.98 | .438 | NR | NR | .438 | .00474 | NR | NR | .00474 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1021 | Btu/scf | 4617 | NR | NR | 28 | .069 | NR | NR | 1 | 0 | 1 | 84 | 2SLB | Naturally Aspirated | 5 | 8454 | 1 | 1000 | 201000 | NR | NR | 201000
29 | 29.6x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-11 | 1235 | HP | 88 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 88% | Natural Gas | Gas Transmission | CO | 69200 | NR | NR | 69200 | 69200 | NA | 3 | 69200 | NR | NR | 1.53 | NR | NR | 1.53 | .153 | NR | NR | .153 | .00141 | NR | NR | .00141 | ppb | NR |  | 15.1 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 5079 | NR | NR | 28 | .072 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 70400 | NR | NR | 70400
29 | 29.7x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-12 | 1235 | HP | 100 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 100% | Natural Gas | Gas Transmission | CO | 67600 | NR | NR | 67600 | 67600 | NA | 3 | 67600 | NR | NR | 1.43 | NR | NR | 1.43 | .137 | NR | NR | .137 | .00116 | NR | NR | .00116 | ppb | NR |  | 14.6 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 4845 | NR | NR | 28 | .083 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 63300 | NR | NR | 63300
29 | 29.8x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-12 | 1235 | HP | 100 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1235 MW / 100% | Natural Gas | Gas Transmission | CO | 67100 | NR | NR | 67100 | 67100 | NA | 3 | 67100 | NR | NR | 1.39 | NR | NR | 1.39 | .134 | NR | NR | .134 | .00113 | NR | NR | .00113 | ppb | NR |  | 14.5 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 4756 | NR | NR | 28 | .084 | NR | NR | 1 | 0 | 1 | 100 | 2SLB | Blower Scavenged | 10 | 8432 | 1 | 1235 | 61900 | NR | NR | 61900
29 | 29.9x | GRI Site 6 | FTIR | NR | GRI Site 6/NR | Radian Corporation | 1994-11-10 | 1800 | HP | 102 | Cooper Bessemer | GMVC-10 | Cooper Bessemer/GMVC-10/1800 MW / 102% | Natural Gas | Gas Transmission | CO | 71200 | NR | NR | 71200 | 71200 | NA | 3 | 71200 | NR | NR | 2.47 | NR | NR | 2.47 | .155 | NR | NR | .155 | .00135 | NR | NR | .00135 | ppb | NR |  | 15 | NR | NR |  |  | 68 | F | 1020 | Btu/scf | 7972 | NR | NR | 28 | .07 | NR | NR | 1 | 0 | 1 | 102 | 2SLB | Turbo Charged | 10 | 8432 | 1 | 1800 | 71200 | NR | NR | 71200
31 | 31.10x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 108 | Clark | HRA-8 | Clark/HRA-8/796 MW / 108% | Natural Gas | Compressor | CO | 538000 | NR | NR | 538000 | 538000 | 20000 | 3 | 538000 | NR | NR | 6.31 | NR | NR | 6.31 | .836 | NR | NR | .836 | .00734 | NR | NR | .00734 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.6 | NR | NR | 811 | Engine 23 - Test 13. Pre-maintenance and post-balance. | 68 | F | 1011 | Btu/scf | 2694 | NR | NR | 28 | 9.3 | NR | NR | 1 | 0 | 1 | 108 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 382000 | NR | NR | 382000
31 | 31.11x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 104 | Clark | HRA-8 | Clark/HRA-8/796 MW / 104% | Natural Gas | Compressor | CO | 188000 | NR | NR | 188000 | 188000 | 5000 | 3 | 188000 | NR | NR | 2.78 | NR | NR | 2.78 | .362 | NR | NR | .362 | .00336 | NR | NR | .00336 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14.2 | NR | NR | 848 | Engine 23 - Test 6. Post-maintenance, bad cam timing. | 68 | F | 1011 | Btu/scf | 3399 | NR | NR | 28 | 7.2 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 166000 | NR | NR | 166000
31 | 31.12x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-16 | 796 | HP | 101 | Clark | HRA-8 | Clark/HRA-8/796 MW / 101% | Natural Gas | Compressor | CO | 297000 | NR | NR | 297000 | 297000 | 5000 | 3 | 297000 | NR | NR | 4.26 | NR | NR | 4.26 | .555 | NR | NR | .555 | .0053 | NR | NR | .0053 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14 | NR | NR | 848 | Engine 23 - Test 17. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3296 | NR | NR | 28 | 8.3 | NR | NR | 1 | 0 | 1 | 101 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 254000 | NR | NR | 254000
31 | 31.13x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 88 | Clark | HRA-8 | Clark/HRA-8/796 MW / 88% | Natural Gas | Compressor | CO | 425000 | NR | NR | 425000 | 425000 | 20000 | 3 | 425000 | NR | NR | 5.63 | NR | NR | 5.63 | .712 | NR | NR | .712 | .00804 | NR | NR | .00804 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 704 | Engine 24 - Test 10. Pre-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 3040 | NR | NR | 28 | 8.6 | NR | NR | 1 | 0 | 1 | 88 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 326000 | NR | NR | 326000
31 | 31.14x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 89 | Clark | HRA-8 | Clark/HRA-8/796 MW / 89% | Natural Gas | Compressor | CO | 442000 | NR | NR | 442000 | 442000 | 20000 | 3 | 442000 | NR | NR | 6.07 | NR | NR | 6.07 | .741 | NR | NR | .741 | .00857 | NR | NR | .00857 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 708 | Engine 24 - Test 11. Pre-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3151 | NR | NR | 28 | 8.3 | NR | NR | 1 | 0 | 1 | 89 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 339000 | NR | NR | 339000
31 | 31.15x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 91 | Clark | HRA-8 | Clark/HRA-8/796 MW / 91% | Natural Gas | Compressor | CO | 476000 | NR | NR | 476000 | 476000 | 10000 | 3 | 476000 | NR | NR | 6.61 | NR | NR | 6.61 | .853 | NR | NR | .853 | .00913 | NR | NR | .00913 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.7 | NR | NR | 726 | Engine 24 - Test 3. Post-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 3188 | NR | NR | 28 | 7.7 | NR | NR | 1 | 0 | 1 | 91 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 390000 | NR | NR | 390000
31 | 31.16x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 796 | HP | 89 | Clark | HRA-8 | Clark/HRA-8/796 MW / 89% | Natural Gas | Compressor | CO | 372000 | NR | NR | 372000 | 372000 | 10000 | 3 | 372000 | NR | NR | 5.15 | NR | NR | 5.15 | .686 | NR | NR | .686 | .00727 | NR | NR | .00727 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.9 | NR | NR | 715 | Engine 24 - Test 4. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 3176 | NR | NR | 28 | 7.6 | NR | NR | 1 | 0 | 1 | 89 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 314000 | NR | NR | 314000
31 | 31.17x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 2050 | HP | 99 | Clark | HBAT-8 | Clark/HBAT-8/2050 MW / 99% | Natural Gas | Compressor | CO | 833000 | NR | NR | 833000 | 833000 | 20000 | 3 | 833000 | NR | NR | 20.6 | NR | NR | 20.6 | 1.17 | NR | NR | 1.17 | .0102 | NR | NR | .0102 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 11.7 | NR | NR | 1929 | Engine 25 - Test 9. Pre-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 5684 | NR | NR | 28 | 4.9 | NR | NR | 1 | 0 | 1 | 99 | 2SLB | Turbo Charged |  | 8498 | 1 | 2050 | 534000 | NR | NR | 534000
31 | 31.18x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 2050 | HP | 95 | Clark | HBAT-8 | Clark/HBAT-8/2050 MW / 95% | Natural Gas | Compressor | CO | 823000 | NR | NR | 823000 | 823000 | 10000 | 3 | 823000 | NR | NR | 20.2 | NR | NR | 20.2 | 1.3 | NR | NR | 1.3 | .0104 | NR | NR | .0104 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.7 | NR | NR | 1836 | Engine 25 - Test 1. Post-maintenance, pre-balance. | 68 | F | 1011 | Btu/scf | 5642 | NR | NR | 28 | 8.3 | NR | NR | 1 | 0 | 1 | 95 | 2SLB | Turbo Charged |  | 8498 | 1 | 2050 | 592000 | NR | NR | 592000
31 | 31.19x | GRI - Campaign 8 | FTIR | None | GRI - Campaign 8/None | Radian Corporation | 1995-11-10 | 2050 | HP | 94 | Clark | HBAT-8 | Clark/HBAT-8/2050 MW / 94% | Natural Gas | Compressor | CO | 799000 | NR | NR | 799000 | 799000 | 10000 | 3 | 799000 | NR | NR | 20 | NR | NR | 20 | 1.26 | NR | NR | 1.26 | .0104 | NR | NR | .0104 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.7 | NR | NR | 1819 | Engine 25 - Test 2. Post-maintenance, post-balance. | 68 | F | 1011 | Btu/scf | 5750 | NR | NR | 28 | 8.2 | NR | NR | 1 | 0 | 1 | 94 | 2SLB | Turbo Charged |  | 8498 | 1 | 2050 | 575000 | NR | NR | 575000
31 | 31.1x | GRI - Campaign 2 | FTIR | None | GRI - Campaign 2/None | Radian Corporation | 1994-03-12 | 1350 | HP | 73 | Cooper Bessemer | GMVA-10 | Cooper Bessemer/GMVA-10/1350 MW / 73% | Natural Gas | Drives Refrigeration Compressor | CO | 79000 | NR | NR | 79000 | 79000 | NA | 3 | 79000 | NR | NR | 2.08 | NR | NR | 2.08 | .185 | NR | NR | .185 | .00211 | NR | NR | .00211 | ppb | NR | Fuel factor is default given in calculations section of report | 15.4 | NR | NR | 984 | Cooper - Test 7 | 68 | F | 1012 | Btu/scf | 6050 | NR | NR | 28 | 5.7 | NR | NR | 1 | 0 | 1 | 73 | 2SLB | Blower Scavenged |  | 8498 | 1 | 1350 | 84700 | NR | NR | 84700
31 | 31.2x | GRI - Campaign 2 | FTIR | None | GRI - Campaign 2/None | Radian Corporation | 1994-03-13 | 1140 | HP | 87 | Clark | BA-6 | Clark/BA-6/1140 MW / 87% | Natural Gas | Gas Compression | CO | 356000 | NR | NR | 356000 | 356000 | NA | 3 | 356000 | NR | NR | 8.2 | NR | NR | 8.2 | .484 | NR | NR | .484 | .00827 | NR | NR | .00827 | ppb | NR | Fuel factor is default given in calculations section of report | 11.4 | NR | NR | 994 | Clark - Test 8 | 68 | F | 1012 | Btu/scf | 5291 | NR | NR | 28 | 9.0 | NR | NR | 1 | 0 | 1 | 87 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1140 | 221000 | NR | NR | 221000
31 | 31.3x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-18 | 2000 | HP | 98 | Cooper Bessemer | GMWA-8 | Cooper Bessemer/GMWA-8/2000 MW / 98% | Natural Gas | Compressor | CO | 53000 | NR | NR | 53000 | 53000 | 10000 | 3 | 53000 | NR | NR | 1.91 | NR | NR | 1.91 | .11 | NR | NR | .11 | .000974 | NR | NR | .000974 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 14.7 | NR | NR | 1958 | Engine 4 - Test 1 | 68 | F | 1206 | Btu/scf | 8290 | NR | NR | 28 | 9.3 | NR | NR | 1 | 0 | 1 | 98 | 2SLB | Blower Scavenged |  | 8498 | 1 | 2000 | 50400 | NR | NR | 50400
31 | 31.4x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-18 | 2000 | HP | 83 | Cooper Bessemer | GMWA-8 | Cooper Bessemer/GMWA-8/2000 MW / 83% | Natural Gas | Compressor | CO | 62300 | NR | NR | 62300 | 62300 | 10000 | 3 | 62300 | NR | NR | 2.3 | NR | NR | 2.3 | .146 | NR | NR | .146 | .00139 | NR | NR | .00139 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 15.4 | NR | NR | 1655 | Engine 4 - Test 2 | 68 | F | 1206 | Btu/scf | 8462 | NR | NR | 28 | 7.8 | NR | NR | 1 | 0 | 1 | 83 | 2SLB | Blower Scavenged |  | 8498 | 1 | 2000 | 66800 | NR | NR | 66800
31 | 31.5x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-18 | 1100 | HP | 81 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 81% | Natural Gas | Compressor | CO | 125000 | NR | NR | 125000 | 125000 | 10000 | 3 | 125000 | NR | NR | 2.35 | NR | NR | 2.35 | .278 | NR | NR | .278 | .00264 | NR | NR | .00264 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 15.1 | NR | NR | 894 | Engine 2 - Test 1 | 68 | F | 1206 | Btu/scf | 4311 | NR | NR | 28 | 7.5 | NR | NR | 1 | 0 | 1 | 81 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 127000 | NR | NR | 127000
31 | 31.6x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-19 | 1100 | HP | 104 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 104% | Natural Gas | Compressor | CO | 81000 | NR | NR | 81000 | 81000 | 10000 | 3 | 81000 | NR | NR | 1.37 | NR | NR | 1.37 | .132 | NR | NR | .132 | .0012 | NR | NR | .0012 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.0 | NR | NR | 1145 | Engine 2 - Test 2 | 68 | F | 1204 | Btu/scf | 3885 | NR | NR | 28 | 10.3 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 60500 | NR | NR | 60500
31 | 31.7x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-19 | 1100 | HP | 104 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 104% | Natural Gas | Compressor | CO | 80400 | NR | NR | 80400 | 80400 | 10000 | 3 | 80400 | NR | NR | 1.36 | NR | NR | 1.36 | .131 | NR | NR | .131 | .00119 | NR | NR | .00119 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.0 | NR | NR | 1142 | Engine 2 - Test 3 | 68 | F | 1204 | Btu/scf | 3890 | NR | NR | 28 | 9.3 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 60000 | NR | NR | 60000
31 | 31.8x | GRI - Campaign 3B | FTIR | None | GRI - Campaign 3B/None | Radian Corporation | 1994-06-20 | 1100 | HP | 104 | Cooper Bessemer | GMV-10TF | Cooper Bessemer/GMV-10TF/1100 MW / 104% | Natural Gas | Compressor | CO | 83700 | NR | NR | 83700 | 83700 | 10000 | 3 | 83700 | NR | NR | 1.41 | NR | NR | 1.41 | .14 | NR | NR | .14 | .00123 | NR | NR | .00123 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 13.2 | NR | NR | 1146 | Engine 2 - Test 4 | 68 | F | 1205 | Btu/scf | 3868 | NR | NR | 28 | 7.8 | NR | NR | 1 | 0 | 1 | 104 | 2SLB | Piston Scavenged |  | 8498 | 1 | 1100 | 64100 | NR | NR | 64100
31 | 31.9x | GRI - Campaign 7 | FTIR | None | GRI - Campaign 7/None | Radian Corporation | 1995-05-21 | 796 | HP | 105 | Clark | HRA-8 | Clark/HRA-8/796 MW / 105% | Natural Gas | Compressor | CO | 994000 | NR | NR | 994000 | 994000 | 20000 | 3 | 994000 | NR | NR | 12.2 | NR | NR | 12.2 | 1.53 | NR | NR | 1.53 | .0146 | NR | NR | .0146 | ppb | NR | Fuel factor is default given in calculations section of report. Exhaust Gas Flowrate is based on fuel factor calculated from fuel analysis. | 12.5 | NR | NR | 813 | Engine 23 - Test 12. Pre-maintenance and pre-balance. | 68 | F | 1011 | Btu/scf | 2826 | NR | NR | 28 | 9.1 | NR | NR | 1 | 0 | 1 | 105 | 2SLB | Naturally Aspirated |  | 8498 | 1 | 796 | 698000 | NR | NR | 698000

## 4SLB-acetaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
25 | 25.2 | Naval Petroleum Reserve #1 | CARB 430 | Elk Hills, CA | Naval Petroleum Reserve #1/Elk Hills, CA | Petro Chem Environmental Services Inc. | 1992-02-02 | 5500 | HP | 70 | Ingersoll Rand | KVR 616 | Ingersoll Rand/KVR 616/5500 MW / 70% | Natural Gas | NR | Acetaldehyde | ND | 120. | 764 | 299 | 299 | 26 | 3 | 13 | 120. | 764 | .00148 | .0137 | .0869 | .034 | .0000381 | .000349 | .00218 | .000856 | .000000384 | .00000356 | .0000226 | .00000885 | ppb | PCC | Test reported 1/2 DL as concentrations. Corrected to ND with full DL | 13.8 | 13.75 | 13.6 | NR |  | 68 | F | NR | Btu/dscf | 16624 | 16624 | 16624 | 44 |  |  |  | 3 | 1 | 3 | 70 | 4SLB | Turbo Charged | 16 | 8710 | 2 | 5500 | ND | 99 | 617 | 243
29 | 29.41x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-29 | 2000 | HP | 91 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 91% | Natural Gas | Gas Transmission | Acetaldehyde | 2530 | NR | NR | 2530 | 2530 | 5760 | 3 | 2530 | NR | NR | .065 | NR | NR | .065 | .00408 | NR | NR | .00408 | .0000357 | NR | NR | .0000357 | ppb | NR |  | 8.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 3754 | NR | NR | 44 | .144 | NR | NR | 1 | 0 | 1 | 91 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1180 | NR | NR | 1180
29 | 29.44x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-27 | 2000 | HP | 89 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 89% | Natural Gas | Gas Transmission | Acetaldehyde | 4030 | NR | NR | 4030 | 4030 | 11710 | 3 | 4030 | NR | NR | .137 | NR | NR | .137 | .00848 | NR | NR | .00848 | .000077 | NR | NR | .000077 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4975 | NR | NR | 44 | .111 | NR | NR | 1 | 0 | 3 | 89 | 4SLB | Turbo Charged | 12 | 8470 | 1 | 2000 | 2480 | NR | NR | 2480

## 4SLB-acrolein
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
25 | 25.2 | Naval Petroleum Reserve #1 | CARB 430 | Elk Hills, CA | Naval Petroleum Reserve #1/Elk Hills, CA | Petro Chem Environmental Services Inc. | 1992-02-02 | 5500 | HP | 70 | Ingersoll Rand | KVR 616 | Ingersoll Rand/KVR 616/5500 MW / 70% | Natural Gas | NR | Acrolein | ND | ND | 37 | 21.6666666666667 | 21.7 | 28 | 3 | 14 | 14 | 37 | .00203 | .00203 | .00536 | .00314 | .0000522 | .0000518 | .000134 | .0000793 | .000000527 | .000000527 | .00000139 | .000000815 | ppb | PCC | Test reported 1/2 DL as concentrations. Corrected to ND with full DL | 13.8 | 13.75 | 13.6 | NR |  | 68 | F | NR | Btu/dscf | 16624 | 16624 | 16624 | 56 |  |  |  | 3 | 2 | 3 | 70 | 4SLB | Turbo Charged | 16 | 8710 | 2 | 5500 | ND | ND | 29.9 | 19.3
29 | 29.46x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 92 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 92% | Natural Gas | Gas Transmission | Acrolein | 1610 | NR | NR | 1610 | 1610 | 6530 | 3 | 1610 | NR | NR | .0691 | NR | NR | .0691 | .00434 | NR | NR | .00434 | .0000376 | NR | NR | .0000376 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4927 | NR | NR | 56 | .12 | NR | NR | 1 | 0 | 3 | 92 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 989 | NR | NR | 989
29 | 29.47x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 85 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 85% | Natural Gas | Gas Transmission | Acrolein | 1860 | NR | NR | 1860 | 1860 | 6530 | 3 | 1860 | NR | NR | .0807 | NR | NR | .0807 | .00512 | NR | NR | .00512 | .0000475 | NR | NR | .0000475 | ppb | PCC |  | 11.5 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4978 | NR | NR | 56 | .118 | NR | NR | 1 | 0 | 3 | 85 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1170 | NR | NR | 1170
29 | 29.48x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 84 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 84% | Natural Gas | Gas Transmission | Acrolein | 1660 | NR | NR | 1660 | 1660 | 6530 | 3 | 1660 | NR | NR | .0756 | NR | NR | .0756 | .00462 | NR | NR | .00462 | .000045 | NR | NR | .000045 | ppb | PCC |  | 11.6 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5229 | NR | NR | 56 | .117 | NR | NR | 1 | 0 | 3 | 84 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1050 | NR | NR | 1050
29 | 29.49x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | Acrolein | 1880 | NR | NR | 1880 | 1880 | 6530 | 3 | 1880 | NR | NR | .0842 | NR | NR | .0842 | .00512 | NR | NR | .00512 | .0000478 | NR | NR | .0000478 | ppb | PCC |  | 11.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5143 | NR | NR | 56 | .118 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1170 | NR | NR | 1170
29 | 29.50x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | Acrolein | 2310 | NR | NR | 2310 | 2310 | 6530 | 3 | 2310 | NR | NR | .101 | NR | NR | .101 | .00616 | NR | NR | .00616 | .0000574 | NR | NR | .0000574 | ppb | PCC |  | 11.2 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5040 | NR | NR | 56 | .119 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1410 | NR | NR | 1410
29 | 29.51x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 87 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 87% | Natural Gas | Gas Transmission | Acrolein | 2300 | NR | NR | 2300 | 2300 | 6530 | 3 | 2300 | NR | NR | .0918 | NR | NR | .0918 | .00607 | NR | NR | .00607 | .0000528 | NR | NR | .0000528 | ppb | PCC |  | 11.1 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4582 | NR | NR | 56 | .121 | NR | NR | 1 | 0 | 3 | 87 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1380 | NR | NR | 1380
29 | 29.52x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 80 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 80% | Natural Gas | Gas Transmission | Acrolein | 2400 | NR | NR | 2400 | 2400 | NA | 3 | 2400 | NR | NR | .0955 | NR | NR | .0955 | .00647 | NR | NR | .00647 | .0000597 | NR | NR | .0000597 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4567 | NR | NR | 56 | .118 | NR | NR | 1 | 0 | 3 | 80 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1480 | NR | NR | 1480

## 4SLB-formaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
21 | 21 | Texaco Exploration & Production, Inc. | CARB 430 | Ferndale, WA | Texaco Exploration & Production, Inc./Ferndale, WA | Emissions Technologies Inc. | 1995-06-27 | 1000 | HP | 100 | Waukesha | 7042-GL | Waukesha/7042-GL/1000 MW / 100% | Natural Gas | NR | Formaldehyde | 24250 | 13190 | 16670 | 18036.6666666667 | 18000 | NA | 3 | 24250 | 13190 | 16670 | .0443 | .0243 | .0303 | 0.033 | .0296 | .0161 | .0204 | .022 | .0000443 | .0000243 | .0000303 | .000033 | ppb | NR |  | 9.28 | 9.30 | 9.30 | NR | Engine type information updated thanks to call to WA State Air Pollution Dept. Std Temp Assumed as 68. Gas flow calculated from MMBtu/hr. | 68 | F | NR | Btu/dscf | 391 | 395 | 390 | 30 |  |  |  | 3 | 0 | 1 | 100 | 4SLB | NR | NR | 8710 | 2 | 1000 | 12300 | 6710 | 8480 | 9163.33333333333
25 | 25.2 | Naval Petroleum Reserve #1 | CARB 430 | Elk Hills, CA | Naval Petroleum Reserve #1/Elk Hills, CA | Petro Chem Environmental Services Inc. | 1992-02-02 | 5500 | HP | 70 | Ingersoll Rand | KVR 616 | Ingersoll Rand/KVR 616/5500 MW / 70% | Natural Gas | NR | Formaldehyde | 4297 | 8815 | 4308 | 5806.66666666667 | 5810 | NA | 3 | 4297 | 8815 | 4308 | .333 | .684 | .334 | .45 | .00858 | .0175 | .00836 | .0115 | .0000865 | .000178 | .0000868 | .000117 | ppb | PCC |  | 13.8 | 13.75 | 13.6 | NR |  | 68 | F | NR | Btu/dscf | 16624 | 16624 | 16624 | 30 |  |  |  | 3 | 0 | 3 | 70 | 4SLB | Turbo Charged | 16 | 8710 | 2 | 5500 | 3570 | 7270 | 3480 | 4773.33333333333
29 | 29.34x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 101 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 101% | Natural Gas | Gas Transmission | Formaldehyde | 31100 | NR | NR | 31100 | 31100 | 1250 | 3 | 31100 | NR | NR | 1.26 | NR | NR | 1.26 | .0374 | NR | NR | .0374 | .000297 | NR | NR | .000297 | ppb | NR |  | 9.4 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8678 | NR | NR | 30 | .141 | NR | NR | 1 | 0 | 1 | 101 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 16000 | NR | NR | 16000
29 | 29.35x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 87 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 87% | Natural Gas | Gas Transmission | Formaldehyde | 35300 | NR | NR | 35300 | 35300 | 1250 | 3 | 35300 | NR | NR | 1.24 | NR | NR | 1.24 | .0444 | NR | NR | .0444 | .000339 | NR | NR | .000339 | ppb | NR |  | 9.9 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 7526 | NR | NR | 30 | .119 | NR | NR | 1 | 0 | 1 | 87 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 18900 | NR | NR | 18900
29 | 29.36x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 85 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 85% | Natural Gas | Gas Transmission | Formaldehyde | 33000 | NR | NR | 33000 | 33000 | 1490 | 3 | 33000 | NR | NR | 1.32 | NR | NR | 1.32 | .0461 | NR | NR | .0461 | .00037 | NR | NR | .00037 | ppb | NR |  | 11 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8581 | NR | NR | 30 | .122 | NR | NR | 1 | 0 | 1 | 85 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 19700 | NR | NR | 19700
29 | 29.37x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-16 | 4200 | HP | 98 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 98% | Natural Gas | Gas Transmission | Formaldehyde | 33100 | NR | NR | 33100 | 33100 | 1490 | 3 | 33100 | NR | NR | 1.3 | NR | NR | 1.3 | .0402 | NR | NR | .0402 | .000316 | NR | NR | .000316 | ppb | NR |  | 9.5 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8421 | NR | NR | 30 | .135 | NR | NR | 1 | 0 | 1 | 98 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 17100 | NR | NR | 17100
29 | 29.38x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-16 | 4200 | HP | 99 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 99% | Natural Gas | Gas Transmission | Formaldehyde | 31200 | NR | NR | 31200 | 31200 | 1490 | 3 | 31200 | NR | NR | 1.22 | NR | NR | 1.22 | .0372 | NR | NR | .0372 | .000293 | NR | NR | .000293 | ppb | NR |  | 9.3 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8409 | NR | NR | 30 | .135 | NR | NR | 1 | 0 | 1 | 99 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 15900 | NR | NR | 15900
29 | 29.41x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-29 | 2000 | HP | 91 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 91% | Natural Gas | Gas Transmission | Formaldehyde | 10000 | NR | NR | 10000 | 10000 | 1170 | 3 | 10000 | NR | NR | .175 | NR | NR | .175 | .011 | NR | NR | .011 | .0000962 | NR | NR | .0000962 | ppb | NR |  | 8.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 3754 | NR | NR | 30 | .144 | NR | NR | 1 | 0 | 1 | 91 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 4680 | NR | NR | 4680
29 | 29.44x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-27 | 2000 | HP | 89 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 89% | Natural Gas | Gas Transmission | Formaldehyde | 33400 | NR | NR | 33400 | 33400 | 2380 | 3 | 33400 | NR | NR | .775 | NR | NR | .775 | .0479 | NR | NR | .0479 | .000435 | NR | NR | .000435 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4975 | NR | NR | 30 | .111 | NR | NR | 1 | 0 | 3 | 89 | 4SLB | Turbo Charged | 12 | 8470 | 1 | 2000 | 20500 | NR | NR | 20500
29 | 29.45x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-27 | 2000 | HP | 82 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 82% | Natural Gas | Gas Transmission | Formaldehyde | 45800 | NR | NR | 45800 | 45800 | 2380 | 3 | 45800 | NR | NR | 1.01 | NR | NR | 1.01 | .0664 | NR | NR | .0664 | .000616 | NR | NR | .000616 | ppb | PCC |  | 11.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4706 | NR | NR | 30 | .111 | NR | NR | 1 | 0 | 3 | 82 | 4SLB | Turbo Charged | 12 | 8470 | 1 | 2000 | 28400 | NR | NR | 28400
29 | 29.46x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 92 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 92% | Natural Gas | Gas Transmission | Formaldehyde | 41400 | NR | NR | 41400 | 41400 | 2380 | 3 | 41400 | NR | NR | .952 | NR | NR | .952 | .0598 | NR | NR | .0598 | .000517 | NR | NR | .000517 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4927 | NR | NR | 30 | .12 | NR | NR | 1 | 0 | 3 | 92 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 25400 | NR | NR | 25400
29 | 29.47x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 85 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 85% | Natural Gas | Gas Transmission | Formaldehyde | 49400 | NR | NR | 49400 | 49400 | 2380 | 3 | 49400 | NR | NR | 1.15 | NR | NR | 1.15 | .0728 | NR | NR | .0728 | .000676 | NR | NR | .000676 | ppb | PCC |  | 11.5 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4978 | NR | NR | 30 | .118 | NR | NR | 1 | 0 | 3 | 85 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 31000 | NR | NR | 31000
29 | 29.48x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 84 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 84% | Natural Gas | Gas Transmission | Formaldehyde | 48200 | NR | NR | 48200 | 48200 | 2380 | 3 | 48200 | NR | NR | 1.18 | NR | NR | 1.18 | .0718 | NR | NR | .0718 | .000702 | NR | NR | .000702 | ppb | PCC |  | 11.6 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5229 | NR | NR | 30 | .117 | NR | NR | 1 | 0 | 3 | 84 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 30600 | NR | NR | 30600
29 | 29.49x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | Formaldehyde | 43100 | NR | NR | 43100 | 43100 | 2380 | 3 | 43100 | NR | NR | 1.03 | NR | NR | 1.03 | .0629 | NR | NR | .0629 | .000585 | NR | NR | .000585 | ppb | PCC |  | 11.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5143 | NR | NR | 30 | .118 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 26800 | NR | NR | 26800
29 | 29.50x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | Formaldehyde | 45600 | NR | NR | 45600 | 45600 | 2380 | 3 | 45600 | NR | NR | 1.07 | NR | NR | 1.07 | .0651 | NR | NR | .0651 | .000608 | NR | NR | .000608 | ppb | PCC |  | 11.2 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5040 | NR | NR | 30 | .119 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 27700 | NR | NR | 27700
29 | 29.51x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 87 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 87% | Natural Gas | Gas Transmission | Formaldehyde | 44300 | NR | NR | 44300 | 44300 | 2380 | 3 | 44300 | NR | NR | .947 | NR | NR | .947 | .0626 | NR | NR | .0626 | .000544 | NR | NR | .000544 | ppb | PCC |  | 11.1 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4582 | NR | NR | 30 | .121 | NR | NR | 1 | 0 | 3 | 87 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 26700 | NR | NR | 26700
29 | 29.52x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 80 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 80% | Natural Gas | Gas Transmission | Formaldehyde | 50200 | NR | NR | 50200 | 50200 | NA | 3 | 50200 | NR | NR | 1.07 | NR | NR | 1.07 | .0725 | NR | NR | .0725 | .000669 | NR | NR | .000669 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4567 | NR | NR | 30 | .118 | NR | NR | 1 | 0 | 3 | 80 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 30900 | NR | NR | 30900
3 | 3.11 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 100 | Dresser-Rand | KVS-412 | Dresser-Rand/KVS-412/2000 MW / 100% | Natural Gas | NR | Formaldehyde | 4300 | 4300 | 4300 | 4300 | 4300 | NA | 3 | 4300 | 4300 | 4300 | .165 | .165 | .165 | .165 | .0053 | .0053 | .0053 | .0053 | .0000825 | .0000825 | .0000825 | .0000825 | ppb | SCR | #D | 9.4 | 9.4 | 9.4 | NR | #D | 68 | F | NR | Btu/dscf | 8241.007 | 8241.007 | 8241.007 | 30 |  |  |  | 3 | 0 | 5 | 100 | 4SLB | NR | 12 | 8710 | 2 | 2000 | 2210 | 2210 | 2210 | 2210
3 | 3.12 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 90 | Dresser-Rand | KVS-412 | Dresser-Rand/KVS-412/2000 MW / 90% | Natural Gas | NR | Formaldehyde | 4800 | 4800 | 4800 | 4800 | 4800 | NA | 3 | 4800 | 4800 | 4800 | .195 | .195 | .195 | .195 | .00618 | .00618 | .00618 | .00618 | .000108 | .000108 | .000108 | .000108 | ppb | NR | #D | 9.9 | 9.9 | 9.9 | NR | #D. Tested at SCR Inlet. | 68 | F | NR | Btu/dscf | 8710.588 | 8710.588 | 8710.588 | 30 |  |  |  | 3 | 0 | 1 | 90 | 4SLB | NR | 12 | 8710 | 2 | 2000 | 2570 | 2570 | 2570 | 2570
3 | 3.7 | California Gas Transmission and Storage Facilities | CARB 430 | NR | California Gas Transmission and Storage Facilities/NR | Huey,S and Castaldini,C | 1992-10-01 | 2000 | HP | 100 | Dresser-Rand | KVS-412 | Dresser-Rand/KVS-412/2000 MW / 100% | Natural Gas | NR | Formaldehyde | 15000 | 15000 | 15000 | 15000 | 15000 | NA | 3 | 15000 | 15000 | 15000 | .593 | .593 | .593 | .593 | .0242 | .0242 | .0242 | .0242 | .000296 | .000296 | .000296 | .000296 | ppb | PCC | #C. Runs are average of three runs (individual concentrations not available) | 12.1 | 12.1 | 12.1 | NR | #C | 68 | F | NR | Btu/dscf | 8465.432 | 8465.432 | 8465.432 | 30 |  |  |  | 3 | 0 | 3 | 100 | 4SLB | NR | 12 | 8710 | 2 | 2000 | 10100 | 10100 | 10100 | 10100
CSU-2 | CSU-2.1.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-04 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 64207.52 | NR | NR | 64207.52 | 64200 | 790 | 5 | 64207.52 | NR | NR | .50043 | NR | NR | .50043 | .081439 | NR | NR | .081439 | .00067993 | NR | NR | .00067993 | ppb | NR |  | 9.80 | NR | NR | 736 |  | 68 | F | 1135 | Btu/dscf | 1670 |  |  | 30 | 0.123 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8654 | 1 | 736 | 34128 | NR | NR | 34128
CSU-2 | CSU-2.10.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 64686.00 | NR | NR | 64686 | 64700 | 790 | 5 | 64686.00 | NR | NR | .48242 | NR | NR | .48242 | .081961 | NR | NR | .081961 | .00065546 | NR | NR | .00065546 | ppb | NR |  | 9.80 | NR | NR | 735 |  | 68 | F | 1095 | Btu/dscf | 1598 |  |  | 30 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 1 | 736 | 34383 | NR | NR | 34383
CSU-2 | CSU-2.11.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 63823.46 | NR | NR | 63823.46 | 63800 | 790 | 5 | 63823.46 | NR | NR | .47748 | NR | NR | .47748 | .080941 | NR | NR | .080941 | .00064875 | NR | NR | .00064875 | ppb | NR |  | 9.81 | NR | NR | 735 |  | 68 | F | 1095 | Btu/dscf | 1603 |  |  | 30 | 0.122 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 1 | 736 | 33955 | NR | NR | 33955
CSU-2 | CSU-2.12.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 65230.06 | NR | NR | 65230.06 | 65200 | 790 | 5 | 65230.06 | NR | NR | .49744 | NR | NR | .49744 | .083402 | NR | NR | .083402 | .00067587 | NR | NR | .00067587 | ppb | NR |  | 9.90 | NR | NR | 735 |  | 68 | F | 1095 | Btu/dscf | 1634 |  |  | 30 | 0.122 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 1 | 736 | 34987 | NR | NR | 34987
CSU-2 | CSU-2.13.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 65138.79 | NR | NR | 65138.79 | 65100 | 790 | 5 | 65138.79 | NR | NR | .57791 | NR | NR | .57791 | .087686 | NR | NR | .087686 | .0007852 | NR | NR | .0007852 | ppb | NR |  | 10.44 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1901 |  |  | 30 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 1 | 736 | 36742 | NR | NR | 36742
CSU-2 | CSU-2.14.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-04 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 63794.08 | NR | NR | 63794.08 | 63800 | 790 | 5 | 63794.08 | NR | NR | .48798 | NR | NR | .48798 | .080988 | NR | NR | .080988 | .00066302 | NR | NR | .00066302 | ppb | NR |  | 9.81 | NR | NR | 736 |  | 68 | F | 1135 | Btu/dscf | 1639 |  |  | 30 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8654 | 1 | 736 | 33939 | NR | NR | 33939
CSU-2 | CSU-2.15.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 65443.68 | NR | NR | 65443.68 | 65400 | 790 | 5 | 65443.68 | NR | NR | .52961 | NR | NR | .52961 | .083771 | NR | NR | .083771 | .00071958 | NR | NR | .00071958 | ppb | NR |  | 9.90 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1734 |  |  | 30 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 1 | 736 | 35102 | NR | NR | 35102
CSU-2 | CSU-2.16.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 65427.75 | NR | NR | 65427.75 | 65400 | 790 | 5 | 65427.75 | NR | NR | .51819 | NR | NR | .51819 | .083146 | NR | NR | .083146 | .00070406 | NR | NR | .00070406 | ppb | NR |  | 9.82 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1697 |  |  | 30 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 1 | 736 | 34840 | NR | NR | 34840
CSU-2 | CSU-2.2.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 70 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 70% | Natural Gas | NR | Formaldehyde | 68802.94 | NR | NR | 68802.94 | 68800 | 820 | 5 | 68802.94 | NR | NR | .39303 | NR | NR | .39303 | .087335 | NR | NR | .087335 | .00076287 | NR | NR | .00076287 | ppb | NR |  | 9.82 | NR | NR | 515 |  | 68 | F | 1095 | Btu/dscf | 1224 |  |  | 30 | 0.117 |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 6 | 8645 | 1 | 736 | 36637 | NR | NR | 36637
CSU-2 | CSU-2.3.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 70 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 70% | Natural Gas | NR | Formaldehyde | 65712.65 | NR | NR | 65712.65 | 65700 | 820 | 5 | 65712.65 | NR | NR | .31006 | NR | NR | .31006 | .083433 | NR | NR | .083433 | .00060182 | NR | NR | .00060182 | ppb | NR |  | 9.81 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1011 |  |  | 30 | 0.123 |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 6 | 8655 | 1 | 736 | 34960 | NR | NR | 34960
CSU-2 | CSU-2.4.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 62782.95 | NR | NR | 62782.95 | 62800 | 820 | 5 | 62782.95 | NR | NR | .38297 | NR | NR | .38297 | .07955 | NR | NR | .07955 | .00052034 | NR | NR | .00052034 | ppb | NR |  | 9.80 | NR | NR | 617 |  | 68 | F | 1095 | Btu/dscf | 1307 |  |  | 30 | 0.12 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 1 | 736 | 33371 | NR | NR | 33371
CSU-2 | CSU-2.5.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 74043.18 | NR | NR | 74043.18 | 74000 | 880 | 5 | 74043.18 | NR | NR | .64275 | NR | NR | .64275 | .10034 | NR | NR | .10034 | .0008733 | NR | NR | .0008733 | ppb | NR |  | 10.51 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1860 |  |  | 30 | 0.12 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 1 | 736 | 42046 | NR | NR | 42046
CSU-2 | CSU-2.6.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 67666.66 | NR | NR | 67666.66 | 67700 | 780 | 5 | 67666.66 | NR | NR | .49992 | NR | NR | .49992 | .080745 | NR | NR | .080745 | .00067924 | NR | NR | .00067924 | ppb | NR |  | 9.10 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1583 |  |  | 30 | 0.127 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 1 | 736 | 33833 | NR | NR | 33833
CSU-2 | CSU-2.7.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 70 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 70% | Natural Gas | NR | Formaldehyde | 75171.23 | NR | NR | 75171.23 | 75200 | 860 | 5 | 75171.23 | NR | NR | .4024 | NR | NR | .4024 | .090362 | NR | NR | .090362 | .00078106 | NR | NR | .00078106 | ppb | NR |  | 9.20 | NR | NR | 515 |  | 68 | F | 1095 | Btu/dscf | 1147 |  |  | 30 | 0.124 |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 6 | 8645 | 1 | 736 | 37907 | NR | NR | 37907
CSU-2 | CSU-2.8.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 65578.05 | NR | NR | 65578.05 | 65600 | 860 | 5 | 65578.05 | NR | NR | .43246 | NR | NR | .43246 | .088684 | NR | NR | .088684 | .00058758 | NR | NR | .00058758 | ppb | NR |  | 10.50 | NR | NR | 616 |  | 68 | F | 1095 | Btu/dscf | 1413 |  |  | 30 | 0.116 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 1 | 736 | 37203 | NR | NR | 37203
CSU-2 | CSU-2.9.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-04 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | Formaldehyde | 64231.47 | NR | NR | 64231.47 | 64200 | 790 | 5 | 64231.47 | NR | NR | .49672 | NR | NR | .49672 | .08067 | NR | NR | .08067 | .00067489 | NR | NR | .00067489 | ppb | NR |  | 9.69 | NR | NR | 736 |  | 68 | F | 1135 | Btu/dscf | 1657 |  |  | 30 | 0.123 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8654 | 1 | 736 | 33806 | NR | NR | 33806

## 4SLB-methanol
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
29 | 29.34x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 101 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 101% | Natural Gas | Gas Transmission | Methanol | 770 | NR | NR | 770 | 770 | NA | 3 | 770 | NR | NR | .0333 | NR | NR | .0333 | .000989 | NR | NR | .000989 | .00000785 | NR | NR | .00000785 | ppb | NR |  | 9.4 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8678 | NR | NR | 32 | .141 | NR | NR | 1 | 0 | 1 | 101 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 395 | NR | NR | 395
29 | 29.35x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 87 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 87% | Natural Gas | Gas Transmission | Methanol | 970 | NR | NR | 970 | 970 | NA | 3 | 970 | NR | NR | .0363 | NR | NR | .0363 | .0013 | NR | NR | .0013 | .00000993 | NR | NR | .00000993 | ppb | NR |  | 9.9 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 7526 | NR | NR | 32 | .119 | NR | NR | 1 | 0 | 1 | 87 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 520 | NR | NR | 520
29 | 29.36x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 85 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 85% | Natural Gas | Gas Transmission | Methanol | 840 | NR | NR | 840 | 840 | NA | 3 | 840 | NR | NR | .0359 | NR | NR | .0359 | .00125 | NR | NR | .00125 | .0000101 | NR | NR | .0000101 | ppb | NR |  | 11 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8581 | NR | NR | 32 | .122 | NR | NR | 1 | 0 | 1 | 85 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 501 | NR | NR | 501
29 | 29.37x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-16 | 4200 | HP | 98 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 98% | Natural Gas | Gas Transmission | Methanol | 910 | NR | NR | 910 | 910 | NA | 3 | 910 | NR | NR | .0381 | NR | NR | .0381 | .00118 | NR | NR | .00118 | .00000926 | NR | NR | .00000926 | ppb | NR |  | 9.5 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8421 | NR | NR | 32 | .135 | NR | NR | 1 | 0 | 1 | 98 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 471 | NR | NR | 471
29 | 29.38x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-16 | 4200 | HP | 99 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 99% | Natural Gas | Gas Transmission | Methanol | 810 | NR | NR | 810 | 810 | NA | 3 | 810 | NR | NR | .0339 | NR | NR | .0339 | .00103 | NR | NR | .00103 | .00000815 | NR | NR | .00000815 | ppb | NR |  | 9.3 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8409 | NR | NR | 32 | .135 | NR | NR | 1 | 0 | 1 | 99 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 412 | NR | NR | 412
29 | 29.41x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-29 | 2000 | HP | 91 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 91% | Natural Gas | Gas Transmission | Methanol | 1130 | NR | NR | 1130 | 1130 | NA | 3 | 1130 | NR | NR | .0211 | NR | NR | .0211 | .00133 | NR | NR | .00133 | .0000116 | NR | NR | .0000116 | ppb | NR |  | 8.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 3754 | NR | NR | 32 | .144 | NR | NR | 1 | 0 | 1 | 91 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 529 | NR | NR | 529
29 | 29.44x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-27 | 2000 | HP | 89 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 89% | Natural Gas | Gas Transmission | Methanol | 1470 | NR | NR | 1470 | 1470 | NA | 3 | 1470 | NR | NR | .0364 | NR | NR | .0364 | .00225 | NR | NR | .00225 | .0000204 | NR | NR | .0000204 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4975 | NR | NR | 32 | .111 | NR | NR | 1 | 0 | 3 | 89 | 4SLB | Turbo Charged | 12 | 8470 | 1 | 2000 | 903 | NR | NR | 903
29 | 29.45x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-27 | 2000 | HP | 82 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 82% | Natural Gas | Gas Transmission | Methanol | 2300 | NR | NR | 2300 | 2300 | NA | 3 | 2300 | NR | NR | .0539 | NR | NR | .0539 | .00356 | NR | NR | .00356 | .0000329 | NR | NR | .0000329 | ppb | PCC |  | 11.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4706 | NR | NR | 32 | .111 | NR | NR | 1 | 0 | 3 | 82 | 4SLB | Turbo Charged | 12 | 8470 | 1 | 2000 | 1430 | NR | NR | 1430
29 | 29.46x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 92 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 92% | Natural Gas | Gas Transmission | Methanol | 2050 | NR | NR | 2050 | 2050 | NA | 3 | 2050 | NR | NR | .0503 | NR | NR | .0503 | .00316 | NR | NR | .00316 | .0000273 | NR | NR | .0000273 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4927 | NR | NR | 32 | .12 | NR | NR | 1 | 0 | 3 | 92 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1260 | NR | NR | 1260
29 | 29.47x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 85 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 85% | Natural Gas | Gas Transmission | Methanol | 2460 | NR | NR | 2460 | 2460 | NA | 3 | 2460 | NR | NR | .061 | NR | NR | .061 | .00387 | NR | NR | .00387 | .0000359 | NR | NR | .0000359 | ppb | PCC |  | 11.5 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4978 | NR | NR | 32 | .118 | NR | NR | 1 | 0 | 3 | 85 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1540 | NR | NR | 1540
29 | 29.48x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 84 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 84% | Natural Gas | Gas Transmission | Methanol | 2570 | NR | NR | 2570 | 2570 | NA | 3 | 2570 | NR | NR | .0669 | NR | NR | .0669 | .00408 | NR | NR | .00408 | .0000398 | NR | NR | .0000398 | ppb | PCC |  | 11.6 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5229 | NR | NR | 32 | .117 | NR | NR | 1 | 0 | 3 | 84 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1630 | NR | NR | 1630
29 | 29.49x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | Methanol | 2230 | NR | NR | 2230 | 2230 | NA | 3 | 2230 | NR | NR | .0571 | NR | NR | .0571 | .00347 | NR | NR | .00347 | .0000324 | NR | NR | .0000324 | ppb | PCC |  | 11.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5143 | NR | NR | 32 | .118 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1380 | NR | NR | 1380
29 | 29.50x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | Methanol | 2250 | NR | NR | 2250 | 2250 | NA | 3 | 2250 | NR | NR | .0565 | NR | NR | .0565 | .00343 | NR | NR | .00343 | .0000321 | NR | NR | .0000321 | ppb | PCC |  | 11.2 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5040 | NR | NR | 32 | .119 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1370 | NR | NR | 1370
29 | 29.51x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 87 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 87% | Natural Gas | Gas Transmission | Methanol | 2080 | NR | NR | 2080 | 2080 | NA | 3 | 2080 | NR | NR | .0474 | NR | NR | .0474 | .00314 | NR | NR | .00314 | .0000272 | NR | NR | .0000272 | ppb | PCC |  | 11.1 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4582 | NR | NR | 32 | .121 | NR | NR | 1 | 0 | 3 | 87 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1250 | NR | NR | 1250
29 | 29.52x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 80 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 80% | Natural Gas | Gas Transmission | Methanol | 2280 | NR | NR | 2280 | 2280 | NA | 3 | 2280 | NR | NR | .0518 | NR | NR | .0518 | .00351 | NR | NR | .00351 | .0000324 | NR | NR | .0000324 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4567 | NR | NR | 32 | .118 | NR | NR | 1 | 0 | 3 | 80 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 1400 | NR | NR | 1400

## 4SLB-CO
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
144 | 144.6 | Lloyd Corporation Central and VL&W East Sites | CARB 103 | Ventura, CA | Lloyd Corporation Central and VL&W East Sites/Ventura, CA | BTC Environmental Inc. | 1990-02-18 | 1100 | HP | 79.19 | Waukesha | L7042GL | Waukesha/L7042GL/1100 MW / 79.19% | Natural Gas | NR | CO | 570000 | NR | NR | 570000 | 570000 | NA | 3 | 570000 | NR | NR | 4.8 | NR | NR | 4.8 | .692 | NR | NR | .692 | .00551 | NR | NR | .00551 | ppb | NR | C-303 | 10 | NR | NR | 871 | C-303 | 68 | F | 1093 | Btu/dscf | 1933 | NR | NR | 28 |  |  |  | 1 | 0 | 1 | 79.19 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1100 | 309000 | NR | NR | 309000
144 | 144.1 | Lloyd Corporation Central and VL&W East Sites | CARB 100 | Ventura, CA | Lloyd Corporation Central and VL&W East Sites/Ventura, CA | BTC Environmental Inc. | 1990-02-15 | 1100 | HP | 83 | Waukesha | L7042GL | Waukesha/L7042GL/1100 MW / 83% | Natural Gas | NR | CO | 514000 | NR | NR | 514000 | 514000 | NA | 3 | 514000 | NR | NR | 4.17 | NR | NR | 4.17 | .612 | NR | NR | .612 | .00457 | NR | NR | .00457 | ppb | NR | Fuel Type deducted from given fuel factor and heating value | 9.8 | NR | NR | 913 | Fuel Type deducted from given fuel factor and heating value | 68 | F | 1062 | Btu/dscf | 1860.97 | NR | NR | 28 |  |  |  | 1 | 0 | 1 | 83 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1100 | 273000 | NR | NR | 273000
144 | 144.2 | Lloyd Corporation Central and VL&W East Sites | CARB 102 | Ventura, CA | Lloyd Corporation Central and VL&W East Sites/Ventura, CA | BTC Environmental Inc. | 1990-02-15 | 1100 | HP | 78.8 | Waukesha | L7042GL | Waukesha/L7042GL/1100 MW / 78.8% | Natural Gas | NR | CO | 539000 | NR | NR | 539000 | 539000 | NA | 3 | 539000 | NR | NR | 4.95 | NR | NR | 4.95 | .666 | NR | NR | .666 | .00571 | NR | NR | .00571 | ppb | NR | Fuel Type deducted from given fuel factor and heating value | 10.2 | NR | NR | 867 | Fuel Type deducted from given fuel factor and heating value | 68 | F | 1093 | Btu/dscf | 2109 | NR | NR | 28 |  |  |  | 1 | 0 | 1 | 78.8 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1100 | 297000 | NR | NR | 297000
144 | 144.3 | Lloyd Corporation Central and VL&W East Sites | CARB 103 | Ventura, CA | Lloyd Corporation Central and VL&W East Sites/Ventura, CA | BTC Environmental Inc. | 1990-02-15 | 1100 | HP | 73.27 | Waukesha | L7042GL | Waukesha/L7042GL/1100 MW / 73.27% | Natural Gas | NR | CO | 528000 | NR | NR | 528000 | 528000 | NA | 3 | 528000 | NR | NR | 4.58 | NR | NR | 4.58 | .678 | NR | NR | .678 | .00568 | NR | NR | .00568 | ppb | NR | Fuel Type deducted from given fuel factor and heating value | 10.6 | NR | NR | 806 | Fuel Type deducted from given fuel factor and heating value | 68 | F | 1093 | Btu/dscf | 1992 | NR | NR | 28 |  |  |  | 1 | 0 | 1 | 73.27 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1100 | 302000 | NR | NR | 302000
144 | 144.4 | Lloyd Corporation Central and VL&W East Sites | CARB 103 | Ventura, CA | Lloyd Corporation Central and VL&W East Sites/Ventura, CA | BTC Environmental Inc. | 1990-02-16 | 1100 | HP | 77.9 | Waukesha | L7042GL | Waukesha/L7042GL/1100 MW / 77.9% | Natural Gas | NR | CO | 556000 | NR | NR | 556000 | 556000 | NA | 3 | 556000 | NR | NR | 4.71 | NR | NR | 4.71 | .675 | NR | NR | .675 | .0055 | NR | NR | .0055 | ppb | NR | C-104 | 10 | NR | NR | 857 | C-104 | 68 | F | 1093 | Btu/dscf | 1945 | NR | NR | 28 |  |  |  | 1 | 0 | 1 | 77.9 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1100 | 301000 | NR | NR | 301000
144 | 144.5 | Lloyd Corporation Central and VL&W East Sites | CARB 103 | Ventura, CA | Lloyd Corporation Central and VL&W East Sites/Ventura, CA | BTC Environmental Inc. | 1990-02-17 | 1100 | HP | 84 | Waukesha | L7042GL | Waukesha/L7042GL/1100 MW / 84% | Natural Gas | NR | CO | 630000 | NR | NR | 630000 | 630000 | NA | 3 | 630000 | NR | NR | 5.3 | NR | NR | 5.3 | .764 | NR | NR | .764 | .00574 | NR | NR | .00574 | ppb | NR | C-304 | 10 | NR | NR | 924 | C-304 | 68 | F | 1093 | Btu/dscf | 1933 | NR | NR | 28 |  |  |  | 1 | 0 | 1 | 84 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1100 | 341000 | NR | NR | 341000
152 | 152 | National Fuel Gas Supply Ellisburg Station | EPA 10 | PA | National Fuel Gas Supply Ellisburg Station/PA | Engineering Science Inc. | 1990-11-15 | 2870 | HP | 100 | Dresser-Rand | 412 KVSE | Dresser-Rand/412 KVSE/2870 MW / 100% | Natural Gas | NR | CO | 437000 | 452000 | 444000 | 444333.333333333 | 444000 | NA | 3 | 437000 | 452000 | 444000 | 16 | 16.9 | 17 | 16.6 | .691 | .709 | .697 | .699 | .00557 | .00589 | .00592 | .00579 | ppb | PCC | Compression Engine | 12.54 | 12.47 | 12.48 | 2875.33 | Compression Engine. PCC assumed because emissions are one order of magnitude compared to gathered data | 68 | F | 1030 | Btu/dscf | 8397 | 8572 | 8775 | 28 |  |  |  | 3 | 0 | 3 | 100 | 4SLB | NR | NR | 8710 | 0 | 2870 | 308000 | 316000 | 311000 | 311666.666666667
29 | 29.33x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-14 | 4200 | HP | 98 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 98% | Natural Gas | Gas Transmission | CO | 203000 | NR | NR | 203000 | 203000 | NA | 3 | 203000 | NR | NR | 7.72 | NR | NR | 7.72 | .232 | NR | NR | .232 | .00188 | NR | NR | .00188 | ppb | NR |  | 9.6 | NR | NR |  |  | 68 | F | 1159 | Btu/scf | 8735 | NR | NR | 28 | .13 | NR | NR | 1 | 0 | 1 | 98 | 4SLB | Turbo Charged | 16 | 8498 | 1 | 4200 | 106000 | NR | NR | 106000
29 | 29.34x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 101 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 101% | Natural Gas | Gas Transmission | CO | 217000 | NR | NR | 217000 | 217000 | NA | 3 | 217000 | NR | NR | 8.2 | NR | NR | 8.2 | .244 | NR | NR | .244 | .00193 | NR | NR | .00193 | ppb | NR |  | 9.4 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8678 | NR | NR | 28 | .141 | NR | NR | 1 | 0 | 1 | 101 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 111000 | NR | NR | 111000
139 | 139 | Conoco Inc. Gibbstown Terminal | EPA method 10 | Lafayette, LA | Conoco Inc. Gibbstown Terminal/Lafayette, LA | Emission Testing Services Inc. | 1991-11-25 | 1100 | HP | 92.73 | White Superior | 8GTLE825 | White Superior/8GTLE825/1100 MW / 92.73% | Natural Gas | NR | CO | 296140 | 298730 | 297110 | 297326.666666667 | 297000 | NA | 3 | 296140 | 298730 | 297110 | 3.51 | 3.48 | 3.48 | 3.49 | .382 | .383 | .379 | .381 | .00344 | .00341 | .00341 | .00342 | ppb | Catalytic Converter for NOx control |  | 10.66 | 10.59 | 10.52 | 1020 |  | 68 | F | 1088 | Btu/dscf | 2724.3 | 2675.9 | 2685.8 | 28 |  |  |  | 3 | 0 | 5 | 92.73 | 4SLB | NR | NR | 8710 | 0 | 1100 | 171000 | 171000 | 169000 | 170333.333333333
29 | 29.36x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 85 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 85% | Natural Gas | Gas Transmission | CO | 209000 | NR | NR | 209000 | 209000 | NA | 3 | 209000 | NR | NR | 7.81 | NR | NR | 7.81 | .273 | NR | NR | .273 | .00219 | NR | NR | .00219 | ppb | NR |  | 11 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8581 | NR | NR | 28 | .122 | NR | NR | 1 | 0 | 1 | 85 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 125000 | NR | NR | 125000
126 | 126.5 | Texaco USA - Lost Hills Gas Plant | CARB method 1-100 | P.O. Bin H, Taft, CA, 93268 | Texaco USA - Lost Hills Gas Plant/P.O. Bin H, Taft, CA, 93268 | Pape & Steiner Environmental Services | 1990-07-09 | 1000 | NR | 87 | Cooper-Superior | 8GTLA | Cooper-Superior/8GTLA/1000 MW / 87% | Natural Gas | NR | CO | 469780 | 462860 | NR | 466320 | 466000 | NA | 3 | 469780 | 462860 | NR | 3.97 | 3.98 | NR | 3.98 | .599 | .59 | NR | .594 | .00456 | .00457 | NR | .00456 | ppb | PCC | Engine # 3 | 10.52 | 10.53 | NR | 920 | Engine # 3. PCC assumed because NOX emissions <100ppm | 68 | F | 1072 | Btu/dscf | 1938.3 | 1972.01 | NR | 28 |  |  |  | 2 | 0 | 3 | 87 | 4SLB | NR | 8 | 8710 | 0 | 1000 | 267000 | 263000 | NR | 265000
29 | 29.37x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-16 | 4200 | HP | 98 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 98% | Natural Gas | Gas Transmission | CO | 258000 | NR | NR | 258000 | 258000 | NA | 3 | 258000 | NR | NR | 9.46 | NR | NR | 9.46 | .292 | NR | NR | .292 | .0023 | NR | NR | .0023 | ppb | NR |  | 9.5 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8421 | NR | NR | 28 | .135 | NR | NR | 1 | 0 | 1 | 98 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 134000 | NR | NR | 134000
29 | 29.35x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-15 | 4200 | HP | 87 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 87% | Natural Gas | Gas Transmission | CO | 247000 | NR | NR | 247000 | 247000 | NA | 3 | 247000 | NR | NR | 8.1 | NR | NR | 8.1 | .29 | NR | NR | .29 | .00222 | NR | NR | .00222 | ppb | NR |  | 9.9 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 7526 | NR | NR | 28 | .119 | NR | NR | 1 | 0 | 1 | 87 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 132000 | NR | NR | 132000
134 | 134 | Florida Gas Transmission Company - Station No. 77 | EPA 10 | Calcasieu Parish, LA | Florida Gas Transmission Company - Station No. 77/Calcasieu Parish, LA | Cubix Corporation | 1992-04-01 | 825 | HP | 100 | Superior | 6GTLA | Superior/6GTLA/825 MW / 100% | Natural Gas | NR | CO | 800000 | 785000 | 807000 | 797333.333333333 | 797000 | NA | 3 | 800000 | 785000 | 807000 | 5.89 | 5.7 | 6 | 5.86 | .928 | .927 | .953 | .936 | .00714 | .00691 | .00727 | .00711 | ppb | PCC | Additional Info. needed | 9.5 | 9.7 | 9.7 | 825 | Additional Info. Needed. PCC assumed because emissions are one order of magnitude from other data, 3/99 | 68 | F | 995 | Btu/dscf | 1690.08 | 1668.03 | 1708.1 | 28 |  |  |  | 3 | 0 | 3 | 100 | 4SLB | Turbo Charged | NR | 8710 | 0 | 825 | 414000 | 414000 | 425000 | 417666.666666667
131 | 131.4 | Tehachapi-Cummings Water District | CARB 1-100 | Tehachapi, CA | Tehachapi-Cummings Water District/Tehachapi, CA | Steiner Environmental Inc. | 1993-09-14 | 1060 | HP | NR | Waukesha | L57990GL | Waukesha/L57990GL/1060 MW / NR% | Natural Gas | NR | CO | 569333 | 571500 | 570166 | 570333 | 570000 | NA | 3 | 569333 | 571500 | 570166 | 4.77 | 4.8 | 4.76 | 4.78 | .701 | .704 | .698 | .701 | .0045 | .00453 | .00449 | .00451 | ppb | NR | Engine # 1 | 10.4 | 10.41 | 10.35 | 1000 | Engine # 1 | 68 | F | 1050.24 | Btu/dscf | 1924.89 | 1926.73 | 1915.77 | 28 |  |  |  | 3 | 0 | 1 | 0 | 4SLB | NR | NR | 8509.74 | 0 | 1060 | 320000 | 321000 | 319000 | 320000
131 | 131.2 | Tehachapi-Cummings Water District | CARB 1-100 | Tehachapi, CA | Tehachapi-Cummings Water District/Tehachapi, CA | Steiner Environmental Inc. | 1993-09-14 | 973 | HP | NR | Waukesha | L5790GL | Waukesha/L5790GL/973 MW / NR% | Natural Gas | NR | CO | 594500 | 589167 | 589833 | 591166.666666667 | 591000 | NA | 3 | 594500 | 589167 | 589833 | 5.03 | 4.99 | 5.03 | 5.02 | .728 | .721 | .722 | .724 | .00517 | .00513 | .00517 | .00516 | ppb | NR | Engine # 3 | 10.34 | 10.34 | 10.34 | 900 | Engine # 3 | 68 | F | 1051.47 | Btu/dscf | 1943.72 | 1943.72 | 1958.56 | 28 |  |  |  | 3 | 0 | 1 | 0 | 4SLB | NR | NR | 8510.97 | 0 | 973 | 332000 | 329000 | 330000 | 330333.333333333
29 | 29.38x | GRI Site 3A | FTIR | NR | GRI Site 3A/NR | Radian Corporation | 1994-06-16 | 4200 | HP | 99 | Cooper Bessemer | LSV-16 | Cooper Bessemer/LSV-16/4200 MW / 99% | Natural Gas | Gas Transmission | CO | 258000 | NR | NR | 258000 | 258000 | NA | 3 | 258000 | NR | NR | 9.45 | NR | NR | 9.45 | .287 | NR | NR | .287 | .00227 | NR | NR | .00227 | ppb | NR |  | 9.3 | NR | NR |  |  | 68 | F | 1148 | Btu/scf | 8409 | NR | NR | 28 | .135 | NR | NR | 1 | 0 | 1 | 99 | 4SLB | Turbo Charged | 16 | 8509 | 1 | 4200 | 131000 | NR | NR | 131000
126 | 126.6 | Texaco USA - Lost Hills Gas Plant | CARB method 1-100 | P.O. Bin H, Taft, CA, 93268 | Texaco USA - Lost Hills Gas Plant/P.O. Bin H, Taft, CA, 93268 | Pape & Steiner Environmental Services | 1990-07-09 | 760 | NR | 102 | Cooper-Superior | 6GTLA | Cooper-Superior/6GTLA/760 MW / 102% | Natural Gas | NR | CO | 671720 | 689170 | NR | 680445 | 680000 | NA | 3 | 671720 | 689170 | NR | 5.68 | 5.84 | NR | 5.76 | .831 | .853 | NR | .842 | .00733 | .00753 | NR | .00743 | ppb | PCC | Engine # 6 | 10.21 | 10.22 | NR | 790.5 | Engine # 6. PCC assumed because NOX emissions <100ppm | 68 | F | 1072 | Btu/dscf | 1942.64 | 1944.46 | NR | 28 |  |  |  | 2 | 0 | 3 | 102 | 4SLB | NR | 6 | 8710 | 0 | 760 | 371000 | 381000 | NR | 376000
29 | 29.44x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-27 | 2000 | HP | 89 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 89% | Natural Gas | Gas Transmission | CO | 352000 | NR | NR | 352000 | 352000 | NA | 3 | 352000 | NR | NR | 7.63 | NR | NR | 7.63 | .472 | NR | NR | .472 | .00429 | NR | NR | .00429 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4975 | NR | NR | 28 | .111 | NR | NR | 1 | 0 | 3 | 89 | 4SLB | Turbo Charged | 12 | 8470 | 1 | 2000 | 216000 | NR | NR | 216000
126 | 126.4 | Texaco USA - Lost Hills Gas Plant | CARB method 1-100 | P.O. Bin H, Taft, CA, 93268 | Texaco USA - Lost Hills Gas Plant/P.O. Bin H, Taft, CA, 93268 | Pape & Steiner Environmental Services | 1990-07-09 | 1000 | NR | 91.5 | Cooper-Superior | 8GTLA | Cooper-Superior/8GTLA/1000 MW / 91.5% | Natural Gas | NR | CO | 593700 | 600640 | NR | 597170 | 597000 | NA | 3 | 593700 | 600640 | NR | 5.39 | 5.12 | NR | 5.26 | .805 | .77 | NR | .788 | .00589 | .0056 | NR | .00574 | ppb | PCC | Engine # 2 | 11.14 | 10.58 | NR | 883.5 | Engine # 2. PCC assumed because NOX emissions <100ppm | 68 | F | 1080 | Btu/dscf | 2086 | 1956.09 | NR | 28 |  |  |  | 2 | 0 | 3 | 91.5 | 4SLB | NR | 8 | 8710 | 0 | 1000 | 359000 | 343000 | NR | 351000
126 | 126.3 | Texaco USA - Lost Hills Gas Plant | CARB method 1-100 | P.O. Bin H, Taft, CA, 93268 | Texaco USA - Lost Hills Gas Plant/P.O. Bin H, Taft, CA, 93268 | Pape & Steiner Environmental Services | 1990-07-09 | 760 | NR | 91.5 | Cooper-Superior | 6GTLA | Cooper-Superior/6GTLA/760 MW / 91.5% | Natural Gas | NR | CO | 498550 | 503580 | NR | 501065 | 501000 | NA | 3 | 498550 | 503580 | NR | 3.37 | 3.47 | NR | 3.42 | .628 | .642 | NR | .635 | .00485 | .00499 | NR | .00492 | ppb | PCC | Engine # 5 | 10.4 | 10.52 | NR | 670.5 | Engine # 5. PCC assumed because NOX emissions <100ppm | 68 | F | 1080 | Btu/dscf | 1550.74 | 1581.5 | NR | 28 |  |  |  | 2 | 0 | 3 | 91.5 | 4SLB | NR | 6 | 8710 | 0 | 760 | 280000 | 286000 | NR | 283000
126 | 126.2 | Texaco USA - Lost Hills Gas Plant | CARB method 1-100 | P.O. Bin H, Taft, CA, 93268 | Texaco USA - Lost Hills Gas Plant/P.O. Bin H, Taft, CA, 93268 | Pape & Steiner Environmental Services | 1990-07-09 | 1000 | NR | 88.5 | Cooper-Superior | 8GTLA | Cooper-Superior/8GTLA/1000 MW / 88.5% | Natural Gas | NR | CO | 588940 | 620870 | NR | 604905 | 605000 | NA | 3 | 588940 | 620870 | NR | 5.29 | 4.98 | NR | 5.14 | .738 | .754 | NR | .746 | .00598 | .00563 | NR | .0058 | ppb | PCC | Engine # 1 | 10.35 | 10.01 | NR | 885.50 | Engine # 1. PCC assumed because NOX emissions <100ppm | 68 | F | 1069 | Btu/dscf | 2061.29 | 1842.12 | NR | 28 |  |  |  | 2 | 0 | 3 | 88.5 | 4SLB | NR | 8 | 8710 | 0 | 1000 | 329000 | 336000 | NR | 332500
126 | 126.1 | Texaco USA - Lost Hills Gas Plant | CARB method 1-100 | P.O. Bin H, Taft, CA, 93268 | Texaco USA - Lost Hills Gas Plant/P.O. Bin H, Taft, CA, 93268 | Pape & Steiner Environmental Services | 1990-07-09 | 760 | NR | 100 | Cooper-Superior | 6GTLA | Cooper-Superior/6GTLA/760 MW / 100% | Natural Gas | NR | CO | 464580 | 450260 | NR | 457420 | 457000 | NA | 3 | 464580 | 450260 | NR | 4.13 | 4.04 | NR | 4.08 | .641 | .622 | NR | .632 | .00543 | .00532 | NR | .00538 | ppb | PCC | Engine # 4 | 11.31 | 11.33 | NR | 766 | Engine # 4. PCC assumed because NOX emissions <100ppm | 68 | F | 1066 | Btu/dscf | 2038.99 | 2058.35 | NR | 28 |  |  |  | 2 | 0 | 3 | 100 | 4SLB | NR | 6 | 8710 | 0 | 760 | 286000 | 278000 | NR | 282000
118 | 118 | Philips Petroleum Company, Lake Washington Central Battery | EPA 10 | P.O. Box 51107 Lafayette, LA 70505 | Philips Petroleum Company, Lake Washington Central Battery/P.O. Box 51107 Lafayette, LA 70505 | Environmental Science & Engineering Inc. | 1992-10-29 | 850 | HP | 100 | Caterpillar | G399T | Caterpillar/G399T/850 MW / 100% | Natural Gas | NR | CO | 566260 | 534680 | 553390 | 551443.333333333 | 551000 | NA | 3 | 566260 | 534680 | 553390 | 3.13 | 2.88 | 2.94 | 2.98 | .457 | .412 | .43 | .433 | .00368 | .00339 | .00346 | .00351 | ppb | NR | No. 4 Compressor | 4.51 | 3.72 | 3.89 | NR | No. 4 Compressor | 68 | F | 1175.9 | Btu/dscf | 1267.7 | 1236.7 | 1218.5 | 28 |  |  |  | 3 | 0 | 1 | 100 | 4SLB | Turbo Charged | 16 | 8710 | 0 | 850 | 204000 | 184000 | 192000 | 193333.333333333
116 | 116.2 | Chevron USA Inc. - Warren Gas Plant | CARB 100 | P.O. Box 1392, Bakersfield, CA | Chevron USA Inc. - Warren Gas Plant/P.O. Box 1392, Bakersfield, CA | Genesis Environmental Services | 1991-10-01 | 1000 | HP | NR | Waukesha | 7042G1 | Waukesha/7042G1/1000 MW / NR% | Natural Gas | NR | CO | 480000 | 480000 | NR | 480000 | 480000 | NA | 3 | 480000 | 480000 | NR | 2.61 | 2.6 | NR | 2.6 | .572 | .577 | NR | .574 | .00261 | .0026 | NR | .0026 | ppb | NR |  | 9.8 | 9.9 | NR | NR | Internal Combustion Engine # 2. Only Two runs. No Fuel Flow data provided | 68 | F | 836.44 | Btu/dscf | 1246 | 1244.3 | NR | 28 |  |  |  | 2 | 0 | 1 | 0 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1000 | 255000 | 257000 | NR | 256000
116 | 116.1 | Chevron USA Inc. - Warren Gas Plant | CARB 100 | P.O. Box 1392, Bakersfield, CA | Chevron USA Inc. - Warren Gas Plant/P.O. Box 1392, Bakersfield, CA | Genesis Environmental Services | 1991-10-01 | 1000 | HP | NR | Waukesha | 7042G1 | Waukesha/7042G1/1000 MW / NR% | Natural Gas | NR | CO | 480000 | 480000 | NR | 480000 | 480000 | NA | 3 | 480000 | 480000 | NR | 2.42 | 2.39 | NR | 2.41 | .572 | .567 | NR | .569 | .00242 | .00239 | NR | .0024 | ppb | NR | Internal Combustion Engine # 2. Only Two runs. No Fuel Flow data provided | 9.8 | 9.7 | NR | NR | Internal Combustion Engine # 1. Only Two runs. No Fuel Flow data provided | 68 | F | 836.44 | Btu/dscf | 1155.5 | 1143.9 | NR | 28 |  |  |  | 2 | 0 | 1 | 0 | 4SLB | Turbo Charged | NR | 8710 | 0 | 1000 | 255000 | 253000 | NR | 254000
115 | 115 | National Fuel Gas Supply Corporation | EPA 10 | Alleghery Township, PA | National Fuel Gas Supply Corporation/Alleghery Township, PA | Engineering Science Inc. | 1990-01-31 | 2850 | HP | 100 | Dresser-Rand | 412KVSE-1 | Dresser-Rand/412KVSE-1/2850 MW / 100% | Natural Gas | NR | CO | 438000 | 411000 | 480000 | 443000 | 443000 | NA | 3 | 438000 | 411000 | 480000 | 18.3 | 17.4 | 20.7 | 18.8 | .794 | .745 | .87 | .803 | .00642 | .00611 | .00726 | .0066 | ppb | PCC |  | 13.6 | 13.6 | 13.6 | NR | PCC assumed because emissions are an order of magnitude less than the other data | 68 | F | NR | NR | 9590 | 9721 | 9877 | 28 |  |  |  | 3 | 0 | 3 | 100 | 4SLB | NR | 12 | 8710 | 0 | 2850 | 354000 | 332000 | 388000 | 358000
131 | 131.1 | Tehachapi-Cummings Water District | CARB 1-100 | Tehachapi, CA | Tehachapi-Cummings Water District/Tehachapi, CA | Steiner Environmental Inc. | 1993-09-14 | 973 | HP | NR | Waukesha | L57990GL | Waukesha/L57990GL/973 MW / NR% | Natural Gas | NR | CO | 630170 | 628330 | 628333 | 628944.333333333 | 629000 | NA | 3 | 630170 | 628330 | 628333 | 5.13 | 5.14 | 5.16 | 5.14 | .753 | .755 | .758 | .755 | .00527 | .00528 | .0053 | .00528 | ppb | NR | Engine # 2 | 10.08 | 10.14 | 10.18 | 1000 | Engine # 2 | 68 | F | 1050.24 | Btu/dscf | 1869.06 | 1879.49 | 1886.5 | 28 |  |  |  | 3 | 0 | 1 | 0 | 4SLB | NR | NR | 8514.74 | 0 | 973 | 344000 | 345000 | 346000 | 345000
CSU-2 | CSU-2.10.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 625610 | NR | NR | 625610 | 626000 | NA | 3 | 625610 | NR | NR | 4.35 | NR | NR | 4.35 | .74 | NR | NR | .74 | .00591 | NR | NR | .00591 | ppb | NR |  | 9.80 | NR | NR | 735 |  | 68 | F | 1095 | Btu/dscf | 1598 |  |  | 28 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 0 | 736 | 333000 | NR | NR | 333000
CSU-2 | CSU-2.9.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-04 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 619700 | NR | NR | 619700 | 620000 | NA | 3 | 619700 | NR | NR | 4.47 | NR | NR | 4.47 | .726 | NR | NR | .726 | .00607 | NR | NR | .00607 | ppb | NR |  | 9.69 | NR | NR | 736 |  | 68 | F | 1135 | Btu/dscf | 1657 |  |  | 28 | 0.123 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8654 | 0 | 736 | 326000 | NR | NR | 326000
CSU-2 | CSU-2.8.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 641350 | NR | NR | 641350 | 641000 | NA | 3 | 641350 | NR | NR | 3.95 | NR | NR | 3.95 | .81 | NR | NR | .81 | .00537 | NR | NR | .00537 | ppb | NR |  | 10.50 | NR | NR | 616 |  | 68 | F | 1095 | Btu/dscf | 1413 |  |  | 28 | 0.116 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 0 | 736 | 364000 | NR | NR | 364000
CSU-2 | CSU-2.7.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 70 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 70% | Natural Gas | NR | CO | 639840 | NR | NR | 639840 | 640000 | NA | 3 | 639840 | NR | NR | 3.2 | NR | NR | 3.2 | .718 | NR | NR | .718 | .00621 | NR | NR | .00621 | ppb | NR |  | 9.20 | NR | NR | 515 |  | 68 | F | 1095 | Btu/dscf | 1147 |  |  | 28 | 0.124 |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 6 | 8645 | 0 | 736 | 323000 | NR | NR | 323000
CSU-2 | CSU-2.6.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 669760 | NR | NR | 669760 | 670000 | NA | 3 | 669760 | NR | NR | 4.62 | NR | NR | 4.62 | .746 | NR | NR | .746 | .00628 | NR | NR | .00628 | ppb | NR |  | 9.10 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1583 |  |  | 28 | 0.127 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 0 | 736 | 335000 | NR | NR | 335000
CSU-2 | CSU-2.5.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 740590 | NR | NR | 740590 | 741000 | NA | 3 | 740590 | NR | NR | 6 | NR | NR | 6 | .937 | NR | NR | .937 | .00815 | NR | NR | .00815 | ppb | NR |  | 10.51 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1860 |  |  | 28 | 0.12 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 0 | 736 | 421000 | NR | NR | 421000
CSU-2 | CSU-2.4.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 590780 | NR | NR | 590780 | 591000 | NA | 3 | 590780 | NR | NR | 3.36 | NR | NR | 3.36 | .699 | NR | NR | .699 | .00457 | NR | NR | .00457 | ppb | NR |  | 9.80 | NR | NR | 617 |  | 68 | F | 1095 | Btu/dscf | 1307 |  |  | 28 | 0.12 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 0 | 736 | 314000 | NR | NR | 314000
CSU-2 | CSU-2.3.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 70 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 70% | Natural Gas | NR | CO | 573320 | NR | NR | 573320 | 573000 | NA | 3 | 573320 | NR | NR | 2.52 | NR | NR | 2.52 | .679 | NR | NR | .679 | .00489 | NR | NR | .00489 | ppb | NR |  | 9.81 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1011 |  |  | 28 | 0.123 |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 6 | 8655 | 0 | 736 | 305000 | NR | NR | 305000
CSU-2 | CSU-2.2.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 70 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 70% | Natural Gas | NR | CO | 590960 | NR | NR | 590960 | 591000 | NA | 3 | 590960 | NR | NR | 3.15 | NR | NR | 3.15 | .7 | NR | NR | .7 | .00611 | NR | NR | .00611 | ppb | NR |  | 9.82 | NR | NR | 515 |  | 68 | F | 1095 | Btu/dscf | 1224 |  |  | 28 | 0.117 |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 6 | 8645 | 0 | 736 | 315000 | NR | NR | 315000
CSU-2 | CSU-2.16.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 627010 | NR | NR | 627010 | 627000 | NA | 3 | 627010 | NR | NR | 4.63 | NR | NR | 4.63 | .744 | NR | NR | .744 | .00629 | NR | NR | .00629 | ppb | NR |  | 9.82 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1697 |  |  | 28 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 0 | 736 | 334000 | NR | NR | 334000
CSU-2 | CSU-2.15.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 625170 | NR | NR | 625170 | 625000 | NA | 3 | 625170 | NR | NR | 4.72 | NR | NR | 4.72 | .747 | NR | NR | .747 | .00641 | NR | NR | .00641 | ppb | NR |  | 9.90 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1734 |  |  | 28 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 0 | 736 | 335000 | NR | NR | 335000
CSU-2 | CSU-2.14.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-04 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 655620 | NR | NR | 655620 | 656000 | NA | 3 | 655620 | NR | NR | 4.68 | NR | NR | 4.68 | .777 | NR | NR | .777 | .00636 | NR | NR | .00636 | ppb | NR |  | 9.81 | NR | NR | 736 |  | 68 | F | 1135 | Btu/dscf | 1639 |  |  | 28 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8654 | 0 | 736 | 349000 | NR | NR | 349000
CSU-2 | CSU-2.13.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-05 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 619920 | NR | NR | 619920 | 620000 | NA | 3 | 619920 | NR | NR | 5.13 | NR | NR | 5.13 | .779 | NR | NR | .779 | .00697 | NR | NR | .00697 | ppb | NR |  | 10.44 | NR | NR | 736 |  | 68 | F | 1152 | Btu/dscf | 1901 |  |  | 28 | 0.121 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8655 | 0 | 736 | 350000 | NR | NR | 350000
29 | 29.42x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-29 | 2000 | HP | 90 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 90% | Natural Gas | Gas Transmission | CO | 103000 | NR | NR | 103000 | 103000 | NA | 3 | 103000 | NR | NR | 1.75 | NR | NR | 1.75 | .111 | NR | NR | .111 | .000972 | NR | NR | .000972 | ppb | SCR |  | 8.6 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 3890 | NR | NR | 28 | .144 | NR | NR | 1 | 0 | 5 | 90 | 4SLB | Turbo Charged | 12 | 8710 | 1 | 2000 | 49400 | NR | NR | 49400
CSU-2 | CSU-2.11.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 620510 | NR | NR | 620510 | 621000 | NA | 3 | 620510 | NR | NR | 4.33 | NR | NR | 4.33 | .734 | NR | NR | .734 | .00588 | NR | NR | .00588 | ppb | NR |  | 9.81 | NR | NR | 735 |  | 68 | F | 1095 | Btu/dscf | 1603 |  |  | 28 | 0.122 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 0 | 736 | 330000 | NR | NR | 330000
29 | 29.47x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 85 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 85% | Natural Gas | Gas Transmission | CO | 419000 | NR | NR | 419000 | 419000 | NA | 3 | 419000 | NR | NR | 9.09 | NR | NR | 9.09 | .577 | NR | NR | .577 | .00535 | NR | NR | .00535 | ppb | PCC |  | 11.5 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4978 | NR | NR | 28 | .118 | NR | NR | 1 | 0 | 3 | 85 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 263000 | NR | NR | 263000
29 | 29.40x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-29 | 2000 | HP | 91 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 91% | Natural Gas | Gas Transmission | CO | 141000 | NR | NR | 141000 | 141000 | NA | 3 | 141000 | NR | NR | 2.4 | NR | NR | 2.4 | .148 | NR | NR | .148 | .00132 | NR | NR | .00132 | ppb | NR |  | 8.56 | NR | NR |  | Before SCR | 68 | F | 1011 | Btu/scf | 3914 | NR | NR | 28 | .144 | NR | NR | 1 | 0 | 1 | 91 | 4SLB | Turbo Charged | 12 | 8522 | 1 | 2000 | 67400 | NR | NR | 67400
29 | 29.41x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-29 | 2000 | HP | 91 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 91% | Natural Gas | Gas Transmission | CO | 126000 | NR | NR | 126000 | 126000 | NA | 3 | 126000 | NR | NR | 2.06 | NR | NR | 2.06 | .129 | NR | NR | .129 | .00113 | NR | NR | .00113 | ppb | NR |  | 8.3 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 3754 | NR | NR | 28 | .144 | NR | NR | 1 | 0 | 1 | 91 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 59000 | NR | NR | 59000
110 | 110.4 | Peoples Natural Gas Company - The Laurel Ridge and Rager Mountain Stations | NR | Cambria County, PA | Peoples Natural Gas Company - The Laurel Ridge and Rager Mountain Stations/Cambria County, PA | Scott Environmental Services | 1991-08-14 | 1100 | HP | NR | Cooper-Superior | SGTLB | Cooper-Superior/SGTLB/1100 MW / NR% | Natural Gas | NR | CO | 549000 | 561000 | 569000 | 559666.666666667 | 560000 | NA | 3 | 549000 | 561000 | 569000 | 4.64 | 4.79 | 4.83 | 4.75 | .606 | .652 | .651 | .636 | .00422 | .00435 | .00439 | .00432 | ppb | NR | Engine # 1 | 8.91 | 9.52 | 9.34 | NR | Engine # 1. Fuel Type information updated thanks to call to PA Air Pollution Dept. | 68 | F | NR | NR | 1941 | 1960 | 1949 | 28 |  |  |  | 3 | 0 | 1 | 0 | 4SLB | NR | NR | 8710 | 0 | 1100 | 270000 | 291000 | 290000 | 283666.666666667
29 | 29.43x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-29 | 2000 | HP | 90 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 90% | Natural Gas | Gas Transmission | CO | 102000 | NR | NR | 102000 | 102000 | NA | 3 | 102000 | NR | NR | 1.73 | NR | NR | 1.73 | .11 | NR | NR | .11 | .000961 | NR | NR | .000961 | ppb | SCR |  | 8.6 | NR | NR |  |  | 68 | F | 1011 | Btu/scf | 3890 | NR | NR | 28 | .144 | NR | NR | 1 | 0 | 5 | 90 | 4SLB | Turbo Charged | 12 | 8710 | 1 | 2000 | 48900 | NR | NR | 48900
CSU-2 | CSU-2.12.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-06 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 612710 | NR | NR | 612710 | 613000 | NA | 3 | 612710 | NR | NR | 4.36 | NR | NR | 4.36 | .731 | NR | NR | .731 | .00592 | NR | NR | .00592 | ppb | NR |  | 9.90 | NR | NR | 735 |  | 68 | F | 1095 | Btu/dscf | 1634 |  |  | 28 | 0.122 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8645 | 0 | 736 | 329000 | NR | NR | 329000
29 | 29.46x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 92 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 92% | Natural Gas | Gas Transmission | CO | 378000 | NR | NR | 378000 | 378000 | NA | 3 | 378000 | NR | NR | 8.11 | NR | NR | 8.11 | .509 | NR | NR | .509 | .00441 | NR | NR | .00441 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4927 | NR | NR | 28 | .12 | NR | NR | 1 | 0 | 3 | 92 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 232000 | NR | NR | 232000
29 | 29.39x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-28 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | CO | 138000 | NR | NR | 138000 | 138000 | NA | 3 | 138000 | NR | NR | 2.2 | NR | NR | 2.2 | .142 | NR | NR | .142 | .00125 | NR | NR | .00125 | ppb | NR |  | 8.3 | NR | NR |  |  | 68 | F | 1010 | Btu/scf | 3656 | NR | NR | 28 | .144 | NR | NR | 1 | 0 | 1 | 88 | 4SLB | Turbo Charged | 12 | 8522 | 1 | 2000 | 64600 | NR | NR | 64600
29 | 29.48x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 84 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 84% | Natural Gas | Gas Transmission | CO | 364000 | NR | NR | 364000 | 364000 | NA | 3 | 364000 | NR | NR | 8.29 | NR | NR | 8.29 | .506 | NR | NR | .506 | .00493 | NR | NR | .00493 | ppb | PCC |  | 11.6 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5229 | NR | NR | 28 | .117 | NR | NR | 1 | 0 | 3 | 84 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 231000 | NR | NR | 231000
29 | 29.49x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | CO | 331000 | NR | NR | 331000 | 331000 | NA | 3 | 331000 | NR | NR | 7.42 | NR | NR | 7.42 | .451 | NR | NR | .451 | .00422 | NR | NR | .00422 | ppb | PCC |  | 11.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5143 | NR | NR | 28 | .118 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 206000 | NR | NR | 206000
29 | 29.50x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 88 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 88% | Natural Gas | Gas Transmission | CO | 394000 | NR | NR | 394000 | 394000 | NA | 3 | 394000 | NR | NR | 8.65 | NR | NR | 8.65 | .525 | NR | NR | .525 | .00491 | NR | NR | .00491 | ppb | PCC |  | 11.2 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 5040 | NR | NR | 28 | .119 | NR | NR | 1 | 0 | 3 | 88 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 240000 | NR | NR | 240000
29 | 29.51x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 87 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 87% | Natural Gas | Gas Transmission | CO | 399000 | NR | NR | 399000 | 399000 | NA | 3 | 399000 | NR | NR | 7.96 | NR | NR | 7.96 | .527 | NR | NR | .527 | .00457 | NR | NR | .00457 | ppb | PCC |  | 11.1 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4582 | NR | NR | 28 | .121 | NR | NR | 1 | 0 | 3 | 87 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 240000 | NR | NR | 240000
29 | 29.52x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-30 | 2000 | HP | 80 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 80% | Natural Gas | Gas Transmission | CO | 451000 | NR | NR | 451000 | 451000 | NA | 3 | 451000 | NR | NR | 8.97 | NR | NR | 8.97 | .608 | NR | NR | .608 | .00561 | NR | NR | .00561 | ppb | PCC |  | 11.3 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4567 | NR | NR | 28 | .118 | NR | NR | 1 | 0 | 3 | 80 | 4SLB | Turbo Charged | 12 | 8518 | 1 | 2000 | 277000 | NR | NR | 277000
CSU-2 | CSU-2.1.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-04 | 736 | HP | 100 | Waukesha | 3521 GL | Waukesha/3521 GL/736 MW / 100% | Natural Gas | NR | CO | 620260 | NR | NR | 620260 | 620000 | NA | 3 | 620260 | NR | NR | 4.51 | NR | NR | 4.51 | .734 | NR | NR | .734 | .00613 | NR | NR | .00613 | ppb | NR |  | 9.80 | NR | NR | 736 |  | 68 | F | 1135 | Btu/dscf | 1670 |  |  | 28 | 0.123 |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 6 | 8654 | 0 | 736 | 330000 | NR | NR | 330000
29 | 29.45x | GRI Site 4 | FTIR | NR | GRI Site 4/NR | Radian Corporation | 1994-08-27 | 2000 | HP | 82 | Ingersoll Rand | KVS-412 | Ingersoll Rand/KVS-412/2000 MW / 82% | Natural Gas | Gas Transmission | CO | 385000 | NR | NR | 385000 | 385000 | NA | 3 | 385000 | NR | NR | 7.89 | NR | NR | 7.89 | .521 | NR | NR | .521 | .00481 | NR | NR | .00481 | ppb | PCC |  | 11.4 | NR | NR |  |  | 68 | F | 1009 | Btu/scf | 4706 | NR | NR | 28 | .111 | NR | NR | 1 | 0 | 3 | 82 | 4SLB | Turbo Charged | 12 | 8470 | 1 | 2000 | 239000 | NR | NR | 239000
119 | 119.1 | City of Tulare | CARB 1-100 | Tulary, CA | City of Tulare/Tulary, CA | Steiner Environmental Inc. | 1993-04-30 | 670 | HP | 100 | Waukesha | L5108GC | Waukesha/L5108GC/670 MW / 100% | Process Gas | NR | CO | 587670 | 589730 | NR | 588700 | 589000 | NA | 3 | 587670 | 589730 | NR | 2.75 | 2.68 | NR | 2.72 | NR | NR | NR | NR | .0041 | .004 | NR | .00405 | ppb | NR | IC Engine 2110 | 9.16 | 9.12 | NR | NR | IC Engine 2110 | 68 | F | 800 | Btu/dscf | 1073.29 | 1042.46 | NR | 28 |  |  |  | 2 | 0 | 1 | 100 | 4SLB | NR | NR | NR | 0 | 670 | 295000 | 295000 | NR | 295000

## CI-acetaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
15 | 15.1 | WSPA Pooled Testing Fresno and Ventura Counties / SWEPI | CARB 430 | Ventura County, CA | WSPA Pooled Testing Fresno and Ventura Counties / SWEPI/Ventura County, CA | ENSR Consulting | 1990-09-18 | 850 | HP | 100 | NR | NR | NR/NR/850 MW / 100% | Diesel | NR | Acetaldehyde | 23 | 8 | 6 | 12.3333333333333 | 12.3 | NA | 3 | 23 | 8 | 6 | 0.000184 | 6.39e-05 | 4.79e-05 | 9.86e-05 | 4.7e-05 | .0000163 | .0000123 | .0000252 | .000000216 | .0000000752 | .0000000564 | .000000116 | ppb | NR |  | 10.2 | 10.2 | 10.2 | NR | Std Temp Assumed as 68 | 68 | F | 138300 | Btu/gal | 1166 | 1166 | 1166 | 44 |  |  |  | 3 | 0 | 1 | 100 | NR | NR | NR | 9157 | 2 | 850 | 12.7 | 4.41 | 3.31 | 6.80666666666667
CSU-3 | CSU-3.1.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Acetaldehyde | 680 | NR | NR | 680 | 680 | 800 | 3 | 680 | NR | NR | 0.016737 | NR | NR | 0.016737 | 0.00253 | NR | NR | .00253 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 680 | NR | NR | 680
CSU-3 | CSU-3.10.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Acetaldehyde | 800 | NR | NR | 800 | 800 | 800 | 3 | 800 | NR | NR | 0.019668 | NR | NR | 0.019668 | 0.00297 | NR | NR | .00297 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 800 | NR | NR | 800
CSU-3 | CSU-3.11.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Acetaldehyde | 790 | NR | NR | 790 | 790 | 800 | 3 | 790 | NR | NR | 0.01945 | NR | NR | 0.01945 | 0.00294 | NR | NR | .00294 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 790 | NR | NR | 790
CSU-3 | CSU-3.12.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Acetaldehyde | 1000 | NR | NR | 1000 | 1000 | 800 | 3 | 1000 | NR | NR | 0.02461 | NR | NR | 0.02461 | 0.00372 | NR | NR | .00372 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1000 | NR | NR | 1000
CSU-3 | CSU-3.13.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Acetaldehyde | 920 | NR | NR | 920 | 920 | 800 | 3 | 920 | NR | NR | 0.022648 | NR | NR | 0.022648 | 0.00342 | NR | NR | .00342 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 920 | NR | NR | 920
CSU-3 | CSU-3.14.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Acetaldehyde | 810 | NR | NR | 810 | 810 | 800 | 3 | 810 | NR | NR | 0.019933 | NR | NR | 0.019933 | 0.00301 | NR | NR | .00301 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 810 | NR | NR | 810
CSU-3 | CSU-3.2.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | Acetaldehyde | 780 | NR | NR | 780 | 780 | 800 | 3 | 780 | NR | NR | 0.013437 | NR | NR | 0.013437 | 0.0029 | NR | NR | .0029 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 692 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 780 | NR | NR | 780
CSU-3 | CSU-3.3.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-02 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | Acetaldehyde | 560 | NR | NR | 560 | 560 | 800 | 3 | 560 | NR | NR | 0.0085653 | NR | NR | 0.0085653 | 0.00208 | NR | NR | .00208 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 615 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 560 | NR | NR | 560
CSU-3 | CSU-3.4.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | Acetaldehyde | 590 | NR | NR | 590 | 590 | 800 | 3 | 590 | NR | NR | 0.012875 | NR | NR | 0.012875 | 0.00219 | NR | NR | .00219 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 878 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 590 | NR | NR | 590
CSU-3 | CSU-3.9.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Acetaldehyde | 920 | NR | NR | 920 | 920 | 800 | 3 | 920 | NR | NR | 0.022625 | NR | NR | 0.022625 | 0.00342 | NR | NR | .00342 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 44 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 920 | NR | NR | 920
0.016422

## CI-acrolein
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
15 | 15.1 | WSPA Pooled Testing Fresno and Ventura Counties / SWEPI | CARB 430 | Ventura County, CA | WSPA Pooled Testing Fresno and Ventura Counties / SWEPI/Ventura County, CA | ENSR Consulting | 1990-09-18 | 850 | HP | 100 | NR | NR | NR/NR/850 MW / 100% | Diesel | NR | Acrolein | 5 | ND | ND | 2.33333333333333 | 2.33 | 2 | 3 | 5 | 1 | 1 | .0000508 | .0000102 | .0000102 | .0000237 | .000013 | .0000026 | .0000026 | .00000607 | .0000000598 | .000000012 | .000000012 | .0000000279 | ppb | NR |  | 10.2 | 10.2 | 10.2 | NR | Std Temp Assumed as 68 | 68 | F | 138300 | Btu/gal | 1166 | 1166 | 1166 | 56 |  |  |  | 3 | 2 | 1 | 100 | NR | NR | NR | 9157 | 2 | 850 | 2.76 | ND | ND | 1.58666666666667

## CI-formaldehyde
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
12 | 12.1 | Vandenburg Airforce Base | CARB 430 | Vandenburg, CA | Vandenburg Airforce Base/Vandenburg, CA | Metco Environmental Inc. | 1990-05-01 | 1270 | HP | 100 | Norberg | FS-138-ISC | Norberg/FS-138-ISC/1270 MW / 100% | Diesel | NR | Formaldehyde | ND | ND | 250 | 106.666666666667 | 107 | 70 | 3 | 35 | 35 | 250 | .000668 | .000668 | .00477 | 0.00204 | .0000563 | .0000489 | .000359 | .000155 | .000000526 | .000000526 | .00000376 | .0000016 | ppb | NR |  | 11.6 | 10.2 | 10.5 | 950 |  | 68 | F | NR | Btu/dscf | 4087 | 4087 | 4087 | 30 | .0784 | .0575 | .0561 | 3 | 2 | 1 | 100 | NR | NR | NR | 9190 | 2 | 1270 | ND | ND | 142 | 70.6666666666667
12 | 12.3 | Vandenburg Airforce Base | CARB 430 | Vandenburg, CA | Vandenburg Airforce Base/Vandenburg, CA | Metco Environmental Inc. | 1990-05-01 | 1270 | HP | 60 | Norberg | FS-138-ISC | Norberg/FS-138-ISC/1270 MW / 60% | Diesel | NR | Formaldehyde | 420 | 230 | 270 | 306.666666666667 | 307 | NA | 3 | 420 | 230 | 270 | .00644 | .00353 | .00414 | 0.0047 | .000592 | .000324 | .000384 | .000433 | .00000845 | .00000463 | .00000543 | .00000617 | ppb | NR |  | 10.3 | 10.3 | 10.4 | 600 |  | 68 | F | NR | Btu/dscf | 3287 | 3287 | 3287 | 30 |  |  |  | 3 | 0 | 1 | 60 | NR | NR | NR | 9190 | 2 | 1270 | 234 | 128 | 152 | 171.333333333333
12 | 12.6 | Vandenburg Airforce Base | CARB 430 | Vandenburg, CA | Vandenburg Airforce Base/Vandenburg, CA | Metco Environmental Inc. | 1990-05-01 | 1270 | HP | 100 | Norberg | FS-138-ISC | Norberg/FS-138-ISC/1270 MW / 100% | Diesel | NR | Formaldehyde | 140 | 70 | 270 | 160 | 160 | NA | 3 | 140 | 70 | 270 | .00234 | .00117 | .00468 | 0.00273 | .000199 | .000111 | .000429 | .000246 | .00000184 | .000000921 | .00000369 | .00000215 | ppb | NR |  | 10.4 | 11.5 | 11.5 | 950 |  | 68 | F | NR | Btu/dscf | 3577 | 3577 | 3717 | 30 | .0532 | .0541 | .0520 | 3 | 0 | 1 | 100 | NR | NR | NR | 9190 | 2 | 1270 | 78.7 | 43.9 | 169 | 97.2
12 | 12.7 | Vandenburg Airforce Base | CARB 430 | Vandenburg, CA | Vandenburg Airforce Base/Vandenburg, CA | Metco Environmental Inc. | 1990-05-01 | 1270 | HP | 100 | Norberg | FS-138-ISC | Norberg/FS-138-ISC/1270 MW / 100% | Diesel | NR | Formaldehyde | ND | 380 | ND | 150 | 150 | 70 | 3 | 35 | 380 | 35 | .000665 | .00713 | .000663 | 0.00282 | .0000539 | .000586 | .0000518 | .000231 | .000000524 | .00000561 | .000000522 | .00000222 | ppb | NR |  | 11.2 | 11.2 | 10.8 | 950 | %O2 for formaldehyde assumed same as PAH. | 68 | F | NR | Btu/dscf | 4074 | 4022 | 4057 | 30 | .06 | .0636 | .0654 | 3 | 2 | 1 | 100 | NR | NR | NR | 9190 | 2 | 1270 | ND | 231 | ND | 100.333333333333
13 | 13 | Reidel International | CARB 430 | Portland, OR | Reidel International/Portland, OR | South Coast Environmental Company | 1991-01-30 | 4500 | HP | 100 | Cooper Bessemer + General Electric + Cooper Bessemer | LSV16+JS-8-1+12-567 | Cooper Bessemer + General Electric + Cooper Bessemer/LSV16+JS-8-1+12-567/4500 MW / 100% | Diesel | Pump Drive + Main Electrical Generator + Auxiliary Electrical Generator | Formaldehyde | 0.329 | 1.67 | 3.98 | 1.993 | 1.99 | NA | 3 | 0.329 | 1.67 | 3.98 | .0000101 | .0000509 | .000122 | 6.1e-05 | .000000565 | .00000287 | .00000684 | .00000342 | .00000000224 | .0000000113 | .0000000271 | .0000000135 | ppb | SCR with NH3 | Combination of three engines | 12.2 | 12.2 | 12.2 | NR | Rating is average of three engines : 4500, 1420, 1120 HP. Fuel consumption was calculated during a separate run for multiple metals.. Combination of three engines. Engine family from M&M Table 12/10 | 68 | F | 139700 | Btu/gal | 6564 | 6527 | 6562 | 30 | .0605 | .0672 | .0618 | 3 | 0 | 5 | 100 | 4SLB | Turbo Charged | 16/8/12 | 9190 | 2 | 4500 | .223 | 1.13 | 2.7 | 1.351
15 | 15.1 | WSPA Pooled Testing Fresno and Ventura Counties / SWEPI | CARB 430 | Ventura County, CA | WSPA Pooled Testing Fresno and Ventura Counties / SWEPI/Ventura County, CA | ENSR Consulting | 1990-09-18 | 850 | HP | 100 | NR | NR | NR/NR/850 MW / 100% | Diesel | NR | Formaldehyde | 9 | 24 | 136 | 56.3333333333333 | 56.3 | NA | 3 | 9 | 24 | 136 | .000049 | .000131 | .00074 | 0.000307 | .0000125 | .0000334 | .000189 | .0000783 | .0000000576 | .000000154 | .000000871 | .000000361 | ppb | NR |  | 10.2 | 10.2 | 10.2 | NR | Std Temp Assumed as 68 | 68 | F | 138300 | Btu/gal | 1166 | 1166 | 1166 | 30 |  |  |  | 3 | 0 | 1 | 100 | NR | NR | NR | 9157 | 2 | 850 | 4.96 | 13.2 | 75 | 31.0533333333333
17 | 17 | U.S. Naval Communication Facility | CARB 430 | Stockton, CA | U.S. Naval Communication Facility/Stockton, CA | BTC Environmental Inc. | 1990-04-26 | 625 | HP | 100 | Waukesha | VLRDB | Waukesha/VLRDB/625 MW / 100% | Diesel | NR | Formaldehyde | 140 | 200 | 60 | 133.333333333333 | 133 | NA | 3 | 140 | 200 | 60 | .000787 | .00112 | .000337 | 0.000748 | .000185 | .000267 | .0000787 | .000177 | .00000126 | .00000179 | .000000539 | .0000012 | ppb | NR |  | 9.6 | 9.7 | 9.5 | NR |  | 68 | F | NR | Btu/dscf | 1205 | 1205 | 1205 | 30 |  |  |  | 3 | 0 | 1 | 100 | 4SLB | NR | NR | 9190 | 2 | 625 | 73.1 | 105 | 31.1 | 69.7333333333333
18 | 18 | Naval Weapons Center | CARB 430 | China Lake, CA | Naval Weapons Center/China Lake, CA | Engineering Science Inc. | 1991-09-10 | 800 | HP | 100 | NR | NR | NR/NR/800 MW / 100% | Diesel | NR | Formaldehyde | 17.3 | 17.7 | 18.4 | 17.8 | 17.8 | NA | 3 | 17.3 | 17.7 | 18.4 | .0000478 | .0000487 | .000052 | 4.95e-05 | .0000976 | .0000995 | .000102 | .0000997 | .0000000598 | .0000000609 | .000000065 | .0000000619 | ppb | NR |  | 18.25 | 18.24 | 18.19 | NR |  | 68 | F | NR | Btu/dscf | 592 | 590 | 605 | 30 | .042 | .051 | .04 | 3 | 0 | 1 | 100 | NR | NR | Nr | 9190 | 2 | 800 | 38.5 | 39.3 | 40.1 | 39.3
5 | 5 | Marine Corps Air Ground Combat Center | CARB 430 | Twenty Nine Palms CA | Marine Corps Air Ground Combat Center/Twenty Nine Palms CA | Steiner Environmental Inc., subcontractor to SAIC | 1992-11-01 | 680 | HP | 75 | Caterpillar | NR | Caterpillar/NR/680 MW / 75% | Diesel | NR | Formaldehyde | 547 | 935 | 834 | 772 | 772 | NA | 3 | 547 | 935 | 834 | .00275 | .0048 | .00426 | 0.00394 | .000732 | .00125 | .00113 | .00104 | .00000539 | .00000941 | .00000835 | .00000772 | ppb | NR |  | 9.69 | 9.72 | 9.80 | NR | Engine family from M&M Table 12/10 | 68 | F | 19441 | Btu/lb | 1077 | 1100 | 1095 | 30 | .069 | .072 | .063 | 3 | 0 | 1 | 75 | 4SLB | NR | NR | 9215.75 | 2 | 680 | 288 | 493 | 443 | 408
9 | 9 | Harbor Dredge | CARB 430 | Ventura, CA | Harbor Dredge/Ventura, CA | BTC Environmental Inc. | 1991-01-29 | 1600 | HP | 100 | NR | 248EMD | NR/248EMD/1600 MW / 100% | Diesel | NR | Formaldehyde | 5070 | 5520 | 5400 | 5330 | 5330 | NA | 3 | 5070 | 5520 | 5400 | .141 | .153 | .15 | 0.148 | .0298 | .0324 | .0317 | .0313 | .0000881 | .0000956 | .0000938 | .0000925 | ppb | NR |  | 18.4 | 18.4 | 18.4 | NR | Fuel usage is from an earlier run. | 70 | F | 150689 | Btu/gal | 5966 | 5966 | 5966 | 30 |  |  |  | 3 | 0 | 1 | 100 | NR | NR | NR | 9055 | 2 | 1600 | 12000 | 13000 | 12700 | 12566.6666666667
CSU-3 | CSU-3.1.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Formaldehyde | 1500 | NR | NR | 1500 | 1500 | 150 | 3 | 1500 | NR | NR | 0.025139 | NR | NR | 0.025139 | 0.0038 | NR | NR | .0038 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1500 | NR | NR | 1500
CSU-3 | CSU-3.10.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Formaldehyde | 1600 | NR | NR | 1600 | 1600 | 170 | 3 | 1600 | NR | NR | 0.02682 | NR | NR | 0.02682 | 0.00405 | NR | NR | .00405 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1600 | NR | NR | 1600
CSU-3 | CSU-3.11.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Formaldehyde | 1400 | NR | NR | 1400 | 1400 | 150 | 3 | 1400 | NR | NR | 0.023485 | NR | NR | 0.023485 | 0.00355 | NR | NR | .00355 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1400 | NR | NR | 1400
CSU-3 | CSU-3.12.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Formaldehyde | 1600 | NR | NR | 1600 | 1600 | 150 | 3 | 1600 | NR | NR | 0.026793 | NR | NR | 0.026793 | 0.00405 | NR | NR | .00405 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1600 | NR | NR | 1600
CSU-3 | CSU-3.13.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Formaldehyde | 1600 | NR | NR | 1600 | 1600 | 160 | 3 | 1600 | NR | NR | 0.02682 | NR | NR | 0.02682 | 0.00405 | NR | NR | .00405 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1600 | NR | NR | 1600
CSU-3 | CSU-3.14.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Formaldehyde | 1400 | NR | NR | 1400 | 1400 | 150 | 3 | 1400 | NR | NR | 0.023509 | NR | NR | 0.023509 | 0.00355 | NR | NR | .00355 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1400 | NR | NR | 1400
CSU-3 | CSU-3.2.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | Formaldehyde | 930 | NR | NR | 930 | 930 | 160 | 3 | 930 | NR | NR | 0.010935 | NR | NR | 0.010935 | 0.00236 | NR | NR | .00236 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 692 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 930 | NR | NR | 930
CSU-3 | CSU-3.3.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-02 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | Formaldehyde | 1400 | NR | NR | 1400 | 1400 | 140 | 3 | 1400 | NR | NR | 0.014619 | NR | NR | 0.014619 | 0.00355 | NR | NR | .00355 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 615 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1400 | NR | NR | 1400
CSU-3 | CSU-3.4.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | Formaldehyde | 1600 | NR | NR | 1600 | 1600 | 130 | 3 | 1600 | NR | NR | 0.02381 | NR | NR | 0.02381 | 0.00405 | NR | NR | .00405 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 878 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1600 | NR | NR | 1600
CSU-3 | CSU-3.9.1 | CSU-Engines & Energy Conversion Laboratory | FTIR | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | Formaldehyde | 1300 | NR | NR | 1300 | 1300 | 160 | 3 | 1300 | NR | NR | 0.021765 | NR | NR | 0.021765 | 0.00329 | NR | NR | .00329 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 15.0 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 30 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 1 | 1000 | 1300 | NR | NR | 1300
0.019454
Note: lb/hr values for formaldehyde were calculated for CSU test using the following formula:
EF (lb/MMBtu) * 42.407 Btu/hp-min * Test Rating (hp) * 1 MMBtu/10^6 Btu * 60 min/hr * 1/efficiency of 38%

## CI-CO
Report | ID | Facility Name | Method | Location | Facility | Testing Company | Date | Rating | Unit | Load | Manufacturer | Model | Engine | Fuel Type | Application Type | Pollutant | Run 1 Conc R | Run 2 Conc R | Run 3 Conc R | Average | Conc R Average | DL | SD | Run 1 Conc C | Run 2 Conc C | Run 3 Conc C | lbh1 | lbh2 | lbh3 | lbhAvg | lbMMBtu1 | lbMMBtu2 | lbMMBtu3 | lbMMBtuAvg | lbHP1 | lbHP2 | lbHP3 | lbHPAvg | CUnit | Control Device | Test Data_Comments | Run 1 O2 | Run 2 O2 | Run 3 O2 | Test Rating | Facilities_Comments | Standard Temperature | Standard Temperature Unit | Fuel Heating Value | Fuel Heating Value Unit | Run 1 Gas Flowrate | Run 2 Gas Flowrate | Run 3 Gas Flowrate | MW | Run 1 Fraction Moisture | Run 2 Fraction Moisture | Run 3 Fraction Moisture | Runs | NDs | Tag Control Device | Load1 | Engine Family | Charging Type | Cylinders | Fuel Factor | Flag Method for Aldehydes | Rating1 | Run 1 Conc | Run 2 Conc | Run 3 Conc | AConc
CSU-3 | CSU-3.1.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | CO | 78560 | NR | NR | 78560 | 78600 | NA | 3 | 78560 | NR | NR | 0.68801 | NR | NR | NR | .104 | NR | NR | .104 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 10.40 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 44100 | NR | NR | 44100
CSU-3 | CSU-3.10.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | CO | 75140 | NR | NR | 75140 | 75100 | NA | 3 | 75140 | NR | NR | 0.68209 | NR | NR | NR | .103 | NR | NR | .103 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 10.70 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 43500 | NR | NR | 43500
CSU-3 | CSU-3.11.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | CO | 72630 | NR | NR | 72630 | 72600 | NA | 3 | 72630 | NR | NR | 0.6503 | NR | NR | NR | .0983 | NR | NR | .0983 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 10.59 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 41600 | NR | NR | 41600
CSU-3 | CSU-3.12.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | CO | 74570 | NR | NR | 74570 | 74600 | NA | 3 | 74570 | NR | NR | 0.66816 | NR | NR | NR | .101 | NR | NR | .101 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 10.60 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 42700 | NR | NR | 42700
CSU-3 | CSU-3.13.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | CO | 78930 | NR | NR | 78930 | 78900 | NA | 3 | 78930 | NR | NR | 0.70857 | NR | NR | NR | .107 | NR | NR | .107 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 10.60 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 45200 | NR | NR | 45200
CSU-3 | CSU-3.14.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | CO | 73820 | NR | NR | 73820 | 73800 | NA | 3 | 73820 | NR | NR | 0.65162 | NR | NR | NR | .0984 | NR | NR | .0984 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 10.43 | NR | NR | 989 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 41600 | NR | NR | 41600
CSU-3 | CSU-3.2.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | CO | 73210 | NR | NR | 73210 | 73200 | NA | 3 | 73210 | NR | NR | 0.48189 | NR | NR | NR | .104 | NR | NR | .104 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 11.11 | NR | NR | 692 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 44100 | NR | NR | 44100
CSU-3 | CSU-3.3.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-02 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | CO | 140420 | NR | NR | 140420 | 140000 | NA | 3 | 140420 | NR | NR | 0.74947 | NR | NR | NR | .182 | NR | NR | .182 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 10.11 | NR | NR | 615 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 76800 | NR | NR | 76800
CSU-3 | CSU-3.4.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-09-01 | 1000 | HP | 70 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 70% | Diesel | NR | CO | 148610 | NR | NR | 148610 | 149000 | NA | 3 | 148610 | NR | NR | 1.0582 | NR | NR | NR | .18 | NR | NR | .18 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 9.40 | NR | NR | 878 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 70 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 76200 | NR | NR | 76200
CSU-3 | CSU-3.9.1 | CSU-Engines & Energy Conversion Laboratory | EPA Method 10 | Ft. Collins, CO | CSU-Engines & Energy Conversion Laboratory/Ft. Collins, CO | Pacific Environmental Services | 1999-08-31 | 1000 | HP | 100 | Caterpillar | 3508 | Caterpillar/3508/1000 MW / 100% | Diesel | NR | CO | 66350 | NR | NR | 66350 | 66400 | NA | 3 | 66350 | NR | NR | 0.62252 | NR | NR | NR | .0941 | NR | NR | .0941 | NR | NR | NR | NR | ppb | NR | Fuel Factor is default value | 11.06 | NR | NR | 988 |  | 68 | F | NR | Btu/dscf | NR |  |  | 28 |  |  |  | 1 | 0 | 1 | 100 | 4SLB | NR | 8 | 9190 | 0 | 1000 | 39800 | NR | NR | 39800
[26 empty] | Average | 0.69608
Note: lb/hr values for CO were calculated for CSU test using the following formula:
EF (lb/MMBtu) * 42.407 Btu/hp-min * Test Rating (hp) * 1 MMBtu/10^6 Btu * 60 min/hr * 1/efficiency of 38%

## efficiency calc
| Emissions/Output | Emissions/Input
| (g/hp-hr) | (lb/MMBtu) | (g/hp-hr)
0-200 | 11.2 | 3.66 | 4.2364 | 0.37825
201-400 | 11.8 | 3.94 | 4.5605 | 0.38648
401-1000 | 13 | 4.22 | 4.8846 | 0.37574
1001-2000 | 11.4 | 3.73 | 4.3174 | 0.37872
2001-4000 | 11.4 | 3.74 | 4.329 | 0.37974
4000+ | 12 | 4.2 | 4.8614 | 0.40512
|  |  | Average | 0.38401