## 25F nomo
Monroe-Custer #2 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 028
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6624.5627
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -456.11 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 497.04 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 168.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 682.4 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 497.04 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 949.51 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | -275.58 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1405.89 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 339.25 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1564.23 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 682.4 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 168.29 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 4.53 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 339.25 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 353.75 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 353.75 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 949.51 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 837.34 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 493.2 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1283.87 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 837.34 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -456.11 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1405.89 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -275.58 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 901.4 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 4.53 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1283.87 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 493.2 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1564.23 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 901.4 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Monroe-Custer #2 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 028
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6292.5173
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -305.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 632.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 46.13 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 795.71 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 632.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 820.02 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | -134.33 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1302.04 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 212.95 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1701.21 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 795.71 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 46.13 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 151.08 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 212.95 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 496.63 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 496.63 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 820.02 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 978.45 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 636.53 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1391.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 978.45 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -305.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1302.04 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -134.33 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1042.19 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 151.08 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1391.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 636.53 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1701.21 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1042.19 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Monroe-Custer #2 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 028
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 6009.1007
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -232.8 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 689.72 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 108.06 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 600.55 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 689.72 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 882.52 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | -50.25 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1362.31 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 288.78 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1796.3 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 600.55 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 108.06 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 227.74 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 288.78 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 567.84 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 567.84 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 882.52 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1050.87 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 712.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1483.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1050.87 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -232.8 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1362.31 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -50.25 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1118.17 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 227.74 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1483.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 712.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1796.3 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1118.17 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Monroe-Custer #2 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 028
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4932.3
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 227.38 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 909.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 607.87 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1058.51 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 909.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1285.72 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 440.99 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1641.2 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 775.77 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1162.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1058.51 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 607.87 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 683.95 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 775.77 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1047.47 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1047.47 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1285.72 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1513.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1171.57 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1223.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1513.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 227.38 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1641.2 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 440.99 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1287.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 683.95 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1223.99 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1171.57 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1162.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1287.73 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Monroe-Custer #2 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 028
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4597.942
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 345.55 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 835.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 679.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 983.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 835.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1217.32 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 546.86 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1593.68 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 901.66 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1028.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 983.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 679.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 817.53 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 901.66 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 1150.71 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1150.71 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1217.32 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1621.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1290.25 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1086.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1621.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 345.55 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 775 | 1593.68 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 546.86 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1151.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 817.53 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 460 | 1086.24 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1290.25 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1400 | 775 | 1028.06 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1151.27 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Monroe-Custer #2 500kV Line (COV-CRES BYP @ COV)
G0 | -456.11 | -305.79 | -232.8 | 227.38 | 345.55
G1 | 168.29 | 46.13 | 108.06 | 607.87 | 679.18 | Season/Year: | WINTER 2009
G2 | 497.04 | 632.79 | 689.72 | 909.54 | 835.79 | Direction: | South-to-North (SN)
G3 | -275.58 | -134.33 | -50.25 | 440.99 | 546.86 | Case Loads: | Heavy Loads
G4 | 339.25 | 212.95 | 288.78 | 775.77 | 901.66 | Outage: | 028
G5 | 682.4 | 795.71 | 600.55 | 1058.51 | 983.91 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 4.53 | 151.08 | 227.74 | 683.95 | 817.53 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 353.75 | 496.63 | 567.84 | 1047.47 | 1150.71 | Study Person: | FRP9899
G8 | 949.51 | 820.02 | 882.52 | 1285.72 | 1217.32 | Source: | 028WINTER09v1SNH
G9 | 493.2 | 636.53 | 712.54 | 1171.57 | 1290.25
G10 | 837.34 | 978.45 | 1050.87 | 1513.91 | 1621.44
G11 | 1405.89 | 1302.04 | 1362.31 | 1641.2 | 1593.68
G12 | 901.4 | 1042.19 | 1118.17 | 1287.73 | 1151.27
G13 | 1283.87 | 1391.91 | 1483.18 | 1223.99 | 1086.24
G14 | 1564.23 | 1701.21 | 1796.3 | 1162.91 | 1028.06
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 028 | Monroe-Custer #2 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6624.5627 | -456.11 | 168.29 | 497.04 | -275.58 | 339.25 | 682.4 | 4.53 | 353.75 | 949.51 | 493.2 | 837.34 | 1405.89 | 901.4 | 1283.87 | 1564.23
35F | 6292.5173 | -305.79 | 46.13 | 632.79 | -134.33 | 212.95 | 795.71 | 151.08 | 496.63 | 820.02 | 636.53 | 978.45 | 1302.04 | 1042.19 | 1391.91 | 1701.21
45F | 6009.1007 | -232.8 | 108.06 | 689.72 | -50.25 | 288.78 | 600.55 | 227.74 | 567.84 | 882.52 | 712.54 | 1050.87 | 1362.31 | 1118.17 | 1483.18 | 1796.3
60F | 4932.3 | 227.38 | 607.87 | 909.54 | 440.99 | 775.77 | 1058.51 | 683.95 | 1047.47 | 1285.72 | 1171.57 | 1513.91 | 1641.2 | 1287.73 | 1223.99 | 1162.91
70F | 4597.942 | 345.55 | 679.18 | 835.79 | 546.86 | 901.66 | 983.91 | 817.53 | 1150.71 | 1217.32 | 1290.25 | 1621.44 | 1593.68 | 1151.27 | 1086.24 | 1028.06

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -456.38 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -501.33 | -501.61 | 6660.83 | -456.11 | 105.86 | FULL
G1 | 169.56 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -549.85 | -549.52 | 6596.42 | 168.29 | -183.79 | CTG_FAIL_IN_FULL
G2 | 497.53 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -545.37 | -545.5 | 6616.53 | 497.04 | -324.93 | CTG_FAIL_IN_FULL
G3 | -276.71 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -505.1 | -505.25 | 6659.29 | -275.58 | 69.79 | FULL
G4 | 337.41 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -551.02 | -550.96 | 6595.5 | 339.25 | -214.04 | CTG_FAIL_IN_FULL
G5 | 683.69 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -549.77 | -549.45 | 6615.78 | 682.4 | -364.34 | CTG_FAIL_IN_FULL
G6 | 3.39 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -506.18 | -506.27 | 6653.54 | 4.53 | 44.98 | FULL
G7 | 352.14 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -502.05 | -502.47 | 6590.04 | 353.75 | -112.8 | FULL
G8 | 949.44 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -549.38 | -548.97 | 6615.9 | 949.51 | -394.58 | CTG_FAIL_IN_FULL
G9 | 492.58 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -506.45 | -506.56 | 6658.98 | 493.2 | -19.51 | FULL
G10 | 837.15 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -502.4 | -502.77 | 6595.73 | 837.34 | -176.79 | FULL
G11 | 1406.32 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -545.26 | -545.28 | 6619.99 | 1405.89 | -432.67 | CTG_FAIL_IN_FULL
G12 | 902.84 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -507.19 | -507.29 | 6664.47 | 901.4 | -90.73 | FULL
G13 | 1284.15 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -513.61 | -513.78 | 6602.84 | 1283.87 | -265.06 | FULL
G14 | 1564.03 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -497.2 | -496.83 | 6622.6 | 1564.23 | -374.02 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -308.47 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -493.5 | -494.2 | 6329.16 | -305.79 | 56.98 | FULL
G1 | 45.2 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -490.25 | -490.94 | 6258.78 | 46.13 | -78.27 | FULL
G2 | 633.99 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -534.42 | -534.1 | 6285.81 | 632.79 | -361.86 | CTG_FAIL_IN_FULL
G3 | -135.74 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -496.17 | -496.25 | 6324.78 | -134.33 | 40.88 | FULL
G4 | 213.06 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -491.8 | -492.21 | 6258.43 | 212.95 | -110.94 | FULL
G5 | 797.24 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -535.45 | -535.09 | 6284.9 | 795.71 | -387.73 | CTG_FAIL_IN_FULL
G6 | 150.93 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -498.69 | -498.09 | 6322.08 | 151.08 | 5.7 | FULL
G7 | 497.35 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -493.05 | -493.24 | 6259.63 | 496.63 | -144.62 | FULL
G8 | 819.9 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -485.68 | -485.41 | 6280.01 | 820.02 | -292.02 | FULL
G9 | 637.61 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -499.49 | -498.85 | 6328.21 | 636.53 | -57.92 | FULL
G10 | 978.76 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -494.88 | -495.16 | 6265.76 | 978.45 | -207.01 | FULL
G11 | 1302.29 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -485.7 | -485.54 | 6286.93 | 1302.04 | -354.49 | FULL
G12 | 1042.51 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -499.29 | -499.4 | 6334.76 | 1042.19 | -128.22 | FULL
G13 | 1391.97 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -495.51 | -495.69 | 6273.53 | 1391.91 | -286.62 | FULL
G14 | 1701.22 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -487.08 | -487.77 | 6294.99 | 1701.21 | -423.01 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -233.47 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -483.34 | -483.43 | 6044.09 | -232.8 | 45.96 | FULL
G1 | 106.82 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -478.36 | -478.54 | 5975.52 | 108.06 | -95.48 | FULL
G2 | 688.38 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.71 | -519.96 | -520.03 | 6002.9 | 689.72 | -381.82 | CTG_FAIL_IN_FULL
G3 | -51.48 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -488.44 | -488.38 | 6039.21 | -50.25 | 15.18 | FULL
G4 | 288.05 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -481.58 | -481.75 | 5975.46 | 288.78 | -130.65 | FULL
G5 | 600.42 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -474.48 | -474.32 | 5996.06 | 600.55 | -271.8 | FULL
G6 | 227.13 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -490.09 | -489.62 | 6038.77 | 227.74 | -18.98 | FULL
G7 | 568.05 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -485.59 | -485.71 | 5976.49 | 567.84 | -166.8 | FULL
G8 | 882.26 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -476.94 | -477.44 | 5997.53 | 882.52 | -310.72 | FULL
G9 | 712.24 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -490.67 | -490.27 | 6045.27 | 712.54 | -82.45 | FULL
G10 | 1050.72 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -486.18 | -486.35 | 5983.4 | 1050.87 | -230.28 | FULL
G11 | 1362.46 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -476.92 | -477.45 | 6004.86 | 1362.31 | -372.7 | FULL
G12 | 1118.06 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -490.85 | -490.24 | 6052.3 | 1118.17 | -153.2 | FULL
G13 | 1483.02 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -492.88 | -493.01 | 5991.97 | 1483.18 | -320.93 | FULL
G14 | 1796.34 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -485.58 | -485.41 | 6012.68 | 1796.3 | -449.1 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 227.4 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -470.25 | -470.02 | 4962.18 | 227.38 | -79.08 | FULL
G1 | 607.01 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -475.58 | -475.04 | 4902.72 | 607.87 | -250.76 | FULL
G2 | 910.4 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -467.32 | -467.6 | 4924.46 | 909.54 | -387.37 | FULL
G3 | 440.16 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -481.95 | -481.74 | 4963.3 | 440.99 | -133.25 | FULL
G4 | 775.96 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -476.81 | -476.38 | 4903.15 | 775.77 | -279.38 | FULL
G5 | 1057.84 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.07 | -424.67 | -424.59 | 4924.23 | 1058.51 | -405.99 | FULL
G6 | 684.71 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -476.36 | -476.15 | 4964.05 | 683.95 | -148.11 | FULL
G7 | 1047.75 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -476.89 | -476.96 | 4905 | 1047.47 | -323.77 | FULL
G8 | 1283.77 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.07 | -427.03 | -427 | 4924.53 | 1285.72 | -415.7 | FULL
G9 | 1171.82 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -477.71 | -477.47 | 4972.51 | 1171.57 | -225.12 | FULL
G10 | 1514.1 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -475.04 | -474.55 | 4913.19 | 1513.91 | -371.13 | FULL
G11 | 1641.59 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.07 | -423.76 | -423.93 | 4927.94 | 1641.2 | -408.42 | FULL
G12 | 1288.27 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -13.33 | -426.55 | -426.31 | 4974.03 | 1287.73 | -144.57 | FULL
G13 | 1224.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -13.33 | -426.07 | -425.76 | 4905.3 | 1223.99 | -80.56 | FULL
G14 | 1163.46 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -13.33 | -423.93 | -423.59 | 4917.91 | 1162.91 | -10.31 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 344.69 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -456.19 | -455.92 | 4628.66 | 345.55 | -117.28 | FULL
G1 | 678.5 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -450.51 | -449.83 | 4568.88 | 679.18 | -262.41 | FULL
G2 | 835.29 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.07 | -398.74 | -398.7 | 4586.11 | 835.79 | -315.85 | FULL
G3 | 546.32 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -464.6 | -464.37 | 4629.99 | 546.86 | -166.42 | FULL
G4 | 903.05 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -466 | -465.61 | 4571.13 | 901.66 | -315.86 | FULL
G5 | 982.87 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.07 | -408.7 | -408.68 | 4586.35 | 983.91 | -334.36 | FULL
G6 | 817.85 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -464.95 | -464.72 | 4631.57 | 817.53 | -199.24 | FULL
G7 | 1152.5 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -460.79 | -460.31 | 4572.99 | 1150.71 | -344.9 | FULL
G8 | 1219.36 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.07 | -412.45 | -412.26 | 4587.06 | 1217.32 | -354.13 | FULL
G9 | 1290.54 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -464.48 | -464.24 | 4640.67 | 1290.25 | -259.11 | FULL
G10 | 1621.79 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -23.44 | -459.75 | -459.14 | 4580.47 | 1621.44 | -403.38 | FULL
G11 | 1594.04 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -21.07 | -412.99 | -413.09 | 4592.53 | 1593.68 | -358.57 | FULL
G12 | 1151.82 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -13.33 | -424.3 | -424.15 | 4638.25 | 1151.27 | -36.19 | FULL
G13 | 1086.73 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -13.33 | -423.86 | -423.64 | 4570.07 | 1086.24 | 28.14 | FULL
G14 | 1028.47 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -13.33 | -423.81 | -423.43 | 4584.4 | 1028.06 | 88.09 | FULL
028WINTER09v1SNH