## 25F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 023
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 6643.3793
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -3505.44 | BFR: 5050 Monroe 500/230kV Bk#1 & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | -2297.96 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 460 | -2642.85 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | -2151.86 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 775 | -2297.96 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G9 | 525 | 775 | -733.82 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 140 | -3006.73 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | -285.98 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 460 | -2428.74 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 307.14 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 775 | -2151.86 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -2642.85 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 140 | -2520.62 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -2428.74 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 460 | -2169.27 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G8 | 525 | 460 | -2169.27 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 775 | -733.82 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | -627.68 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 140 | -2163.66 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | -501.74 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 460 | -627.68 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -3505.44 | BFR: 5050 Monroe 500/230kV Bk#1 & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | -285.98 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -3006.73 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | -1461.24 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -2520.62 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | -501.74 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | -2163.66 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 775 | 307.14 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | -1461.24 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 023
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 6290.3133
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -2688.17 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | -759.86 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 460 | -2195.63 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | -595.43 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 775 | -759.86 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G9 | 525 | 775 | -69.91 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 140 | -2361.41 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 476.14 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 460 | -2044.55 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 885.35 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 775 | -595.43 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -2195.63 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 140 | -2109.88 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -2044.55 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 460 | -644.36 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G8 | 525 | 460 | -644.36 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 775 | -69.91 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 2.83 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 140 | -576.7 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 464.71 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 460 | 2.83 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -2688.17 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | 476.14 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -2361.41 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | -17.38 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -2109.88 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | 464.71 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | -576.7 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 775 | 885.35 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | -17.38 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 023
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 5998.2213
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | -2238.17 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | -425.05 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 460 | -755.15 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 42.14 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 775 | -425.05 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 309.53 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 140 | -2069.22 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 791.06 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 460 | -594.51 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1205.43 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 775 | 42.14 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G2 | 100 | 465 | -755.15 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 140 | -683.86 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | -594.51 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 460 | -317.87 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G8 | 525 | 460 | -317.87 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 775 | 309.53 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 470.49 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 140 | 0.01 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 876.4 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 460 | 470.49 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G1 | 100 | 140 | -2238.17 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | 791.06 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G4 | 260 | 140 | -2069.22 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | 462.25 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G7 | 525 | 140 | -683.86 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | 876.4 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 0.01 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 775 | 1205.43 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 462.25 | T-1: Eastpine 230/115kV Bank | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 023
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 4922.3333
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 234.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 883.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 460 | 572.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1006.22 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
100 | 775 | 883.18 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1308.77 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 140 | 373.77 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1775.7 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
260 | 460 | 674.25 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1560.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1006.22 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 572.54 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 140 | 640.89 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 674.25 | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 460 | 988.98 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 988.98 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 775 | 1308.77 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1455.08 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 140 | 1117.59 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1634.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1455.08 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 234.44 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | 1775.7 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 373.77 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | 1510.92 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 640.89 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | 1634.83 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1117.59 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 775 | 1560.91 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1510.92 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Heavy Loads
Outage: |  | 023
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 4590.8167
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 598.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 1017.99 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 939.59 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1134.01 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 1017.99 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1350.96 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 757.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1729.76 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 1092.82 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 1384.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 1134.01 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 939.59 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 140 | 1027.01 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 1092.82 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 460 | 1355.11 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 1355.11 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
525 | 775 | 1350.96 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1787.85 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1515.81 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1437.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1787.85 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 598.79 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1000 | 775 | 1729.76 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 757.91 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 140 | 1521.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 1027.01 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 460 | 1437.88 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1515.81 | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV]
1400 | 775 | 1384.11 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 1521.21 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
G0 | -3505.44 | -2688.17 | -2238.17 | 234.44 | 598.79
G1 | -2642.85 | -2195.63 | -755.15 | 572.54 | 939.59 | Season/Year: | WINTER 2009
G2 | -2297.96 | -759.86 | -425.05 | 883.18 | 1017.99 | Direction: | South-to-North (SN)
G3 | -3006.73 | -2361.41 | -2069.22 | 373.77 | 757.91 | Case Loads: | Heavy Loads
G4 | -2428.74 | -2044.55 | -594.51 | 674.25 | 1092.82 | Outage: | 023
G5 | -2151.86 | -595.43 | 42.14 | 1006.22 | 1134.01 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | -2520.62 | -2109.88 | -683.86 | 640.89 | 1027.01 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | -2169.27 | -644.36 | -317.87 | 988.98 | 1355.11 | Study Person: | FRP9899
G8 | -733.82 | -69.91 | 309.53 | 1308.77 | 1350.96 | Source: | 023WINTER09v1SNH
G9 | -2163.66 | -576.7 | 0.01 | 1117.59 | 1515.81
G10 | -627.68 | 2.83 | 470.49 | 1455.08 | 1787.85
G11 | -285.98 | 476.14 | 791.06 | 1775.7 | 1729.76
G12 | -1461.24 | -17.38 | 462.25 | 1510.92 | 1521.21
G13 | -501.74 | 464.71 | 876.4 | 1634.83 | 1437.88
G14 | 307.14 | 885.35 | 1205.43 | 1560.91 | 1384.11
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| YES | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Heavy Loads |  |  | 023 | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 6643.3793 | -3505.44 | -2642.85 | -2297.96 | -3006.73 | -2428.74 | -2151.86 | -2520.62 | -2169.27 | -733.82 | -2163.66 | -627.68 | -285.98 | -1461.24 | -501.74 | 307.14
35F | 6290.3133 | -2688.17 | -2195.63 | -759.86 | -2361.41 | -2044.55 | -595.43 | -2109.88 | -644.36 | -69.91 | -576.7 | 2.83 | 476.14 | -17.38 | 464.71 | 885.35
45F | 5998.2213 | -2238.17 | -755.15 | -425.05 | -2069.22 | -594.51 | 42.14 | -683.86 | -317.87 | 309.53 | 0.01 | 470.49 | 791.06 | 462.25 | 876.4 | 1205.43
60F | 4922.3333 | 234.44 | 572.54 | 883.18 | 373.77 | 674.25 | 1006.22 | 640.89 | 988.98 | 1308.77 | 1117.59 | 1455.08 | 1775.7 | 1510.92 | 1634.83 | 1560.91
70F | 4590.8167 | 598.79 | 939.59 | 1017.99 | 757.91 | 1092.82 | 1134.01 | 1027.01 | 1355.11 | 1350.96 | 1515.81 | 1787.85 | 1729.76 | 1521.21 | 1437.88 | 1384.11

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -3527.78 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 5050 Monroe 500/230kV Bk#1 & Mon Caps | -1.68 | -144.16 | -144.18 | 6744.71 | -3505.44 | 0 | YES
G1 | -2653.76 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.17 | -145.1 | 6625.5 | -2642.85 | 0 | FULL
G2 | -2305.8 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -144.94 | -145.43 | 6628.16 | -2297.96 | 0 | FULL
G3 | -3021.89 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -132.37 | -147.67 | 6715.15 | -3006.73 | 0 | CTG_FAIL_IN_FULL
G4 | -2438.94 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.98 | -146 | 6619.44 | -2428.74 | 0 | FULL
G5 | -2160.39 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -144.79 | -144.82 | 6625.44 | -2151.86 | 0 | FULL
G6 | -2532.06 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146 | -145.99 | 6702.3 | -2520.62 | 0 | FULL
G7 | -2177.97 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.87 | -145.89 | 6621.65 | -2169.27 | 0 | FULL
G8 | -734.82 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -144.28 | -144.26 | 6593.9 | -733.82 | 0 | FULL
G9 | -2170.71 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.1 | -145.14 | 6711.02 | -2163.66 | 0 | FULL
G10 | -628.36 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -144.81 | -144.8 | 6589.94 | -627.68 | 0 | FULL
G11 | -285.25 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -144.67 | -144.66 | 6596.96 | -285.98 | 0 | FULL
G12 | -1461.08 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.13 | -144.84 | 6680.07 | -1461.24 | 0 | FULL
G13 | -502.12 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -144.23 | -144.21 | 6597.51 | -501.74 | 0 | FULL
G14 | 306.18 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | T-1: Eastpine 230/115kV Bank | -2.84 | -142.88 | -142.8 | 6598.94 | 307.14 | 0 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -2700.83 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.45 | -145.5 | -145.48 | 6365.73 | -2688.17 | 0 | CTG_FAIL_IN_FULL
G1 | -2203.34 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.14 | -146.15 | 6279.38 | -2195.63 | 0 | FULL
G2 | -762.55 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -144.58 | -144.57 | 6261.25 | -759.86 | 0 | FULL
G3 | -2370.27 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.6 | -146.61 | 6354.82 | -2361.41 | 0 | FULL
G4 | -2050.98 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.91 | -145.88 | 6276.44 | -2044.55 | 0 | FULL
G5 | -595.78 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -144.57 | -144.48 | 6259.16 | -595.43 | 0 | FULL
G6 | -2116.92 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.4 | -146.41 | 6356.13 | -2109.88 | 0 | FULL
G7 | -644.92 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.08 | -145.07 | 6249.05 | -644.36 | 0 | FULL
G8 | -71.75 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | T-1: Eastpine 230/115kV Bank | -2.84 | -144.17 | -144.16 | 6258.37 | -69.91 | 0 | FULL
G9 | -576.25 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.11 | -145.1 | 6328.22 | -576.7 | 0 | FULL
G10 | 1.61 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | T-1: Eastpine 230/115kV Bank | -2.84 | -144.19 | -144.13 | 6252.08 | 2.83 | 0 | FULL
G11 | 477.11 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.13 | -145.16 | 6262.38 | 476.14 | 0 | FULL
G12 | -18.66 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | T-1: Eastpine 230/115kV Bank | -2.84 | -144.12 | -144.13 | 6329.14 | -17.38 | 0 | FULL
G13 | 465.41 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | T-1: Eastpine 230/115kV Bank | -2.84 | -144.25 | -144.17 | 6255.71 | 464.71 | 0 | FULL
G14 | 884.14 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.25 | -145.26 | 6266.84 | 885.35 | 0 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | -2247.56 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.53 | -146.53 | 6065.48 | -2238.17 | 0 | FULL
G1 | -757.32 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.72 | -145.67 | 5965.86 | -755.15 | 0 | FULL
G2 | -424.76 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.37 | -145.37 | 5976.95 | -425.05 | 0 | FULL
G3 | -2077.99 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.62 | -146.62 | 6061.93 | -2069.22 | 0 | FULL
G4 | -596.36 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.57 | -145.53 | 5963.65 | -594.51 | 0 | FULL
G5 | 42.8 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.68 | -145.69 | 5975.7 | 42.14 | 0 | FULL
G6 | -684.54 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.58 | -145.57 | 6036.02 | -683.86 | 0 | FULL
G7 | -320.3 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.51 | -145.55 | 5963.66 | -317.87 | 0 | FULL
G8 | 309.35 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.54 | -145.58 | 5975.71 | 309.53 | 0 | FULL
G9 | -1.21 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | T-1: Eastpine 230/115kV Bank | -2.84 | -145.3 | -145.26 | 6038.75 | 0.01 | 0 | FULL
G10 | 469.73 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -146.02 | -146.02 | 5967.71 | 470.49 | 0 | FULL
G11 | 792.16 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.76 | -145.75 | 5980.68 | 791.06 | 0 | FULL
G12 | 460.22 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | T-1: Eastpine 230/115kV Bank | -2.84 | -145.32 | -145.29 | 6042.67 | 462.25 | 0 | FULL
G13 | 875.25 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.09 | -146.09 | 5972.43 | 876.4 | 0 | FULL
G14 | 1203.83 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -145.93 | -145.92 | 5986.12 | 1205.43 | 0 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 235.32 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -147.08 | -147.08 | 4956.09 | 234.44 | 0 | FULL
G1 | 571.36 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.87 | -146.84 | 4890.7 | 572.54 | 0 | FULL
G2 | 881.49 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.46 | -146.35 | 4908.97 | 883.18 | 0 | FULL
G3 | 374.3 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.59 | -146.65 | 4955.1 | 373.77 | 0 | FULL
G4 | 673.8 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.37 | -145.35 | 4890.38 | 674.25 | 0 | FULL
G5 | 1004.64 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4672 Chief Jo-Mon 500kV & Mon Caps | -3.7 | -145.28 | -145.2 | 4909.02 | 1006.22 | 0 | FULL
G6 | 641.62 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.58 | -146.63 | 4955.93 | 640.89 | 0 | FULL
G7 | 988.81 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.7 | -146.61 | 4891.5 | 988.98 | 0 | FULL
G8 | 1305.75 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.28 | -146.24 | 4909.67 | 1308.77 | 0 | FULL
G9 | 1115.25 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.62 | -146.61 | 4963.39 | 1117.59 | 0 | FULL
G10 | 1453.64 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.32 | -146.39 | 4898.63 | 1455.08 | 0 | FULL
G11 | 1769.3 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.05 | -146.01 | 4917.37 | 1775.7 | 0 | FULL
G12 | 1509.86 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.38 | -146.49 | 4970.95 | 1510.92 | 0 | FULL
G13 | 1630.31 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.72 | -430.57 | -430.41 | 4902.72 | 1634.83 | 0 | FULL
G14 | 1557.65 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.72 | -426.16 | -425.88 | 4914.58 | 1560.91 | 0 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 599.75 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.73 | -146.83 | 4624.97 | 598.79 | 0 | FULL
G1 | 937.46 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.59 | -146.64 | 4562.61 | 939.59 | 0 | FULL
G2 | 1016.16 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -22.52 | -405.65 | -405.92 | 4576.16 | 1017.99 | 0 | FULL
G3 | 756.44 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.68 | -146.66 | 4624.89 | 757.91 | 0 | FULL
G4 | 1090.36 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.46 | -146.51 | 4563.02 | 1092.82 | 0 | FULL
G5 | 1131.63 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -22.52 | -407.5 | -407.95 | 4575.81 | 1134.01 | 0 | FULL
G6 | 1024.88 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.71 | -146.69 | 4626.55 | 1027.01 | 0 | FULL
G7 | 1351.84 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -146.36 | -146.3 | 4564.17 | 1355.11 | 0 | FULL
G8 | 1350.19 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -22.52 | -408.42 | -408.08 | 4574.99 | 1350.96 | 0 | FULL
G9 | 1512.26 | Branch MASS (46433) TO MASS (46435) CKT 2 [115.00 - 230.00 kV] | BFR: 4714 Chief Jo-Mon 500kV & Mon Caps | -3.68 | -147.01 | -146.99 | 4634.21 | 1515.81 | 0 | FULL
G10 | 1782.68 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -22.52 | -412.02 | -410.63 | 4570.03 | 1787.85 | 0 | FULL
G11 | 1727 | Branch HRTAP MS (40963) TO SNOH S4 (41330) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -22.52 | -410.58 | -411.11 | 4580.89 | 1729.76 | 0 | FULL
G12 | 1518.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.72 | -421.72 | -421.68 | 4636.39 | 1521.21 | 0 | FULL
G13 | 1435.48 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.72 | -416.88 | -416.82 | 4567.12 | 1437.88 | 0 | FULL
G14 | 1379.52 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -12.72 | -420.72 | -420.71 | 4580.44 | 1384.11 | 0 | FULL
023WINTER09v1SNH