## 25F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 001R2
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3177.9287
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3246.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3306.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 3292.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3373.01 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3306.34 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 3534.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
260 | 140 | 3335.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2769.39 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3359.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | 475.31 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3373.01 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3292.57 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3492.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G5 | 260 | 460 | 3359.8 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3511.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G8 | 525 | 460 | 3511.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 775 | 3534.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G11 | 1000 | 460 | 2815.96 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2866.14 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | 553.79 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2815.96 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3246.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2769.39 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3335.39 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | 644.3 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3492.38 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 460 | 553.79 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2866.14 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | 475.31 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | 644.3 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 35F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 001R2
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2503.4613
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3198.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3250.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 3237.5 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 3324.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3250.24 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 3133.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 3277.85 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 2150.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 3316.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -451.75 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 3324.59 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3237.5 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 3397.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 3316.51 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 3162.52 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 3162.52 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 3133.74 | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 2258.05 | 3TM: Murr - Cust - Sedro 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 2363.12 | 3TM: Murr - Cust - Sedro 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -380.79 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 2258.05 | 3TM: Murr - Cust - Sedro 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3198.69 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 2150.94 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 3277.85 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -304.58 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 3397.74 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 460 | -380.79 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 2363.12 | 3TM: Murr - Cust - Sedro 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -451.75 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -304.58 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 45F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 001R2
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2265.3693
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 3121.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 3151.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 3140.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2995.38 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 3151.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2817.55 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2933.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 900.03 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2954.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -1537.75 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2995.38 | N-1: Monroe - Custer #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 3140.67 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2868.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 2954.66 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2845.38 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2845.38 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 2817.55 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 984.1 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1156.4 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -1489.34 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 984.1 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 3121.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 900.03 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2933.76 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -1430.01 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2868.52 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 460 | -1489.34 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1156.4 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1537.75 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -1430.01 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 60F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 001R2
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2789.9047
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2651.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2662.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2663.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2757.79 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2662.09 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2716.42 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2720.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1574.33 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2752.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -1037.57 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2757.79 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 460 | 2663.11 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2814.21 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 2752.72 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2740.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2740.99 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 2716.42 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 1680.37 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1800.19 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -969.75 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1680.37 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2651.14 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1574.33 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2720.33 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -911.91 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2814.21 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 460 | -969.75 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1800.19 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -1037.57 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -911.91 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## 70F nomo
Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
WINTER 2009
South-to-North (SN)
Light Loads
Outage: |  | 001R2
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3142.1007
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2518.64 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G3 | 100 | 775 | 2542.02 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 460 | 2532.31 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G6 | 260 | 775 | 2627.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
100 | 775 | 2542.02 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G9 | 525 | 775 | 2603.12 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
260 | 140 | 2618.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G12 | 1000 | 775 | 1673.86 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 460 | 2614.15 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G15 | 1400 | 775 | -941.28 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
260 | 775 | 2627.03 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] |  |  | G2 | 100 | 465 | 2532.31 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 140 | 2702.04 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G5 | 260 | 460 | 2614.15 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
525 | 460 | 2669.09 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G8 | 525 | 460 | 2669.09 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
525 | 775 | 2603.12 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] |  |  | G11 | 1000 | 460 | 1769.81 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 140 | 1894.53 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G14 | 1400 | 460 | -872 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 460 | 1769.81 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G1 | 100 | 140 | 2518.64 | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1000 | 775 | 1673.86 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G4 | 260 | 140 | 2618.54 | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV]
1400 | 140 | -803.82 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G7 | 525 | 140 | 2702.04 | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV]
1400 | 460 | -872 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G10 | 1000 | 140 | 1894.53 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1400 | 775 | -941.28 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G13 | 1400 | 140 | -803.82 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
[5 empty] | 2000 | 0
[5 empty] | 2000 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
G0 | 3246.24 | 3198.69 | 3121.03 | 2651.14 | 2518.64
G1 | 3292.57 | 3237.5 | 3140.67 | 2663.11 | 2532.31 | Season/Year: | WINTER 2009
G2 | 3306.34 | 3250.24 | 3151.11 | 2662.09 | 2542.02 | Direction: | South-to-North (SN)
G3 | 3335.39 | 3277.85 | 2933.76 | 2720.33 | 2618.54 | Case Loads: | Light Loads
G4 | 3359.8 | 3316.51 | 2954.66 | 2752.72 | 2614.15 | Outage: | 001R2
G5 | 3373.01 | 3324.59 | 2995.38 | 2757.79 | 2627.03 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 3492.38 | 3397.74 | 2868.52 | 2814.21 | 2702.04 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 3511.03 | 3162.52 | 2845.38 | 2740.99 | 2669.09 | Study Person: | FRP9899
G8 | 3534.38 | 3133.74 | 2817.55 | 2716.42 | 2603.12 | Source: | 001R2WINTER09v5SNL
G9 | 2866.14 | 2363.12 | 1156.4 | 1800.19 | 1894.53
G10 | 2815.96 | 2258.05 | 984.1 | 1680.37 | 1769.81
G11 | 2769.39 | 2150.94 | 900.03 | 1574.33 | 1673.86
G12 | 644.3 | -304.58 | -1430.01 | -911.91 | -803.82
G13 | 553.79 | -380.79 | -1489.34 | -969.75 | -872
G14 | 475.31 | -451.75 | -1537.75 | -1037.57 | -941.28
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | CTG_FAIL_IN_FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| CTG_FAIL_IN_FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
South-to-North (SN) |  |  |  | Light Loads |  |  | 001R2 | Bellingham-Custer #1 230kV Line with Novelty Hill Transformer I/S (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3177.9287 | 3246.24 | 3292.57 | 3306.34 | 3335.39 | 3359.8 | 3373.01 | 3492.38 | 3511.03 | 3534.38 | 2866.14 | 2815.96 | 2769.39 | 644.3 | 553.79 | 475.31
35F | 2503.4613 | 3198.69 | 3237.5 | 3250.24 | 3277.85 | 3316.51 | 3324.59 | 3397.74 | 3162.52 | 3133.74 | 2363.12 | 2258.05 | 2150.94 | -304.58 | -380.79 | -451.75
45F | 2265.3693 | 3121.03 | 3140.67 | 3151.11 | 2933.76 | 2954.66 | 2995.38 | 2868.52 | 2845.38 | 2817.55 | 1156.4 | 984.1 | 900.03 | -1430.01 | -1489.34 | -1537.75
60F | 2789.9047 | 2651.14 | 2663.11 | 2662.09 | 2720.33 | 2752.72 | 2757.79 | 2814.21 | 2740.99 | 2716.42 | 1800.19 | 1680.37 | 1574.33 | -911.91 | -969.75 | -1037.57
70F | 3142.1007 | 2518.64 | 2532.31 | 2542.02 | 2618.54 | 2614.15 | 2627.03 | 2702.04 | 2669.09 | 2603.12 | 1894.53 | 1769.81 | 1673.86 | -803.82 | -872 | -941.28

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3246.4 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2688.98 | -2687.91 | 3248.95 | 3246.24 | -2142.47 | CTG_FAIL_IN_FULL
G1 | 3292.36 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2714.7 | -2714.44 | 3177.05 | 3292.57 | -2151.55 | CTG_FAIL_IN_FULL
G2 | 3305.79 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2710.92 | -2711.44 | 3189.19 | 3306.34 | -2132.74 | CTG_FAIL_IN_FULL
G3 | 3335.49 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2698.37 | -2698.18 | 3245.26 | 3335.39 | -2136.63 | CTG_FAIL_IN_FULL
G4 | 3359.96 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2713.44 | -2712.36 | 3174.32 | 3359.8 | -2138.61 | CTG_FAIL_IN_FULL
G5 | 3371.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2707.29 | -2707.78 | 3186.93 | 3373.01 | -2119.5 | CTG_FAIL_IN_FULL
G6 | 3492.5 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2710.19 | -2708.38 | 3241.13 | 3492.38 | -2134.76 | CTG_FAIL_IN_FULL
G7 | 3509.59 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2705.29 | -2705.67 | 3172.08 | 3511.03 | -2112.9 | CTG_FAIL_IN_FULL
G8 | 3533.47 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2716.11 | -2715.01 | 3183.54 | 3534.38 | -2110.62 | CTG_FAIL_IN_FULL
G9 | 2866.31 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -11.23 | -482.61 | -482.95 | 3201.14 | 2866.14 | -1580.56 | FULL
G10 | 2816.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -11.23 | -482.05 | -482.08 | 3129.89 | 2815.96 | -1524.39 | FULL
G11 | 2768.51 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | -11.23 | -480.44 | -480.4 | 3140.76 | 2769.39 | -1471.85 | FULL
G12 | 645.36 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -456.25 | -456.23 | 3164.65 | 644.3 | -161.56 | FULL
G13 | 554.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -456.27 | -456.26 | 3098.67 | 553.79 | -84.09 | FULL
G14 | 474.85 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -458.07 | -457.89 | 3115.37 | 475.31 | -12.96 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3199.75 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2620.39 | -2620.71 | 2569.51 | 3198.69 | -2076.09 | CTG_FAIL_IN_FULL
G1 | 3236.16 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2631.06 | -2631.46 | 2500.93 | 3237.5 | -2069.23 | CTG_FAIL_IN_FULL
G2 | 3251.02 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2630.83 | -2631.05 | 2514.46 | 3250.24 | -2055.93 | CTG_FAIL_IN_FULL
G3 | 3277.98 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2624.28 | -2622.55 | 2567.55 | 3277.85 | -2066.32 | CTG_FAIL_IN_FULL
G4 | 3314.99 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2637.45 | -2637.89 | 2499.43 | 3316.51 | -2064.1 | CTG_FAIL_IN_FULL
G5 | 3322.79 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2628.12 | -2628.62 | 2512.92 | 3324.59 | -2042.3 | CTG_FAIL_IN_FULL
G6 | 3398.17 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.18 | 132.9 | 132.91 | 2564.13 | 3397.74 | -2028.36 | CTG_FAIL_IN_FULL
G7 | 3162.76 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 3.25 | 125.67 | 125.73 | 2487.18 | 3162.52 | -1868.94 | FULL
G8 | 3133.89 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4519 Cust-Mon #1 500kV & Mon Caps | 3.25 | 125.97 | 125.92 | 2497.55 | 3133.74 | -1829.32 | FULL
G9 | 2364.01 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | 3TM: Murr - Cust - Sedro 230kV | -8.57 | -458.35 | -458.5 | 2515.89 | 2363.12 | -1246.9 | FULL
G10 | 2259.12 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | 3TM: Murr - Cust - Sedro 230kV | -8.57 | -456.58 | -456.67 | 2445.25 | 2258.05 | -1160.16 | FULL
G11 | 2150.67 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | -8.57 | -454.62 | -454.77 | 2457.66 | 2150.94 | -1072.31 | FULL
G12 | -307.02 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -451.89 | -451.81 | 2508.97 | -304.58 | 416.35 | FULL
G13 | -381.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -452.77 | -452.7 | 2445.64 | -380.79 | 485.2 | FULL
G14 | -450.68 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -454.72 | -454.61 | 2464.85 | -451.75 | 550.81 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 3121.36 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2540.2 | -2540.33 | 2328.5 | 3121.03 | -2000.49 | CTG_FAIL_IN_FULL
G1 | 3141.44 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2537.63 | -2537.85 | 2259.95 | 3140.67 | -1980.53 | CTG_FAIL_IN_FULL
G2 | 3151.88 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -68.34 | -2535.03 | -2535.25 | 2273.16 | 3151.11 | -1964.77 | CTG_FAIL_IN_FULL
G3 | 2934.63 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2323.59 | -2322.56 | 2319.97 | 2933.76 | -1837.44 | FULL
G4 | 2955.58 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2331.91 | -2333.28 | 2252.23 | 2954.66 | -1825.03 | FULL
G5 | 2996.4 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | N-1: Monroe - Custer #1 500kV | -71.01 | -2332.89 | -2331.08 | 2266.61 | 2995.38 | -1821.74 | FULL
G6 | 2868.25 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 122.69 | 122.74 | 2309.89 | 2868.52 | -1696.39 | FULL
G7 | 2844.48 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 123.19 | 123.14 | 2238.97 | 2845.38 | -1659.95 | FULL
G8 | 2816.68 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 123.49 | 123.41 | 2251.21 | 2817.55 | -1616.82 | FULL
G9 | 1157.63 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -415.44 | -415.4 | 2262.44 | 1156.4 | -524.46 | FULL
G10 | 985.39 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -410.64 | -410.59 | 2194.54 | 984.1 | -397.7 | FULL
G11 | 899.87 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -411.34 | -411.3 | 2210.11 | 900.03 | -324.14 | FULL
G12 | -1430.18 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -426.55 | -426.46 | 2304.6 | -1430.01 | 1072.64 | FULL
G13 | -1489.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -429.06 | -428.91 | 2243.71 | -1489.34 | 1131.27 | FULL
G14 | -1537.25 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -429.88 | -429.79 | 2264.65 | -1537.75 | 1173.83 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2651.25 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2215.91 | -2214.84 | 2848.02 | 2651.14 | -1755.83 | FULL
G1 | 2663.22 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2216.6 | -2215.03 | 2778.24 | 2663.11 | -1737.97 | FULL
G2 | 2662.17 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2210.46 | -2211.68 | 2790.63 | 2662.09 | -1720.29 | FULL
G3 | 2720.45 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2209.04 | -2210.48 | 2845.99 | 2720.33 | -1749.67 | FULL
G4 | 2752.85 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2232.11 | -2233.16 | 2776.23 | 2752.72 | -1746.52 | FULL
G5 | 2757.91 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2222.94 | -2224.33 | 2789.61 | 2757.79 | -1717.24 | FULL
G6 | 2813.19 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 114.84 | 114.88 | 2840.29 | 2814.21 | -1695.45 | FULL
G7 | 2739.83 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 114.87 | 114.91 | 2768.57 | 2740.99 | -1633.66 | FULL
G8 | 2717.15 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 115.19 | 115.14 | 2780.02 | 2716.42 | -1593.75 | FULL
G9 | 1801.37 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -420.28 | -420.32 | 2802.62 | 1800.19 | -929.14 | FULL
G10 | 1681.53 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -417.85 | -417.72 | 2733.28 | 1680.37 | -830.49 | FULL
G11 | 1575.26 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -417.18 | -417 | 2746.24 | 1574.33 | -743.76 | FULL
G12 | -912.14 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -424.27 | -424.32 | 2818.28 | -911.91 | 750.44 | FULL
G13 | -970.35 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -426.91 | -426.97 | 2755.57 | -969.75 | 801.91 | FULL
G14 | -1036.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -427.36 | -427.42 | 2774.98 | -1037.57 | 865.48 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow Custer - Ingledow SN (201) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2518.66 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | -71.01 | -2101.16 | -2102.95 | 3197.74 | 2518.64 | -1692.16 | FULL
G1 | 2532.39 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | -71.01 | -2095.8 | -2093.94 | 3127.89 | 2532.31 | -1672.07 | FULL
G2 | 2541.29 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | -71.01 | -2098.72 | -2097.01 | 3140.31 | 2542.02 | -1648.68 | FULL
G3 | 2618.57 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2163.94 | -2165.15 | 3195.85 | 2618.54 | -1690.88 | FULL
G4 | 2614.3 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4272 Cust-Ing #1 & Mon-Cust #1 500kV | -71.01 | -2096.74 | -2095.78 | 3127.02 | 2614.15 | -1663.65 | FULL
G5 | 2627.11 | Branch CUST MON2 (95010) TO MONROE2 (95013) CKT 2 [500.00 - 500.00 kV] | BFR: 4268 Mon-Cust #1 500kV & Cust 500/230kV Bk#1 | -72.2 | -2143.14 | -2144.45 | 3139.99 | 2627.03 | -1645.86 | FULL
G6 | 2702.3 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 109.5 | 109.46 | 3192.3 | 2702.04 | -1638.19 | FULL
G7 | 2669.58 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 109.8 | 109.77 | 3120.17 | 2669.09 | -1594.34 | FULL
G8 | 2603.63 | Branch CAROLINA (42060) TO ENTRPRIS (42063) CKT 1 [115.00 - 115.00 kV] | BFR: 4526 Monroe-EchoLK-SnoK 500 kV #1 & Mon-Cust #2 500kV | 3.41 | 110.05 | 110.12 | 3130.5 | 2603.12 | -1526.47 | FULL
G9 | 1894.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -419.37 | -419.28 | 3160.81 | 1894.53 | -985.32 | FULL
G10 | 1772.45 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -417.24 | -417.1 | 3090.27 | 1769.81 | -887.68 | FULL
G11 | 1676.57 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -417.15 | -416.99 | 3102.88 | 1673.86 | -806.93 | FULL
G12 | -803.92 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -424.66 | -424.51 | 3171.26 | -803.82 | 688.28 | FULL
G13 | -872.24 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -426.74 | -426.78 | 3107.88 | -872 | 744.64 | FULL
G14 | -941.88 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -6.08 | -427.12 | -427.16 | 3126.64 | -941.28 | 808.22 | FULL
001R2WINTER09v5SNL