## 25F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 023
Temp: |  | 25F
|  |  | Average Puget Sound Net Area Load = | 3335.0307
Gen Level |  | Trans | Worst | Limiting |  |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [6 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2503.18 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  |  | G3 | 100 | 775 | 2641.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
100 | 460 | 2584.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G6 | 260 | 775 | 2461.49 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2641.23 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  |  | G9 | 525 | 775 | 2174.73 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2862.71 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  |  | G12 | 1000 | 775 | 1496.66 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2835.9 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G15 | 1400 | 775 | 1054.83 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 2461.49 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G2 | 100 | 465 | 2584.29 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
525 | 140 | 2592.9 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  |  | G5 | 260 | 460 | 2835.9 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2551.59 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G8 | 525 | 460 | 2551.59 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 2174.73 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G11 | 1000 | 460 | 2016.06 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 2120.9 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  |  | G14 | 1400 | 460 | 1561.03 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 2016.06 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G1 | 100 | 140 | 2503.18 | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1496.66 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G4 | 260 | 140 | 2862.71 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1667.44 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  |  | G7 | 525 | 140 | 2592.9 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1561.03 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G10 | 1000 | 140 | 2120.9 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 1054.83 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  |  | G13 | 1400 | 140 | 1667.44 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450
G1
789

## 35F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 023
Temp: |  | 35F
|  |  | Average Puget Sound Net Area Load = | 2657.7473
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2823.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] |  |  | G3 | 100 | 775 | 2353.53 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2831.33 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2162.85 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2353.53 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1877.97 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2787.05 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1358.98 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2651.19 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 905.04 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 2162.85 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2831.33 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2514.96 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2651.19 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2342.61 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2342.61 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1877.97 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1850.69 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 2043.86 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1296.46 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1850.69 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2823.36 | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV]
1000 | 775 | 1358.98 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2787.05 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV]
1400 | 140 | 1539.93 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2514.96 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1296.46 | N-1: Bothell - SnoKing #1 230kV | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 2043.86 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 905.04 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1539.93 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 45F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 023
Temp: |  | 45F
|  |  | Average Puget Sound Net Area Load = | 2413.8927
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2767.04 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2153.7 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2635.05 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1957.09 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2153.7 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1667.19 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2684.95 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1163.16 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2456.75 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 712.03 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1957.09 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2635.05 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 140 | 2389.71 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2456.75 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 460 | 2168 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2168 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1667.19 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1650.58 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1895.19 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1198.73 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1650.58 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2767.04 | N-1: Chief Joe - Monroe #1 500kV | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1163.16 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2684.95 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1371.44 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2389.71 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1198.73 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1895.19 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 712.03 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1371.44 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 60F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 023
Temp: |  | 60F
|  |  | Average Puget Sound Net Area Load = | 2932.7307
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2482.81 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2190.08 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2582.98 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 2016.88 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2190.08 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1706.84 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2431.09 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1201.52 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2505.82 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 744.43 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 2016.88 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 460 | 2582.98 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 2210.7 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2505.82 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2190.11 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2190.11 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
525 | 775 | 1706.84 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1672.64 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1737.87 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1106.96 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1672.64 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2482.81 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1201.52 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2431.09 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1235.22 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 2210.7 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1106.96 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1737.87 | BFR: Snohomish 230kV Bus Sect #4 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 744.43 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1235.22 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## 70F nomo
Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
WINTER 2009
North-to-South (NS)
Light Loads
Outage: |  | 023
Temp: |  | 70F
|  |  | Average Puget Sound Net Area Load = | 3278.3167
Gen Level |  | Trans | Worst | Limiting |  |  | Gen | PSE | SCL | Transfer | Worst | Limiting
PSE | SCL/ | Limit | Contingency | Facility
| SNOH | [5 empty] | # | Gen | Gen | Limit | Contingency | Facility
100 | 140 | 2152.14 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G3 | 100 | 775 | 2154.12 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 460 | 2260.39 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G6 | 260 | 775 | 1843.48 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
100 | 775 | 2154.12 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G9 | 525 | 775 | 1678.99 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 140 | 2091.16 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G12 | 1000 | 775 | 1035.37 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 460 | 2180.24 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G15 | 1400 | 775 | 576.82 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
260 | 775 | 1843.48 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G2 | 100 | 465 | 2260.39 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 140 | 1875.51 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G5 | 260 | 460 | 2180.24 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 460 | 2001.92 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] |  |  | G8 | 525 | 460 | 2001.92 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
525 | 775 | 1678.99 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G11 | 1000 | 460 | 1502.19 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 140 | 1535.47 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G14 | 1400 | 460 | 1069.75 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV]
1000 | 460 | 1502.19 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G1 | 100 | 140 | 2152.14 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1000 | 775 | 1035.37 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G4 | 260 | 140 | 2091.16 | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 140 | 1051 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] |  |  | G7 | 525 | 140 | 1875.51 | 3TM: Mon - Snoh - Horse Rnch 230kV | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV]
1400 | 460 | 1069.75 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G10 | 1000 | 140 | 1535.47 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
1400 | 775 | 576.82 | BFR: Bothell 230kV Bus Sect #3 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] |  |  | G13 | 1400 | 140 | 1051 | N-2: Snohomish - Bothell #1&2 230kV | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV]
[5 empty] | 2850 | 0
[5 empty] | 2850 | 1450

## Results
| 25F | 35F | 45F | 60F | 70F | Description: | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
G0 | 2503.18 | 2823.36 | 2767.04 | 2482.81 | 2152.14
G1 | 2584.29 | 2831.33 | 2635.05 | 2582.98 | 2260.39 | Season/Year: | WINTER 2009
G2 | 2641.23 | 2353.53 | 2153.7 | 2190.08 | 2154.12 | Direction: | North-to-South (NS)
G3 | 2862.71 | 2787.05 | 2684.95 | 2431.09 | 2091.16 | Case Loads: | Light Loads
G4 | 2835.9 | 2651.19 | 2456.75 | 2505.82 | 2180.24 | Outage: | 023
G5 | 2461.49 | 2162.85 | 1957.09 | 2016.88 | 1843.48 | Power World: | 13.0 (*.exe Date: 08/18/08)
G6 | 2592.9 | 2514.96 | 2389.71 | 2210.7 | 1875.51 | File Location: | RS4F01\Wrkgrp\Tot\Northern Intertie\Archives\2009\WINTER_2009
G7 | 2551.59 | 2342.61 | 2168 | 2190.11 | 2001.92 | Study Person: | FRP9899
G8 | 2174.73 | 1877.97 | 1667.19 | 1706.84 | 1678.99 | Source: | 023WINTER09v1NSL
G9 | 2120.9 | 2043.86 | 1895.19 | 1737.87 | 1535.47
G10 | 2016.06 | 1850.69 | 1650.58 | 1672.64 | 1502.19
G11 | 1496.66 | 1358.98 | 1163.16 | 1201.52 | 1035.37
G12 | 1667.44 | 1539.93 | 1371.44 | 1235.22 | 1051
G13 | 1561.03 | 1296.46 | 1198.73 | 1106.96 | 1069.75
G14 | 1054.83 | 905.04 | 712.03 | 744.43 | 576.82
*Note: The presence of a "red" box indicates a further examination in Powerworld is required
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL
| FULL | FULL | FULL | FULL | FULL

## Pink Table
North-to-South (NS) |  |  |  | Light Loads |  |  | 023 | Echo Lake-Monroe-Sno-King #1 500kV Line (COV-CRES BYP @ COV)
PSE Gen | LOAD | 100 | 100 | 100 | 260 | 260 | 260 | 525 | 525 | 525 | 1000 | 1000 | 1000 | 1400 | 1400 | 1400
SCL Gen |  | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775 | 140 | 460 | 775
25F | 3335.0307 | 2503.18 | 2584.29 | 2641.23 | 2862.71 | 2835.9 | 2461.49 | 2592.9 | 2551.59 | 2174.73 | 2120.9 | 2016.06 | 1496.66 | 1667.44 | 1561.03 | 1054.83
35F | 2657.7473 | 2823.36 | 2831.33 | 2353.53 | 2787.05 | 2651.19 | 2162.85 | 2514.96 | 2342.61 | 1877.97 | 2043.86 | 1850.69 | 1358.98 | 1539.93 | 1296.46 | 905.04
45F | 2413.8927 | 2767.04 | 2635.05 | 2153.7 | 2684.95 | 2456.75 | 1957.09 | 2389.71 | 2168 | 1667.19 | 1895.19 | 1650.58 | 1163.16 | 1371.44 | 1198.73 | 712.03
60F | 2932.7307 | 2482.81 | 2582.98 | 2190.08 | 2431.09 | 2505.82 | 2016.88 | 2210.7 | 2190.11 | 1706.84 | 1737.87 | 1672.64 | 1201.52 | 1235.22 | 1106.96 | 744.43
70F | 3278.3167 | 2152.14 | 2260.39 | 2154.12 | 2091.16 | 2180.24 | 1843.48 | 1875.51 | 2001.92 | 1678.99 | 1535.47 | 1502.19 | 1035.37 | 1051 | 1069.75 | 576.82

## Excel Sheet
Interface Scenario I0
25F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2511.76 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | N-2: Murr - Cust #1 & Sedro W - Belling #1 230kV | -19.29 | -507.02 | -506.71 | 3352.06 | 2503.18 | 0 | FULL
G1 | 2594.03 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 490.58 | 490.68 | 3293.43 | 2584.29 | 0 | FULL
G2 | 2651.34 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 491.42 | 491.6 | 3314.25 | 2641.23 | 0 | FULL
G3 | 2874.8 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -757.49 | -757.93 | 3377.59 | 2862.71 | 0 | FULL
G4 | 2848.09 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 529.16 | 529.06 | 3315.64 | 2835.9 | 0 | FULL
G5 | 2470.13 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 543.83 | 543.96 | 3312.51 | 2461.49 | 0 | FULL
G6 | 2602.71 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -757.78 | -757.83 | 3378.78 | 2592.9 | 0 | FULL
G7 | 2561.53 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 531.01 | 530.93 | 3316 | 2551.59 | 0 | FULL
G8 | 2180.56 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 544.42 | 544.51 | 3313.15 | 2174.73 | 0 | FULL
G9 | 2127.27 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -761.17 | -761.3 | 3387.02 | 2120.9 | 0 | FULL
G10 | 2021.42 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 527.73 | 528.18 | 3320.46 | 2016.06 | 0 | FULL
G11 | 1499.33 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 519.17 | 519.08 | 3314.31 | 1496.66 | 0 | FULL
G12 | 1670.27 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -762.5 | -762.45 | 3389.48 | 1667.44 | 0 | FULL
G13 | 1563.61 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 528.17 | 528.14 | 3322.88 | 1561.03 | 0 | FULL
G14 | 1054.74 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 522.33 | 522.4 | 3317.9 | 1054.83 | 0 | FULL
35F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2835.2 | Branch CUST PW (95003) TO PORTALWY (42001) CKT 1 [230.00 - 115.00 kV] | N-2: Murr - Cust #1 & Belling - Cust #1 230kV | 12.72 | 482.09 | 482.31 | 2694.63 | 2823.36 | 0 | FULL
G1 | 2842.34 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 536.83 | 536.9 | 2634.03 | 2831.33 | 0 | FULL
G2 | 2361.77 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 531.85 | 532.03 | 2629.39 | 2353.53 | 0 | FULL
G3 | 2797.98 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 2 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -22.39 | -473.15 | -472.81 | 2701.21 | 2787.05 | 0 | FULL
G4 | 2661.35 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 536.7 | 536.84 | 2631.21 | 2651.19 | 0 | FULL
G5 | 2169.7 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 529.32 | 529.48 | 2627.39 | 2162.85 | 0 | FULL
G6 | 2524.08 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -736.15 | -736.27 | 2703.35 | 2514.96 | 0 | FULL
G7 | 2350.46 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 532.48 | 532.5 | 2632.84 | 2342.61 | 0 | FULL
G8 | 1882.97 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 531.05 | 531.22 | 2628.59 | 1877.97 | 0 | FULL
G9 | 2048.7 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -744.09 | -744.11 | 2712.01 | 2043.86 | 0 | FULL
G10 | 1854.73 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 531.48 | 531.41 | 2639.97 | 1850.69 | 0 | FULL
G11 | 1360.75 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 530.41 | 530.6 | 2636.06 | 1358.98 | 0 | FULL
G12 | 1541.74 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -740.41 | -740.46 | 2713.17 | 1539.93 | 0 | FULL
G13 | 1297.95 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | N-1: Bothell - SnoKing #1 230kV | 18.35 | 516.43 | 516.41 | 2640.61 | 1296.46 | 0 | FULL
G14 | 905.19 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 530.17 | 530.55 | 2641.75 | 905.04 | 0 | FULL
45F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2777.82 | Branch HRTAP MS (40963) TO MONROE T (40751) CKT 1 [230.00 - 230.00 kV] | N-1: Chief Joe - Monroe #1 500kV | -22.39 | -462.58 | -462.37 | 2455.56 | 2767.04 | 0 | FULL
G1 | 2644.75 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 523.17 | 523.16 | 2386.62 | 2635.05 | 0 | FULL
G2 | 2159.53 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 518.52 | 518.72 | 2383.5 | 2153.7 | 0 | FULL
G3 | 2695.14 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -722.29 | -722.37 | 2459.28 | 2684.95 | 0 | FULL
G4 | 2464.97 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 518.27 | 518.39 | 2385.22 | 2456.75 | 0 | FULL
G5 | 1962.77 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 517.31 | 517.21 | 2381.53 | 1957.09 | 0 | FULL
G6 | 2397.94 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -717.19 | -717.28 | 2460.84 | 2389.71 | 0 | FULL
G7 | 2174.14 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 517.46 | 517.57 | 2386.98 | 2168 | 0 | FULL
G8 | 1670.35 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 518.46 | 518.67 | 2383.05 | 1667.19 | 0 | FULL
G9 | 1899.1 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -718.23 | -718.21 | 2469.2 | 1895.19 | 0 | FULL
G10 | 1652.98 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 518.41 | 518.64 | 2394.69 | 1650.58 | 0 | FULL
G11 | 1164.5 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 517.88 | 518.03 | 2392.34 | 1163.16 | 0 | FULL
G12 | 1372.85 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -715.91 | -715.94 | 2471.03 | 1371.44 | 0 | FULL
G13 | 1199.19 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 517.86 | 517.77 | 2400 | 1198.73 | 0 | FULL
G14 | 710.19 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 518.22 | 518.11 | 2398.55 | 712.03 | 0 | FULL
60F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2491.74 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.59 | 542.43 | 542.66 | 2964.93 | 2482.81 | 0 | FULL
G1 | 2591.89 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 551.59 | 551.57 | 2906.61 | 2582.98 | 0 | FULL
G2 | 2196.2 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 492.23 | 492.26 | 2907.68 | 2190.08 | 0 | FULL
G3 | 2439.58 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 543.59 | 543.52 | 2968.4 | 2431.09 | 0 | FULL
G4 | 2515.01 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 542.58 | 542.9 | 2909.72 | 2505.82 | 0 | FULL
G5 | 2022.44 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 494.78 | 494.94 | 2905.83 | 2016.88 | 0 | FULL
G6 | 2217.21 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -685.49 | -685.45 | 2973.3 | 2210.7 | 0 | FULL
G7 | 2196.18 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 495.56 | 495.77 | 2910.07 | 2190.11 | 0 | FULL
G8 | 1710.85 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 493.33 | 493.52 | 2907.14 | 1706.84 | 0 | FULL
G9 | 1740.97 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | BFR: Snohomish 230kV Bus Sect #4 | -26.83 | -689.09 | -689.18 | 2982.2 | 1737.87 | 0 | FULL
G10 | 1675.59 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 493.53 | 493.52 | 2917.2 | 1672.64 | 0 | FULL
G11 | 1202.79 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 492.15 | 492.24 | 2914.93 | 1201.52 | 0 | FULL
G12 | 1237.16 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -684.81 | -684.69 | 2984.88 | 1235.22 | 0 | FULL
G13 | 1108.08 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 475.82 | 476.37 | 2917.17 | 1106.96 | 0 | FULL
G14 | 744.28 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 493.48 | 493.53 | 2920.9 | 744.43 | 0 | FULL
70F | Trans Lim | Limiting Element | Limiting CTG | % OTDF | Pre-Trans Est | Limit Used | ATC Mon: MW flow Puget Sound Area Net Load (207) | ATC Mon: MW flow CUSTER - INGLEDOW NS (200) | ATC Mon: MW flow Monroe-Echo Lake (@ Monroe) (208) | Iteratively Found
G0 | 2158.43 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 503.37 | 503.55 | 3305.24 | 2152.14 | 0 | FULL
G1 | 2267.43 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 503 | 503.17 | 3245.45 | 2260.39 | 0 | FULL
G2 | 2160.01 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 474.89 | 474.9 | 3260.31 | 2154.12 | 0 | FULL
G3 | 2097.12 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | BFR: A178 or A182 Snoh Bus Sect#4 & Mon-Snoh-HRanch 230kV | 18.59 | 503.69 | 503.94 | 3308.42 | 2091.16 | 0 | FULL
G4 | 2185.55 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 503.31 | 503.28 | 3247.85 | 2180.24 | 0 | FULL
G5 | 1848.51 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 456.31 | 456.4 | 3254.56 | 1843.48 | 0 | FULL
G6 | 1878.85 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 509.35 | 509.59 | 3312.9 | 1875.51 | 0 | FULL
G7 | 2007.17 | Branch MONROE (40747) TO NOVELTY (42304) CKT 1 [230.00 - 230.00 kV] | 3TM: Mon - Snoh - Horse Rnch 230kV | 18.59 | 502.4 | 502.64 | 3254.4 | 2001.92 | 0 | FULL
G8 | 1683.14 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 474.53 | 474.48 | 3259.85 | 1678.99 | 0 | FULL
G9 | 1537.83 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -663.01 | -662.65 | 3328.25 | 1535.47 | 0 | FULL
G10 | 1504.03 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 453.16 | 453.08 | 3265.07 | 1502.19 | 0 | FULL
G11 | 1036.95 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 456.78 | 456.77 | 3263.1 | 1035.37 | 0 | FULL
G12 | 1052.03 | Branch BOTHELL (46403) TO HRNCHTAP (42321) CKT 1 [230.00 - 230.00 kV] | N-2: Snohomish - Bothell #1&2 230kV | -23.03 | -664.15 | -663.85 | 3331.38 | 1051 | 0 | FULL
G13 | 1070.96 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 457.91 | 457.9 | 3269.09 | 1069.75 | 0 | FULL
G14 | 576.82 | Branch BOTHELL (46403) TO SNOK S3 (41008) CKT 2 [230.00 - 230.00 kV] | BFR: Bothell 230kV Bus Sect #3 | 18.45 | 457.03 | 457.5 | 3268.88 | 576.82 | 0 | FULL
023WINTER09v1NSL