## Drop-Down
IMPORTANT NOTE: Input/select information into cells that have a blue color font. Cells with black color fonts are calculated cells.
Expanded Standard Offer+ (ESO+) Program Drop-Down Wattage Reduction Tool - Updated April 19, 2005
| Project Name: | Alvey substation | [5 empty] | Servicing Utility: | NW Public Power
| Project Number: | [6 empty] | Utility Representative: | Manie Hats
| Customer: | BPA Transmission Business Line | [5 empty] | Energy Rate ($/kWh) & $savings/yr: | 0.045 |  | 4779.2205
| Address: | [6 empty] | Demand Rate ($/kW) & $savings/yr: | 2.5 |  | 1194.09
| Contact Name: | Jim Domschot Resource Mangement Spec. | [5 empty] | Audit Prepared By: | Nelly leap
| Phone: | (541) 465 - 6992 | [5 empty] | Phone Number(s): | 503-230-5865
[8 empty] | Date (fills in automatically): | 2005-07-12 15:03
Summary Table >> |  | Total Existing Watts | Total Proposed Watts |  |  |  |  | Annual kWh Savings | Average Annual Hours |  |  |  | Total Watt Reduction
|  | 60173 | 20370 |  |  |  |  | 106204.9 | 2668.2637 |  |  |  | 66.15%
Projet Cost = (493 fixtures*$40) = $19,720
|  | Existing Lamp/Ballast Combination | [5 empty] | Proposed Lamp/Ballast Combination | [5 empty] | Watt Reduction | Change in Light Level
Location | Annual Operating Hours | Existing Lamp/Ballast | Q'ty | Watts Each | Mean Lumens Each | Total Watts | Select Proposed Lamp/Ballast | Proposed Lamp/Ballast | Q'ty | Watts Each | Mean Lumens Each | Total Watts | Annual kWh Savings |  |  | Proposed kWh
[7 empty] | #N/A |  | 0 | [7 empty] | LINE, LINE, LINE
Control House
Control room | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 48 | 192 | 7301.7 | 9216 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 48 | 73 | 6891.3 | 3504 | 14280 | 61.98% | -5.621%
Entry/Office | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 3 | 96 | 4867.8 | 288 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-2P32-LW-SC | 3 | 48 | 4594.2 | 144 | 360 | 50% | -5.621%
Comm Room | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 10 | 96 | 4867.8 | 960 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 10 | 66 | 6125.6 | 660 | 750 | 31.25% | 25.84% | 1650 | LINE, LINE, LINE
Battery Room | 2500 | Incandescent, 3-A 100W, no ballast | 8 | 192 | 4644 | 1536 | Hard-Wired CFL, 2-2D 38W, 1-Elec | Screw-In CFL, 1-85W spiral, 1-Mag | 8 | 85 | 4675 | 680 | 2140 | 55.73% | 0.6675% | 1700 | LINE, LINE, LINE
MW Office | 2500 | Incandescent, 1-A 100W, no ballast | 1 | 100 | 1548 | 100 | Hard-Wired CFL, 1-PL 26W, 1-Mag | Screw-In CFL, 1-27W spiral, 1-Mag | 1 | 27 | 1488 | 27 | 182.5 | 73% | -3.876% | 67.5 | LINE, LINE, LINE
Hall/Misc | 2500 | Incandescent, 1-A 100W, no ballast | 11 | 100 | 1548 | 1100 | Hard-Wired CFL, 1-PL 26W, 1-Mag | Screw-In CFL, 1-27W spiral, 1-Mag | 11 | 27 | 1488 | 297 | 2007.5 | 73% | -3.876% | 742.5 | LINE, LINE, LINE
| 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 8 | 96 | 4867.8 | 768 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-2P32-LW-SC | 8 | 48 | 4594.2 | 384 | 960 | 50% | -5.621% | 960 | LINE, LINE, LINE
Basement | 2500 | Incandescent, 1-A 100W, no ballast | 70 | 100 | 1548 | 7000 | Hard-Wired CFL, 1-PL 26W, 1-Mag | Screw-In CFL, 1-27W spiral, 1-Mag | 70 | 27 | 1488 | 1890 | 12775 | 73% | -3.876% | 4725 | LINE, LINE, LINE
| 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 24 | 96 | 4867.8 | 2304 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-2P32-LW-SC | 24 | 48 | 4594.2 | 1152 | 2880 | 50% | -5.621% | 2880 | LINE, LINE, LINE
Yard Lighting | 8760 | Incandescent, 2-A 150W, no ballast | 6 | 300 | 5073 | 1800 | Hard-Wired CFL, 2-2D 38W, 1-Elec | Screw-In CFL, 1-85W spiral, 1-Mag | 6 | 85 | 4675 | 510 | 11300.4 | 71.67% | -7.845% | 4467.6 | LINE, LINE, LINE
Maint. HQ
Raedy Room | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 5 | 126 | 7301.7 | 630 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 5 | 73 | 6891.3 | 365 | 662.5 | 42.06% | -5.621% | 912.5 | LINE, LINE, LINE
Parts/toilet | 2500 | T12 8' Fluorescent, 2-F96T12 75W, 1-Mag | 27 | 173 | 10290.18 | 4671 | T8 Fluorescent, 4-F32T8 32W, 1-Elec | T8HP 8', 2-F96T8, 5900+lumens Alto+, 1-Universal/GE B259I277HE | 27 | 108 | 9864.8 | 2916 | 4387.5 | 37.57% | -4.134% | 7290
| 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 12 | 96 | 4867.8 | 1152 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 12 | 66 | 6125.6 | 792 | 900 | 31.25% | 25.84% | 1980
Linemens Room | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 6 | 126 | 7301.7 | 756 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 6 | 73 | 6891.3 | 438 | 795 | 42.06% | -5.621% | 1095
Hallway | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 11 | 96 | 4867.8 | 1056 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 11 | 66 | 6125.6 | 726 | 825 | 31.25% | 25.84% | 1815
Office | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 4 | 96 | 4867.8 | 384 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 4 | 66 | 6125.6 | 264 | 300 | 31.25% | 25.84% | 660
Training room | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 8 | 126 | 7301.7 | 1008 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 8 | 73 | 6891.3 | 584 | 1060 | 42.06% | -5.621% | 1460
Sub. Maint | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 10 | 96 | 4867.8 | 960 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-2P32-HL-SC | 10 | 48 | 7068 | 480 | 1200 | 50% | 45.2% | 1200
PSC Office | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 18 | 126 | 7301.7 | 2268 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 18 | 73 | 6891.3 | 1314 | 2385 | 42.06% | -5.621% | 3285
SPM Office | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 12 | 126 | 7301.7 | 1512 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 12 | 73 | 6891.3 | 876 | 1590 | 42.06% | -5.621%
District Office | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 12 | 126 | 7301.7 | 1512 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 12 | 73 | 6891.3 | 876 | 1590 | 42.06% | -5.621%
Storage | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 6 | 96 | 4867.8 | 576 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 6 | 66 | 6125.6 | 396 | 450 | 31.25% | 25.84%
PSC Shop | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 15 | 126 | 7301.7 | 1890 |  | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 15 | 73 | 6891.3 | 1095 | 1987.5 | 42.06% | -5.621%
Break Room | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 6 | 126 | 7301.7 | 756 |  | T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 6 | 73 | 6891.3 |  | 994 |  | -5.621%
S-W Shop | 2500 | T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 15 | 126 | 7301.7 | 1890 |  | T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-4P32-SC | 15 | 89 | 8128.2 |  | 1988 |  | 11.32%
N Garage | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 24 | 96 | 4867.8 | 2304 |  | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 24 | 66 | 6125.6 |  | 3000 |  | 25.84%
S Garage | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 16 | 96 | 4867.8 | 1536 |  | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 16 | 66 | 6125.6 |  | 2000 |  | 25.84%
Shop | 2500 | Metal Halide, 250W, 1-Std Mag | 32 | 295 | 11300 | 9440 |  | T8 Standard Electronic, 2-F96T8HO 86W, 1-Elec | 32 | 155 | 12693.6 |  | 11200 |  | 12.33%
Substation Buiding | 8760 | Exit Sign, 2-Inc 20W, no ballast | 20 | 40 | 2 | 800 |  | New Exit Sign, 1 face LED, 1.5W, no ballast | 20 | 1.5 | 2 |  | 6657 |  | 0%
Garage/Shop
Office | 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 6 | 96 | 4867.8 |  |  | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 6 | 66 | 6125.6 |  | 450 |  | 25.84%
Garage | 2500 | Mercury Vapor, 250W, 1-Std Mag | 12 | 285 | 10700 |  |  | Hard-Wired CFL, 1-bi-ax 85W, 1-Mag | 12 | 82 | 4207.5 |  | 6000 |  | -60.68%
| 2500 | T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 8 | 96 | 4867.8 |  |  | T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 8 | 66 | 6125.6 |  | 600 |  | 25.84%
| 2500 | T12 8' Fluorescent, 2-F96T12 75W, 1-Mag | 8 | 173 | 10290.18 |  |  | T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-Elec RLO | 8 | 55 | 4371.9 |  | 2360 |  | -57.51%
| 2500 | T12 8' Fluorescent, 4-F96T12ES 60W, 2-Mag | 2 | 276 | 17034.6 |  |  | T8HP 8', 2-F96T8, 6100+lumens, 1-Advance Centium RCN/VCN-2P59 | 2 | 110 | 10199.2 |  | 830 |  | -40.13%
Exterior Lighting | 2500 | Metal Halide, 175W, 1-Std Mag | 5 | 210 | 9400 |  |  | Hard-Wired CFL, 1-bi-ax 85W, 1-Mag | 5 | 82 | 4207.5 |  | 1600 |  | -55.24%
| 2500 | T12 8' Fluorescent, 4-F96T12ES 60W, 2-Mag | 2 | 276 | 17034.6 |  |  | T8HP 8', 2-F96T8, 6100+lumens, 1-Advance Centium RCN/VCN-2P59 | 2 | 110 | 10199.2 |  | 830 |  | -40.13%
Parking Lot | 4000 | High Pressure Sodium, 250W, 1-Std Mag | 2 | 295 | 22550 |  |  | Hard-Wired CFL, 1-bi-ax 55W, 1-Mag | 2 | 54 | 2677.5 |  | 1928 |  | -88.13%
TOTAL FIXTURE COUNT |  |  | 493 |  |  |  | #N/A |  | 493 | [7 empty] | LINE, LINE, LINE
Note: When you add a row, Excel automatically protects this worksheet. To unprotect the worksheet; click on tools, protection, and unprotect sheet. There is no password. The best way to add rows is; 1) click the "Add A Row" button to add as many rows as you need, 2) unprotect the sheet, 3) copy and paste a row into the new empty rows. If you do it this way, you will copy all the fonts, and other formatting. If your computer has trouble with this procedure, just add rows like you normally would. Make sure you copy an existing row into the new rows. This will retain all the fonts and other formatting. P.S. the print area is set on this page so that this note box and the Add a Row button does not print. The print area is set on the other pages as well.
36890.1
Note on P15: Font is RED if Watt Reduction is NOT between 20 and 50%.
Note on Q15: Font is RED if Change in Light Level is NOT between -10% and +10%. Calculates total change in light output of lamp(s) only. Ignores luminaire efficiency.
Note on K16: Automatically copies the Existing Luminaires Q'ty unless user types in a changed value.
Note on G16: Mean lamp(s) light output per existing luminaire. Does not include luminaire efficiency. Drawn from the Data Existing tab of this workbook.
Note on E16: Quantity of existing luminaires. User input value.
Note on F16: Existing watts per luminaire. Drawn from the Data Existing tab of this workbook.
Note on D16: Automatically draws from the Data Existing tab of this workbook.
Note on C16: User calculated and input. Same value is used for proposed Annual Operating Hours.
Note on B16: Area of building, room number, location, office name, etc.. You can group exact same combos together if they have the same hours of operation.
Note on O13: Must be 30% or greater in order to receive a rebate. This value is automatically put into the Verification Report.
Note on J13: Total Project Annual kWh saved. This value is automatically put into the Verification Report.
Note on L16: Proposed watts per luminaire. Drawn from the Data Proposed tab of this workbook.
Note on M16: Mean lamp(s) light output per proposed luminaire. Does not include luminaire efficiency. Drawn from the Data Proposed tab of this workbook.
Note on O16: Spreadsheet automatically calculates this value.
Note on J16: Automatically draws from the Data Proposed tab of this workbook.
Note on K13: Weighted average
Note on E13: Calculated from column N of this worksheet. Column N is a hidden column.
Note on D13: Calculated from column H of this worksheet. Column H is a hidden column.
Note on M6: This cell automatically calculates the dollar savings per year associated with kWh energy savings.
Note on M7: This cell automatically calculates the dollar savings per year associated with kW or Demand savings.
Note on K6: This value is based on the most representative energy rate. Usually the highest block rate in the utilities rate structure. May have to average seasonal energy rates.
Note on K7: This value is based on the most representative utility demand rate. You may have to average seasonal demand rates.

## Data Existing
Updated April 19, 2005. This list is not meant to be complete, you can add equipment to this list.
Description of Existing Lamp/Ballast Combination | Input Watts | Mean System Lumens | Suggested Retrofits / Notes
Incandescent, 1-A 15W, no ballast | 15 | 95.45 | Screw-In CFL, 1-CF 9W, 1-Mag
Incandescent, 1-A 25W, no ballast | 25 | 169.85 | Screw-In CFL, 1-CF 9W, 1-Mag
Incandescent, 1-A 40W, no ballast | 40 | 402.5 | Screw-In CFL, 1-CF 9W, 1-Mag
Incandescent, 1-A 50W, no ballast | 50 | 428.75 | Screw-In CFL, 1-CF 11W, 1-Mag
Incandescent, 1-A 60W, no ballast | 60 | 799.8 | Screw-In CFL, 1-CF 15W, 1-Mag
Incandescent, 1-A 75W, no ballast | 75 | 1085.6 | Hard-Wired CFL, 1-PL 20W, 1-Mag
Incandescent, 1-A 100W, no ballast | 100 | 1548 | Hard-Wired CFL, 1-PL 26W, 1-Mag
Incandescent, 1-A 150W, no ballast | 150 | 2536.5 | Hard-Wired CFL, 2-PL 23W, 2-Mag
----------------------------
Incandescent, 2-A 15W, no ballast | 30 | 190.9 | Screw-In CFL, 1-CF 9W, 1-Mag
Incandescent, 2-A 25W, no ballast | 50 | 339.7 | Screw-In CFL, 1-CF 11W, 1-Mag
Incandescent, 2-A 40W, no ballast | 80 | 805 | Hard-Wired CFL, 1-PL 23W, 1-Mag
Incandescent, 2-A 50W, no ballast | 100 | 857.5 | Hard-Wired CFL, 1-PL 26W, 1-Mag
Incandescent, 2-A 60W, no ballast | 120 | 1599.6 | Hard-Wired CFL, 1-PL 32W, 1-Mag
Incandescent, 2-A 75W, no ballast | 150 | 2171.2 | Hard-Wired CFL, 2-PL 23W, 2-Mag
Incandescent, 2-A 100W, no ballast | 200 | 3096 | Hard-Wired CFL, 2-2D 28W, 1-Elec
Incandescent, 2-A 150W, no ballast | 300 | 5073 | Hard-Wired CFL, 2-2D 38W, 1-Elec
----------------------------
Incandescent, 3-A 15W, no ballast | 45 | 286.35 | Screw-In CFL, 1-CF 9W, 1-Mag
Incandescent, 3-A 25W, no ballast | 75 | 509.55 | Hard-Wired CFL, 1-PL 20W, 1-Mag
Incandescent, 3-A 40W, no ballast | 120 | 1207.5 | Hard-Wired CFL, 1-PL 32W, 1-Mag
Incandescent, 3-A 50W, no ballast | 150 | 1286.25 | Hard-Wired CFL, 2-PL 23W, 2-Mag
Incandescent, 3-A 60W, no ballast | 180 | 2399.4 | Hard-Wired CFL, 2-PL 23W, 2-Mag
Incandescent, 3-A 75W, no ballast | 225 | 3256.8 | Hard-Wired CFL, 2-2D 28W, 1-Elec
Incandescent, 3-A 100W, no ballast | 300 | 4644 | Hard-Wired CFL, 2-2D 38W, 1-Elec
----------------------------
Incandescent, 4-A 40W, no ballast | 160 | 1610 | Hard-Wired CFL, 2-2D 28W, 1-Elec
Incandescent, 4-A 60W, no ballast | 240 | 3199.2 | Hard-Wired CFL, 2-2D 28W, 1-Elec
Incandescent, 4-A 75W, no ballast | 300 | 4342.4 | Hard-Wired CFL, 2-2D 28W, 1-Elec
Incandescent, 4-A 100W, no ballast | 400 | 6192 | Hard-Wired CFL, 2-2D 28W, 1-Elec
----------------------------
Incandescent, 1-R 75W, no ballast | 75 | 801 | Hard-Wired CFL, 1-PL 20W, 1-Mag
Incandescent, 1-R 90W, no ballast | 90 | 1071 | Hard-Wired CFL, 1-PL 23W, 1-Mag
Incandescent, 1-R 100W, no ballast | 100 | 1071 | Hard-Wired CFL, 1-PL 26W, 1-Mag
Incandescent, 1-R 120W, no ballast | 120 | 1440 | Hard-Wired CFL, 1-PL 32W, 1-Mag
Incandescent, 1-R 150W, no ballast | 150 | 1710 | Ceramic Metal Halide, 1-PAR 39W, 1-Elec
----------------------------
Incandescent, 1-PAR 65W, no ballast | 65 | 607.5 | Screw-In CFL, 1-CF 15W, 1-Mag
Incandescent, 1-PAR 75W, no ballast | 75 | 688.5 | Hard-Wired CFL, 1-PL 20W, 1-Mag
Incandescent, 1-PAR 85W, no ballast | 85 | 837 | Hard-Wired CFL, 1-PL 23W, 1-Mag
Incandescent, 1-PAR 100W, no ballast | 100 | 1260 | Hard-Wired CFL, 1-PL 26W, 1-Mag
Incandescent, 1-PAR 150W, no ballast | 150 | 1566 | Ceramic Metal Halide, 1-PAR 39W, 1-Elec
Incandescent, 2-PAR 150W, no ballast | 300 | 3132 | Hard-Wired CFL, 2-2D 38W, 1-Elec
----------------------------
Incandescent, 1-PS30 200W, no ballast | 200 | 3153.5 | Hard-Wired CFL, 2-2D 28W, 1-Elec
Incandescent, 1-PS35 300W, no ballast | 300 | 4801.5 | Hard-Wired CFL, 2-2D 38W, 1-Elec
Incandescent, 1-PS40 500W, no ballast | 500 | 8811 | Ceramic Metal Halide, 1-SE 150W, 1-Elec
Incandescent, 1-PS40 620W, no ballast | 620 | 9350 | Ceramic Metal Halide, 1-SE 150W, 1-Elec
----------------------------
Halogen, 1-T3 100W, no ballast | 100 | 1440 | Ceramic Metal Halide, 1-39W, 1-Elec
Halogen, 1-T3 150W, no ballast | 150 | 2160 | Ceramic Metal Halide, 1-39W, 1-Elec
Halogen, 1-T3 250W, no ballast | 250 | 3600 | Ceramic Metal Halide, 1-70W, 1-Elec
Halogen, 1-T3 300W, no ballast | 300 | 4680 | Ceramic Metal Halide, 1-100W, 1-Elec
Halogen, 1-T3 500W, no ballast | 500 | 8550 | Ceramic Metal Halide, 1-150W, 1-Elec
Halogen, 1-T5 750W, no ballast | 750 | 13500 | Ceramic Metal Halide, 1-250W, 1-Elec
Halogen, 1-T3 1000W, no ballast | 1000 | 18900 | Ceramic Metal Halide, 1-320W, 1-Elec
Halogen, 1-T3 1500W, no ballast | 1500 | 29700 | Ceramic Metal Halide, 1-400W, 1-Elec
=================================
T12 2' Fluorescent, 1-F24T12/CW 20W, 1-Mag | 24 | 960 | T5, 1-F14T5
T12 3' Fluorescent, 1-F36T12/CW 30W, 1-Mag | 36 | 1630 | T5, 1-F21T5
T12 2'x2' Fluorescent, 1-F40T12 40W U-Tube, 1-Mag | 48 | 2775 | T5, 2-F14T5
T12 2'x2' Fluorescent, 2-F40T12 40W U-Tube, 1-Mag | 86 | 5550 | T5, 3-F14T5
T12 6' Fluorescent, 1-F72T12/CW 56W, 1-Mag | 65 | 4000 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP
----------------------------
T12 4' Fluorescent, 1-F40T12ES 34W, 1-Mag EE | 43 | 1890.51 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 1-F40T12 40W, 1-Mag EE | 46 | 2433.9 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP
T12 4' Fluorescent, 1-F40T12ES 34W, 1-Mag | 48 | 1933.97 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 1-F40T12 40W, 1-Mag | 52 | 2433.9 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP
----------------------------
T12 4' Fluorescent, 2-F40T12ES 34W, 1-Mag EE | 72 | 3781.02 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 2-F40T12ES 34W, 1-Mag | 82 | 3867.94 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 2-F40T12 40W, 1-Mag EE | 88 | 4867.8 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 2-F40T12 40W, 1-Mag | 96 | 4867.8 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO
----------------------------
T12 4' Fluorescent, 3-F40T12ES 34W, 2-Mag EE | 106 | 5671.53 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP
T12 4' Fluorescent, 3-F40T12ES 34W, 2-Mag EE | 112 | 5671.53 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP
T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 126 | 7301.7 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 3-F40T12ES 34W, 2-Mag | 130 | 5801.91 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP
T12 4' Fluorescent, 3-F40T12 40W, 2-Mag EE | 134 | 7301.7 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 3-F40T12 40W, 2-Mag | 148 | 7301.7 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO
----------------------------
T12 4' Fluorescent, 4-F40T12ES 34W, 2-Mag EE | 144 | 7562.04 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP
T12 4' Fluorescent, 4-F40T12ES 34W, 2-Mag | 164 | 7735.88 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP
T12 4' Fluorescent, 4-F40T12 40W, 2-Mag EE | 176 | 9735.6 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO
T12 4' Fluorescent, 4-F40T12 40W, 2-Mag | 192 | 9735.6 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO
=================================
T12 8' Fluorescent, 1-F96T12ES 60W, 1-Mag | 83 | 4258.65 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO
T12 8' Fluorescent, 1-F96T12 75W, 1-Mag | 100 | 5145.09 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP
T12 8' Fluorescent, 1-F96T12HOES 95W, 1-Mag | 125 | 5728.8 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP
T12 8' Fluorescent, 1-F96T12HO 110W, 1-Mag | 140 | 6715.94 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP HLO
T12 8' Fluorescent, 1-F96T12VHOES 185W, 1-Mag | 200 | 8370 | T8 Fluorescent, 1-F96T8 59W, 1-Elec
T12 8' Fluorescent, 1-F96T12VHO 215W, 1-Mag | 230 | 9525.6 | T8 Fluorescent, 1-F96T8 59W, 1-Elec
----------------------------
T12 8' Fluorescent, 2-F96T12ES 60W, 1-Mag EE | 123 | 8321.5 | T8 Fluorescent, 4-F32T8 32W, 1-Elec
T12 8' Fluorescent, 2-F96T12ES 60W, 1-Mag | 138 | 8517.3 | T8 Fluorescent, 4-F32T8 32W, 1-Elec
T12 8' Fluorescent, 2-F96T12 75W, 1-Mag EE | 158 | 10180.71 | T8 Fluorescent, 4-F32T8 32W, 1-Elec
T12 8' Fluorescent, 2-F96T12 75W, 1-Mag | 173 | 10290.18 | T8 Fluorescent, 4-F32T8 32W, 1-Elec
T12 8' Fluorescent, 2-F96T12HOES 95W, 1-Mag | 227 | 11457.6 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO
T12 8' Fluorescent, 2-F96T12HO 110W, 1-Mag EE | 237 | 13431.88 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO
T12 8' Fluorescent, 2-F96T12HO 110W, 1-Mag | 252 | 13431.88 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO
T12 8' Fluorescent, 2-F96T12VHOES 185W, 1-Mag | 325 | 16740 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec
T12 8' Fluorescent, 2-F96T12VHO 215W, 1-Mag | 440 | 19051.2 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec
----------------------------
T12 8' Fluorescent, 3-F96T12ES 60W, 2-Mag | 220 | 12775.95 | T8 Fluorescent, 2-F96T8HO 86W, 1-Elec
T12 8' Fluorescent, 3-F96T12 75W, 2-Mag | 274 | 15435.27 | T8 Fluorescent, 6-F32T8 32W, 1-Elec
T12 8' Fluorescent, 3-F96T12HOES 95W, 2-Mag | 352 | 17186.4 | T8 Fluorescent, 6-F32T8 32W, 2-Elec HLO
T12 8' Fluorescent, 3-F96T12HO 110W, 2-Mag EE | 392 | 20147.82 | T8 Fluorescent, 6-F32T8 32W, 2-Elec HLO
----------------------------
T12 8' Fluorescent, 4-F96T12ES 60W, 2-Mag EE | 246 | 16643 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO
T12 8' Fluorescent, 4-F96T12ES 60W, 2-Mag | 276 | 17034.6 | T8 Fluorescent, 4-F32T8 32W, 2-Elec HLO
T12 8' Fluorescent, 4-F96T12 75W, 2-Mag EE | 316 | 20361.42 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
T12 8' Fluorescent, 4-F96T12 75W, 2-Mag | 346 | 20580.36 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
T12 8' Fluorescent, 4-F96T12HOES 95W, 2-Mag EE | 416 | 22915.2 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
T12 8' Fluorescent, 4-F96T12HOES 95W, 2-Mag | 454 | 22915.2 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
T12 8' Fluorescent, 4-F96T12HO 110W, 2-Mag EE | 474 | 26863.76 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
T12 8' Fluorescent, 4-F96T12HO 110W, 2-Mag | 504 | 26863.76 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
T12 8' Fluorescent, 4-F96T12VHOES 185W, 2-Mag | 650 | 33480 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
T12 8' Fluorescent, 4-F96T12VHO 215W, 2-Mag | 880 | 38102.4 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
=================================
T12 Other Fluorescent, 1-F4T5 4W, 1-Mag Pre | 8 | 81.405 | None
T12 Other Fluorescent, 1-F6T5 6W, 1-Mag Pre | 10 | 177.885 | None
T12 Other Fluorescent, 1-F8T5 8W, 1-Mag Pre | 12 | 270 | None
T12 Other Fluorescent, 1-F15T12 15W, 1-Mag Pre | 19 | 554.04 | None
T12 Other Fluorescent, 1-F15T8 15W, 1-Mag Pre | 19 | 586.575 | None
T12 Other Fluorescent, 1-F20T12 20W, 1-Mag Pre | 25 | 943.5 | None
T12 Other Fluorescent, 1-FC6T9 20W, 1-Mag | 25 | 504 | None
T12 Other Fluorescent, 1-FC8T9 22W, 1-Mag | 27 | 675 | None
T12 Other Fluorescent, 1-F30T12ES 25W, 1-Mag | 42 | 1513.5312 | None
T12 Other Fluorescent, 1-FC12T9 32W, 1-Mag | 45 | 1231.875 | None
T12 Other Fluorescent, 1-F30T12 30W, 1-Mag | 46 | 1790.5688 | None
T12 Other Fluorescent, 1-F30T12 30W, 1-Mag Pre | 46 | 1667.0813 | None
T12 Other Fluorescent, 1-F30T8 30W, 1-Mag Pre | 46 | 1589.3813 | None
T12 Other Fluorescent, 1-FB40T12 40W, 1-Mag EE | 48 | 2234.4 | None
T12 Other Fluorescent, 1-FC16T9 40W, 1-Mag | 57 | 1822.5 | None
----------------------------
T12 Other Fluorescent, 2-F20T12 20W, 1-Mag Pre | 50 | 1887 | None
T12 Other Fluorescent, 2-F30T12ES 25W, 1-Mag EE | 66 | 3027.0625 | None
T12 Other Fluorescent, 2-F30T12 30W, 1-Mag Pre EE | 74 | 3581.1375 | None
T12 Other Fluorescent, 2-F30T12ES 25W, 1-Mag | 74 | 3027.0625 | None
T12 Other Fluorescent, 2-F30T12 30W, 1-Mag | 79 | 3334.1625 | None
T12 Other Fluorescent, 2-F30T12 30W, 1-Mag Pre | 79 | 3334.1625 | None
T12 Other Fluorescent, 2-F30T8 30W, 1-Mag Pre | 79 | 3178.7625 | None
T12 Other Fluorescent, 2-FB40T12 40W, 1-Mag EE | 86 | 4468.8 | None
=================================
High Pressure Sodium, 35W, 1-Std Mag | 45 | 1845 | None
High Pressure Sodium, 50W, 1-Std Mag | 68 | 3280 | None
High Pressure Sodium, 70W, 1-Std Mag | 86 | 5166 | None
High Pressure Sodium, 100W, 1-Std Mag | 120 | 7790 | None
High Pressure Sodium, 150W, 1-Std Mag | 170 | 13120 | None
High Pressure Sodium, 200W, 1-Std Mag | 245 | 18040 | None
High Pressure Sodium, 250W, 1-Std Mag | 295 | 22550 | None
High Pressure Sodium, 310W, 1-Std Mag | 365 | 30340 | None
High Pressure Sodium, 400W, 1-Std Mag | 457 | 41000 | None
High Pressure Sodium, 1000W, 1-Std Mag | 1100 | 114800 | None
=================================
Mercury Vapor, 100W, 1-Std Mag | 125 | 3400 | Hard-Wired CFL, 2-PL 32W, 1-Elec
Mercury Vapor, 175W, 1-Std Mag | 205 | 7600 | T8 Fluorescent, 2-F32T8 32W, 1-Elec HLO
Mercury Vapor, 250W, 1-Std Mag | 285 | 10700 | T5HO Fluorescent, 2-F54T5HO 54W, 1-Elec
Mercury Vapor, 400W, 1-Std Mag | 454 | 19100 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
Mercury Vapor, 1000W, 1-Std Mag | 1080 | 45000 | MH Pulse Start, 1-PS 400W, 1-Elec
=================================
Metal Halide, 50W, 1-Std Mag | 62 | 2006 | Hard-Wired CFL, 1-PL 32W, 1-Elec
Metal Halide, 70W, 1-Std Mag | 90 | 2950 | Hard-Wired CFL, 2-PL 26W, 1-Elec
Metal Halide, 100W, 1-Std Mag | 129 | 5440 | Hard-Wired CFL, 2-PL 42W, 1-Elec
Metal Halide, 150W, 1-Std Mag | 185 | 8640 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP
Metal Halide, 175W, 1-Std Mag | 210 | 9400 | T5HO Fluorescent, 2-F54T5HO 54W, 1-Elec
Metal Halide, 250W, 1-Std Mag | 295 | 11300 | T5HO Fluorescent, 3-F54T5HO 54W, 1-Elec
Metal Halide, 400W, 1-Std Mag | 458 | 26000 | T5HO Fluorescent, 4-F54T5HO 54W, 1-Elec
Metal Halide, 1000W, 1-Std Mag | 1080 | 78000 | MH Pulse Start, 750W, 1-PS Mag
Metal Halide, 1500W, 1-Std Mag | 1605 | 132000 | MH Pulse Start, 1000W, 1-PS Mag
=================================
Exit Sign, 2-inc 5W, no ballast | 10 | 2 | New Exit Sign, 1-LED <5W, 1-None
Exit Sign, 2-inc 8W, no ballast | 16 | 2 | New Exit Sign, 1-LED <5W, 1-None
Exit Sign, 2-Inc 10W, no ballast | 20 | 2 | New Exit Sign, 1-LED <5W, 1-None
Exit Sign, 2-Inc 11W, no ballast | 22 | 2 | New Exit Sign, 1-LED <5W, 1-None
Exit Sign, 2-Inc 15W, no ballast | 30 | 2 | New Exit Sign, 1-LED <5W, 1-None
Exit Sign, 2-Inc 20W, no ballast | 40 | 2 | New Exit Sign, 1-LED <5W, 1-None
Exit Sign, 2-Inc 25W, no ballast | 50 | 2 | New Exit Sign, 1-LED <5W, 1-None
Exit Sign, 2-Inc 40W, no ballast | 80 | 2 | New Exit Sign, 1-LED <5W, 1-None
=================================
Note on B184: Add additional fixture types in this area.

## Data Proposed
Updated April 19, 2005. This list is not meant to be complete, you can add qualifying equipment to this list.
Description of Proposed Lamp/Ballast Combination | Input Watts | Mean System Lumens | Notes / Alternate Suggestions | # lamps | bf | lumen lamp | lumen maint | ballast type | BEF | LPW
See attached lamp/ballast specification sheet |  |  | <<Input a wattage and mean system lumens
Decommission (Permanently Remove) Lighting Fixture | 0 | 0 | Permanently remove unneeded light fixtures
----------------------------
T8HP 4', 1-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 25 | 2297.1 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD | 1 | 0.78 | 3100 | 0.95 | ISL | 3.12 | 96.72
T8HP 4', 1-F32T8, 3100+lumen, 1-RLO Universal Triad Ultim8 B132IUNVEL-A | 25 | 2267.65 | Universal-Voltage, Instant-Start, Reduced Output | 1 | 0.77 | 3100 | 0.95 | PRS | 3.08 | 95.48
T8HP 4', 1-F32T8, 3100+lumen, 1-RLO GE-132-Ultramax-L | 25 | 2267.65 | Universal-Voltage, Instant-Start, Low-Output | 1 | 0.77 | 3100 | 0.95 | ISL | 3.08 | 95.48
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 28 | 2591.6 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD | 1 | 0.88 | 3100 | 0.95 | ISN | 3.1429 | 97.4286
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Universal Triad Ultim8 B132IUNVHE-A | 28 | 2562.15 | Universal-Voltage, Instant-Start, Normal-Output | 1 | 0.87 | 3100 | 0.95 | PRS | 3.1071 | 96.3214
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO GE-132/232-Ultramax-N | 28 | 2562.15 | Universal-Voltage, Instant-Start, Normal-Output | 1 | 0.87 | 3100 | 0.95 | ISN | 3.1071 | 96.3214
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Advance Optanium RCN/VCN-132-MC | 29 | 2886.1 | Dedicated-Voltage, Optanium, Centium, Micro Can | 1 | 0.98 | 3100 | 0.95 | ISN | 3.3793 | 104.7586
T8HP 4', 1-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP-2S32-SC | 29 | 2650.5 | Intellivolt, Optanium 2-lamp Program-Start operating 1 lamp | 1 | 0.9 | 3100 | 0.95 | PRS | 3.1034 | 96.2069
T8HP 4', 1-F32T8, 3100+lumen, 1-HLO Universal/GE B232PUNVHP-A | 32 | 2945 | Universal-Voltage, 2-lamp Program-Start operating 1 lamp | 1 | 1 | 3100 | 0.95 | PRS | 3.125 | 96.875
T8HP 4', 1-F32T8, 3100+lumen, 1-HLO Universal/GE B232I120HE | 33 | 3033.35 | 120 Volt, High-Efficency 2-lamp Instant-Start operating 1 lamp | 1 | 1.03 | 3100 | 0.95 | ISH | 3.1212 | 96.7576
---------------------------- | [8 empty] | 1.6/1.58/1.55/1.48/1.47 | 95
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Sylvania Extreme/UNV PSX-TC | 46 | 4181.9 | Use Program-Rapid-Start on frequently switched circuits | 2 | 0.71 | 3100 | 0.95 | PRS | 1.5435 | 95.6957
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 48 | 4594.2 | Best Energy Efficient Choice, High-Eff, Univ-Volt, IS, Low-THD | 2 | 0.78 | 3100 | 0.95 | ISL | 1.625 | 100.75
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-2P32-LW-SC | 48 | 4594.2 | Best Energy Efficient Choice, Dedicated-Voltage, Instant-Start | 2 | 0.78 | 3100 | 0.95 | ISL | 1.625 | 100.75
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Universal/GE B232I120EL or 277EL | 48 | 4594.2 | Best Energy Efficient Choice, Dedicated-Voltage, Instant-Start | 2 | 0.78 | 3100 | 0.95 | ISL | 1.625 | 100.75
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO GE-232-Ultramax-L | 48 | 4535.3 | Best Energy Efficient Choice, Universal-Voltage, Low-Output | 2 | 0.77 | 3100 | 0.95 | ISL | 1.6042 | 99.4583
T8HP 4', 2-F32T8, 3100+lumen, 1-RLO Advance Centium RCN/VCN-2P32-LW | 50 | 4594.2 | Dedicated-Voltage, Centium Low-THD, Low-Output | 2 | 0.78 | 3100 | 0.95 | ISL | 1.56 | 96.72
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO GE-232/332-Ultramax-N | 53 | 5124.3 | Universal-Voltage, Instant-Start, Normal-Output | 2 | 0.87 | 3100 | 0.95 | ISN | 1.6415 | 101.7736
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-3P32-LW-SC | 54 | 5006.5 | Dedicated-Voltage, 3 lamp Instant-Start driving 2 lamps | 2 | 0.85 | 3100 | 0.95 | ISN | 1.5741 | 97.5926
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 55 | 5183.2 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD | 2 | 0.88 | 3100 | 0.95 | ISN | 1.6 | 99.2
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-2P32-SC | 55 | 5183.2 | Dedicated-Voltage, Instant-Start, Normal-Output | 2 | 0.88 | 3100 | 0.95 | ISN | 1.6 | 99.2
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Universal/GE B232I120HE or 277HE | 55 | 5183.2 | Dedicated-Voltage, High-Efficiency Instant-Start, Normal-Output | 2 | 0.88 | 3100 | 0.95 | ISN | 1.6 | 99.2
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Universal/GE B332I277EL | 55 | 5124.3 | 277 Volt, standard 3 lamp Instant-Start driving 2 lamps | 2 | 0.87 | 3100 | 0.95 | ISN | 1.5818 | 98.0727
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Advance Optanium IOP-2S32-SC | 56 | 5183.2 | Intellivolt (120, 230, or 277 Volt), Optanium Program-Start | 2 | 0.88 | 3100 | 0.95 | PRS | 1.5714 | 97.4286
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Universal/GE B332I120EL | 56 | 5183.2 | 120 Volt, standard 3 lamp Instant-Start driving 2 lamps | 2 | 0.88 | 3100 | 0.95 | ISN | 1.5714 | 97.4286
T8HP 4', 2-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-4P32-LW-SC | 58 | 5242.1 | Dedicated-Voltage, 4 lamp Instant-Start driving 2 lamps | 2 | 0.89 | 3100 | 0.95 | ISN | 1.5345 | 95.1379
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Universal/GE B332I277HE | 61 | 5948.9 | 277 Volt, High-Efficiency 3 lamp Instant-Start driving 2 lamps | 2 | 1.01 | 3100 | 0.95 | ISH | 1.6557 | 102.6557
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Universal/GE B332I120HE | 63 | 5831.1 | 120 Volt, High-Efficiency 3 lamp Instant-Start driving 2 lamps | 2 | 0.99 | 3100 | 0.95 | ISN | 1.5714 | 97.4286
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Universal/GE B332PUNVHP-A | 64 | 5831.1 | Use Program-Start Universal-Voltage ballasts only if needed | 2 | 0.99 | 3100 | 0.95 | PRS | 1.5469 | 95.9062
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-3P32-SC | 65 | 6066.7 | Dedicated-Voltage, standard 3 lamp Instant-Start driving 2 lamps | 2 | 1.03 | 3100 | 0.95 | ISH | 1.5846 | 98.2462
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Centium RCN/VCN-3P32-SC | 65 | 6066.7 | Dedicated-Voltage, 3 lamp Instant-Start driving 2 lamps | 2 | 1.03 | 3100 | 0.95 | ISH | 1.5846 | 98.2462
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Centium Intellivolt ICN-3P32 | 65 | 5948.9 | Use Intellivolt Low-THD Centium ballasts only if needed | 2 | 1.01 | 3100 | 0.95 | ISH | 1.5538 | 96.3385
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Optanium ROP/VOP-4P32-SC | 66 | 6125.6 | Dedicated-Voltage, 4 lamp Instant-Start driving 2 lamps | 2 | 1.04 | 3100 | 0.95 | ISH | 1.5758 | 97.697
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO GE-232-Ultramax-H | 74 | 6773.5 | Universal-Voltage, Instant-Start, High-Output | 2 | 1.15 | 3100 | 0.95 | ISH | 1.5541 | 96.3514
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-2P32-HL-SC | 77 | 7068 | Dedicated-Voltage, standard electronic HLO can be efficient | 2 | 1.2 | 3100 | 0.95 | ISH | 1.5584 | 96.6234
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Sylvania Quicktronic QT2x32/120/277 Plus | 78 | 7068 | Dedicated-Voltage, standard electronic HLO can be efficient | 2 | 1.2 | 3100 | 0.95 | ISH | 1.5385 | 95.3846
T8HP 4', 2-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-3P32-HL-SC | 85 | 7774.8 | Dedicated-Voltage, standard electronic VHLO ballast | 2 | 1.32 | 3100 | 0.95 | ISH | 1.5529 | 96.2824
---------------------------- | [9 empty] | 95
T8HP 8', 2-F96T8, 5780+lumens Alto+, 1-Universal/GE B259I277HE | 106 | 9664.16 | Best Energy Efficient Choice, 277 Volt, High-Eff Instant-Start | 2 | 0.88 | 5780 | 0.95 | ISN | 0.83019 | 95.9698
T8HP 8', 2-F96T8, 5900+lumens Alto+, 1-Universal/GE B259I120HE | 106 | 9864.8 | Best Energy Efficient Choice, 120 Volt, High-Eff Instant-Start | 2 | 0.88 | 5900 | 0.95 | ISN | 0.83019 | 97.9623
T8HP 8', 2-F96T8, 5900+lumens Alto+, 1-Universal/GE B259I277HE | 108 | 9864.8 | Best Energy Efficient Choice, 277 Volt, High-Eff Instant-Start | 2 | 0.88 | 5900 | 0.95 | ISN | 0.81481 | 96.1481
T8HP 8', 2-F96T8, 5950+lumens GE XL Starcoat, 1-Universal/GE B259I120HE | 106 | 9948.4 | Best Energy Efficient Choice, 120 Volt, High-Eff Instant-Start | 2 | 0.88 | 5950 | 0.95 | ISN | 0.83019 | 98.7925
T8HP 8', 2-F96T8, 5950+lumens GE XL Starcoat, 1-Universal/GE B259I277HE | 108 | 9948.4 | Best Energy Efficient Choice, 277 Volt, High-Eff Instant-Start | 2 | 0.88 | 5950 | 0.95 | ISN | 0.81481 | 96.963
T8HP 8', 2-F96T8, 6100+lumens, 1-Sylvania Quicktronic 2x59/120 or 277v IS | 110 | 10199.2 | Dedicated-Voltage, Instant-Start, 12 hours per start | 2 | 0.88 | 6100 | 0.95 | ISN | 0.8 | 97.6
T8HP 8', 2-F96T8, 6100+lumens, 1-Advance Centium RCN/VCN-2P59 | 110 | 10199.2 | Dedicated-Voltage, Instant-Start, 12 hours per start | 2 | 0.88 | 6100 | 0.95 | ISN | 0.8 | 97.6
---------------------------- | [8 empty] | 1.04/1.05/1.04/0.97/1.0 | 95
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO TCP 4/3/2IS32-120U | 65.8 | 6184.5 | Best Energy Efficient Choice with significant light reduction | 3 | 0.7 | 3100 | 0.95 | ISL | 1.0638 | 98.9362
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Universal/GE B332I277EL | 70 | 6891.3 | Best Energy Efficient Choice, 277 Volt, standard electronic | 3 | 0.78 | 3100 | 0.95 | ISL | 1.1143 | 103.6286
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Universal/GE B332I120EL | 71 | 6891.3 | Best Energy Efficient Choice, 120 Volt, standard electronic | 3 | 0.78 | 3100 | 0.95 | ISL | 1.0986 | 102.169
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 73 | 6891.3 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD | 3 | 0.78 | 3100 | 0.95 | ISL | 1.0685 | 99.3699
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-3P32-LW-SC | 73 | 6891.3 | Dedicated-Voltage, Instant-Start, Low-Output | 3 | 0.78 | 3100 | 0.95 | ISL | 1.0685 | 99.3699
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO GE-332-Ultramax-L | 73 | 6802.95 | Universal-Voltage, Instant-Start, Low-Output | 3 | 0.77 | 3100 | 0.95 | ISL | 1.0548 | 98.0959
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Maxlite 50014 | 74 | 6802.95 | Reduced-Output | 3 | 0.77 | 3100 | 0.95 | ISL | 1.0405 | 96.7703
T8HP 4', 3-F32T8, 3100+lumen, 1-RLO Advance Centium RCN/VCN-3P32-LW-SC | 75 | 6979.65 | Dedicated-Voltage, Low-THD, Low-Output | 3 | 0.79 | 3100 | 0.95 | ISL | 1.0533 | 97.96
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B432I277EL | 76 | 7686.45 | 277 Volt, standard 4 lamp Instant-Start driving 3 lamps | 3 | 0.87 | 3100 | 0.95 | ISN | 1.1447 | 106.4605
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO GE-432-Ultramax-L | 78 | 7686.45 | Universal-Voltage, Low-Output, 4 lamp ballast driving 3 lamps | 3 | 0.87 | 3100 | 0.95 | ISN | 1.1154 | 103.7308
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-4P32-LW-SC | 78 | 7244.7 | Dedicated-Voltage, 4 lamp Instant-Start driving 3 lamps | 3 | 0.82 | 3100 | 0.95 | ISL | 1.0513 | 97.7692
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B432I120EL | 79 | 7421.4 | 120 Volt, standard 4 lamp Instant-Start driving 3 lamps | 3 | 0.84 | 3100 | 0.95 | ISL | 1.0633 | 98.8861
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B332I277HE | 80 | 7774.8 | 277 Volt, High-Efficiency Instant-Start | 3 | 0.88 | 3100 | 0.95 | ISN | 1.1 | 102.3
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B332I120HE | 81 | 7774.8 | 120 Volt, High-Efficiency, Instant-Start | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0864 | 101.037
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO GE-332-Ultramax-N | 82 | 7686.45 | Universal-Voltage, Instant-Start, Normal Light Output | 3 | 0.87 | 3100 | 0.95 | ISN | 1.061 | 98.6707
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 83 | 7774.8 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0602 | 98.6024
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-3P32-SC | 83 | 7774.8 | Dedicated-Voltage, Instant-Start | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0602 | 98.6024
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Elec REL/VEL-3P32-SC | 85 | 7774.8 | Dedicated-Voltage, standard Instant-Start | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0353 | 96.2824
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Centium RCN/VCN-3P32-SC | 85 | 7774.8 | Dedicated-Voltage, Centium Low-THD | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0353 | 96.2824
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Centium Intellivolt ICN-3P32 | 85 | 7774.8 | Intellivolt, Centium Low-THD | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0353 | 96.2824
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO GE-432-Ultramax-N | 85 | 7686.45 | Univ-Volt, Normal-Out, 4 lamp Instant-Start driving 3 lamps | 3 | 0.87 | 3100 | 0.95 | ISN | 1.0235 | 95.1882
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B332IUNVHP-A | 86 | 7774.8 | Universal-Voltage, Instant-Start, Normal Light Output | 3 | 0.88 | 3100 | 0.95 | ISN | 1.0233 | 95.1628
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QT3x32/120/277/ISN-SC | 87 | 7863.15 | Dedicated-Voltage, standard Instant-Start, Normal Light Output | 3 | 0.89 | 3100 | 0.95 | ISN | 1.023 | 95.1379
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B432I277HE | 88 | 8481.6 | 277 Volt, High-Efficiency 4 lamp Instant-Start driving 3 lamps | 3 | 0.96 | 3100 | 0.95 | ISN | 1.0909 | 101.4545
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B432I120HE | 89 | 8481.6 | 120 Volt, High-Efficiency 4 lamp Instant-Start driving 3 lamps | 3 | 0.96 | 3100 | 0.95 | ISN | 1.0787 | 100.3146
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-4P32-SC | 89 | 8128.2 | Dedicated-Voltage, 4 lamp Instant-Start driving 3 lamps | 3 | 0.92 | 3100 | 0.95 | ISN | 1.0337 | 96.1348
T8HP 4', 3-F32T8, 3100+lumen, 1-NLO Universal/GE B432PUNVHP-A | 91 | 8216.55 | Use Program-Start Universal-Voltage ballasts only if needed | 3 | 0.93 | 3100 | 0.95 | PRS | 1.022 | 95.044
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Advance Centium Intellivolt ICN-4P32-SC | 93 | 8835 | Intellivolt, Centium 4 lamp Instant-Start driving 3 lamps | 3 | 1 | 3100 | 0.95 | ISH | 1.0753 | 100
T8HP 4', 3-F32T8, 3100+lumen, 1-Advance Bi-Level REL/VEL-4P32-2LS | 93 | 8481.6 | Use Bi-Level Switching where possible | 3 | 0.96 | 3100 | 0.95 | ISN | 1.0323 | 96
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-4P32-SC | 94 | 8835 | Dedicated-Voltage, standard 4 lamp Instant-Start driving 3 lamps | 3 | 1 | 3100 | 0.95 | ISH | 1.0638 | 98.9362
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Advance Elec RCN/VCN-4P32-SC | 94 | 8835 | Dedicated-Voltage, Centium 4 lamp Instant-Start driving 3 lamps | 3 | 1 | 3100 | 0.95 | ISH | 1.0638 | 98.9362
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Univ/GE B332PUNVHP-A, 1-B232PUNVHP-A | 96 | 8746.65 | Use Bi-Level Switching where possible, Program-Start, Univ-Volt | 3 | 0.99 | 3100 | 0.95 | PRS | 1.0312 | 95.9062
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Advance Elec REL/VEL-3P32-HL-SC | 111 | 10513.65 | Use HLO system only if absolutely necessary | 3 | 1.19 | 3100 | 0.95 | ISH | 1.0721 | 99.7027
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO GE-332-Ultramax-H | 111 | 10160.25 | Use HLO system only if absolutely necessary | 3 | 1.15 | 3100 | 0.95 | ISH | 1.036 | 96.3514
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Sylvania Quicktronic QT3X32/120/277/IS Plus | 112 | 10425.3 | Use HLO system only if absolutely necessary | 3 | 1.18 | 3100 | 0.95 | ISH | 1.0536 | 97.9821
T8HP 4', 3-F32T8, 3100+lumen, 1-HLO Maxlite 50024 | 115 | 10602 | Use HLO system only if absolutely necessary | 3 | 1.2 | 3100 | 0.95 | ISH | 1.0435 | 97.0435
---------------------------- | [8 empty] | 0.79/0.8/0.77/0.76/0.75 | 95
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO TCP 4/3/2IS32-120U | 82 | 8128.2 | Best Energy Efficient Choice with significant light reduction | 4 | 0.69 | 3100 | 0.95 | ISL | 0.84146 | 104.3415
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Sylvania Extreme/UNV PSX-SC | 91 | 8363.8 | Use Program-Rapid-Start Ballasts on frequently switched circuits | 4 | 0.71 | 3100 | 0.95 | PRS | 0.78022 | 96.7473
T8HP 4', 4-F32T8, 3100+lumen, 2-RLO Sylvania Extreme/UNV PSX-TC | 92 | 8363.8 | Use Bi-Level Program-Rapid-Start where possible | 4 | 0.71 | 3100 | 0.95 | PRS | 0.77174 | 95.6957
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Universal/GE B432I277EL | 94 | 9188.4 | Best Energy Efficient Choice, 277 Volt, standard Instant-Start | 4 | 0.78 | 3100 | 0.95 | ISL | 0.82979 | 102.8936
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QHE/UNV ISL-SC | 95 | 9188.4 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD | 4 | 0.78 | 3100 | 0.95 | ISL | 0.82105 | 101.8105
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Universal/GE B432I120EL | 95 | 9188.4 | 120 Volt, standard Instant-Start | 4 | 0.78 | 3100 | 0.95 | ISL | 0.82105 | 101.8105
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Advance Optanium ROP/VOP-4P32-LW-SC | 96 | 9188.4 | Dedicated-Voltage, Instant-Start, Low-Output ballast | 4 | 0.78 | 3100 | 0.95 | ISL | 0.8125 | 100.75
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO GE-432-Ultramax-L | 97 | 9070.6 | Universal-Voltage, Instant-Start, Low-Output | 4 | 0.77 | 3100 | 0.95 | ISL | 0.79381 | 98.433
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Sylvania Quicktronic QT4x32/120/277 LP | 98 | 9070.6 | Dedicated-Voltage, standard Instant-Start, Low-Output | 4 | 0.77 | 3100 | 0.95 | ISL | 0.78571 | 97.4286
T8HP 4', 4-F32T8, 3100+lumen, 1-RLO Advance Centium RCN/VCN-4P32-LW-SC | 99 | 8952.8 | Dedicated-Voltage, Centium Low-THD, Low-Output, Small-Can | 4 | 0.76 | 3100 | 0.95 | ISL | 0.76768 | 95.1919
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Universal/GE B432I277HE | 107 | 10366.4 | 277 Volt, High Efficiency Instant-Start | 4 | 0.88 | 3100 | 0.95 | ISN | 0.82243 | 101.9813
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QHE/UNV ISN-SC | 108 | 10366.4 | High-Efficiency, Universal-Voltage, Instant-Start, Low-THD | 4 | 0.88 | 3100 | 0.95 | ISN | 0.81481 | 101.037
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Universal/GE B432I120HE | 108 | 10366.4 | 120 Volt, High-Efficiency Instant-Start | 4 | 0.88 | 3100 | 0.95 | ISN | 0.81481 | 101.037
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Optanium ROP/VOP-4P32-SC | 108 | 10366.4 | Dedicated-Voltage, Instant-Start, Normal-Output, Small-Can | 4 | 0.88 | 3100 | 0.95 | ISN | 0.81481 | 101.037
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO GE-432-Ultramax-N | 109 | 10248.6 | Universal-Voltage, Instant-Start, Normal-Output | 4 | 0.87 | 3100 | 0.95 | ISN | 0.79817 | 98.9725
T8HP 4', 4-F32T8, 3100+lumen, 1-Advance Bi-Level REL/VEL-4P32-2LS | 110 | 10248.6 | Use Bi-Level Switching where possible | 4 | 0.87 | 3100 | 0.95 | ISN | 0.79091 | 98.0727
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Elec REL/VEL-4P32-SC | 112 | 10366.4 | Dedicated-Voltage, standard Instant-Start, Small-Can | 4 | 0.88 | 3100 | 0.95 | ISN | 0.78571 | 97.4286
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Centium RCN/VCN-4P32-SC | 112 | 10366.4 | Dedicated-Voltage, Centium Low-THD, Normal-Output | 4 | 0.88 | 3100 | 0.95 | ISN | 0.78571 | 97.4286
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Advance Centium Intellivolt ICN-4P32-SC | 112 | 10366.4 | Intellivolt, Centium Low-THD | 4 | 0.88 | 3100 | 0.95 | ISN | 0.78571 | 97.4286
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QT/120/277ISN-SC | 114 | 10484.2 | Dedicated-Voltage, standard Instant-Start | 4 | 0.89 | 3100 | 0.95 | ISN | 0.7807 | 96.807
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Maxlite 50006 | 114 | 10366.4 | Normal-Output | 4 | 0.88 | 3100 | 0.95 | ISN | 0.77193 | 95.7193
T8HP 4', 4-F32T8, 3100+lumen, 1-NLO Sylvania Quicktronic QTP4x32/UNV-ISN-SC | 114 | 10366.4 | Universal-Voltage, standard Instant-Start | 4 | 0.88 | 3100 | 0.95 | ISN | 0.77193 | 95.7193
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-3P32-SC | 130 | 12133.4 | Use 2-2 lamp HLO ballasts only if absolutely necessary | 4 | 1.03 | 3100 | 0.95 | ISH | 0.79231 | 98.2462
T8HP 4', 4-F32T8, 3100+lumen, 1-HLO GE-432-Ultramax-H | 147 | 13547 | Universal-Voltage, Instant-Start, High-Output | 4 | 1.15 | 3100 | 0.95 | ISH | 0.78231 | 97.0068
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO GE-232-Ultramax-H | 148 | 13547 | Use 2-2 lamp HLO ballasts only if absolutely necessary | 4 | 1.15 | 3100 | 0.95 | ISH | 0.77703 | 96.3514
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-2P32-HL-SC | 154 | 14136 | Use 2-2 lamp HLO ballasts only if absolutely necessary | 4 | 1.2 | 3100 | 0.95 | ISH | 0.77922 | 96.6234
T8HP 4', 4-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-3P32-HL-SC | 170 | 15549.6 | Use 2-3 lamp HLO ballasts only if absolutely necessary | 4 | 1.32 | 3100 | 0.95 | ISH | 0.77647 | 96.2824
---------------------------- | [9 empty] | 95
T8HP 4', 6-F32T8, 3100+lumen, 1-2 lamp & 1-4 lamp RLO Sylvania Extreme | 137 | 12545.7 | Use Bi-Level ProgStart System on frequently switched circuits | 6 | 0.71 | 3100 | 0.95 | ISL | 0.51825 | 96.3942
T8HP 4', 6-F32T8, 3100+lumen, 2-HLO GE-332-Ultramax-H | 222 | 20320.5 | Use 2-3 lamp HLO system only if absolutely necessary | 6 | 1.15 | 3100 | 0.95 | ISH | 0.51802 | 96.3514
T8HP 4', 6-F32T8, 3100+lumen, 2-HLO Advance Elec REL/VEL-4P32-HL-SC | 222 | 21027.3 | Use 2-4 lamp HLO ballasts only if absolutely necessary | 6 | 1.19 | 3100 | 0.95 | ISH | 0.53604 | 99.7027
T8HP 4', 6-F32T8, 3100+lumen, 2-HLO Sylvania Quicktronic QT/3x32/120/277 Plus | 224 | 20850.6 | Use 2-3 lamp HLO system only if absolutely necessary | 6 | 1.18 | 3100 | 0.95 | ISH | 0.52679 | 97.9821
T8HP 4', 6-F32T8, 3100+lumen, 3-HLO Advance Elec REL/VEL-3P32-HL-SC | 255 | 23324.4 | Use 3-3 lamp HLO ballasts only if absolutely necessary | 6 | 1.32 | 3100 | 0.95 | ISH | 0.51765 | 96.2824
---------------------------- | [9 empty] | 95
T8HP 4', 8-F32T8, 3100+lumen, 2-4 lamp RLO Sylvania Extreme | 182 | 16727.6 | Use Bi-Level ProgStart System on frequently switched circuits | 8 | 0.71 | 3100 | 0.95 | ISL | 0.39011 | 96.7473
T8HP 4', 8-F32T8, 3100+lumen, 2-NLO Sylvania Quicktronic QT/120/277ISN-SC | 228 | 20968.4 | Dedicated-Voltage, standard Instant-Start | 8 | 0.89 | 3100 | 0.95 | ISN | 0.39035 | 96.807
T8HP 4', 8-F32T8, 3100+lumen, 2-HLO GE-432-Ultramax-H | 294 | 27094 | Universal-Voltage, Instant-Start, High-Output | 8 | 1.15 | 3100 | 0.95 | ISH | 0.39116 | 97.0068
================================= |  |  |  | # lamps | bf | lumen lamp | lumen maint | ballast type | BEF | LPW
Standard Electronic T8 lamp/ballast combinations
T8 Standard Electronic, 1-F17T8 17W, 1-Elec | 16 | 1102.5 | None
T8 Standard Electronic, 1-F25T8 25W, 1-Elec | 23 | 1752.1875 | None
T8 Standard Electronic, 1-F32T8 32W, 1-Elec RLO | 27 | 1991.25 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO
T8 Standard Electronic, 1-F32T8 32W, 1-Elec | 31 | 2400 | T8 High Performance, 1-F32T8HP 32W, 1-Elec HP RLO
T8 Standard Electronic, 1-F96T8 59W, 1-Elec | 68 | 4513.5 | None
T8 Standard Electronic, 1-F96T8HO 86W, 1-Elec | 99 | 7380 | None
----------------------------
T8 Standard Electronic, 2-F17T8 17W, 1-Elec | 31 | 2205 | None
T8 Standard Electronic, 2-F25T8 25W, 1-Elec | 46 | 3504.375 | None | [5 empty] | 1.6/1.58/1.55/1.48/1.47
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-Elec VRLO | 51 | 4315.85 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | 2 | 0.77 | 2950 | 0.95 | ISL | 1.5098 | 89.0784
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-Elec RLO | 55 | 4371.9 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | 2 | 0.78 | 2950 | 0.95 | ISL | 1.4182 | 83.6727
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-ISElec | 59 | 4932.4 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | 2 | 0.88 | 2950 | 0.95 | ISN | 1.4915 | 88
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-RSElec | 62 | 4932.4 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP RLO | 2 | 0.88 | 2950 | 0.95 | ISN | 1.4194 | 83.7419
T8 Standard Electronic, 2-F32T8, 2950+lumen, 1-Elec HLO | 76 | 6265.8 | T8 High Performance, 2-F32T8HP 32W, 1-Elec HP HLO | 2 | 1.15 | 2950 | 0.95 | ISH | 1.5132 | 89.2763
T8 Standard Electronic, 2-F96T8 59W, 1-Elec | 105 | 9027 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO
T8 Standard Electronic, 2-F96T8HO 86W, 1-Elec | 155 | 12693.6 | T8 High Performance, 4-F32T8HP 32W, 2-Elec HP HLO
----------------------------
T8 Standard Electronic, 3-F17T8 17W, 1-Elec | 46 | 3307.5 | None
T8 Standard Electronic, 3-F25T8 25W, 1-Elec | 66 | 5256.5625 | None
T8 Standard Electronic, 3-F32T8 32W, 1-Elec RLO | 80 | 5973.75 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO
T8 Standard Electronic, 3-F32T8 32W, 1-Elec | 90 | 6969.375 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP RLO
----------------------------
T8 Standard Electronic, 4-F17T8 17W, 1-Elec | 63 | 4410 | None
T8 Standard Electronic, 4-F25T8 25W, 1-Elec | 90 | 7008.75 | None
T8 Standard Electronic, 4-F32T8 32W, 1-Elec RLO | 98 | 7728 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP
T8 Standard Electronic, 4-F32T8 32W, 1-Elec RLO | 101 | 7965 | T8 High Performance, 3-F32T8HP 32W, 1-Elec HP
T8 Standard Electronic, 4-F32T8 32W, 1-Elec | 114 | 9292.5 | T8 High Performance, 4-F32T8HP 32W, 1-Elec HP RLO
T8 Standard Electronic, 4-F32T8 32W, 2-Elec HLO | 172 | 13593.6 | T8 High Performance, 4-F32T8HP 32W, 2-Elec HP HLO
----------------------------
T8 Standard Electronic, 6-F32T8 32W, 2-Elec | 175 | 13938.75 | None
T8 Standard Electronic, 6-F32T8 32W, 2-Elec HLO | 228 | 18797.4 | None
=========================== |  |  |  | # lamps | bf | lumen lamp | lumen maint | ballast type | BEF | LPW
High Output T5 fluorescent lamp/ballast combinations | [8 empty] | 2.84/1.47/1.00/0.75
T5HO Fluorescent, 1-F54T5HO 54W, 1-Program Start | 62 | 4750 | None | 1 | 1 | 5000 | 0.95 | PRS | 1.6129 | 80.6452
T5HO Fluorescent, 2-F54T5HO 54W, 1-Program Start | 118 | 9500 | None | 2 | 1 | 5000 | 0.95 | PRS | 0.84746 | 84.7458
T5HO Fluorescent, 3-F54T5HO 54W, 2-Program Start | 179 | 14250 | None | 3 | 1 | 5000 | 0.95 | PRS | 0.55866 | 83.7989
T5HO Fluorescent, 4-F54T5HO 54W, 2-Program Start | 234 | 19000 | None | 4 | 1 | 5000 | 0.95 | PRS | 0.42735 | 85.4701
T5HO Fluorescent, 5-F54T5HO 54W, 3-Program Start | 298 | 23750 | None | 5 | 1 | 5000 | 0.95 | PRS | 0.33557 | 83.8926
T5HO Fluorescent, 6-F54T5HO 54W, 3-Program Start | 352 | 28500 | None | 6 | 1 | 5000 | 0.95 | PRS
T5HO Fluorescent, 8-F54T5HO 54W, 4-Program Start | 472 | 38000 | None | 8 | 1 | 5000 | 0.95 | PRS
===========================
Hard-Wired CFL, 1-bi-ax 13W, 1-Elec | 16 | 765 | None
Hard-Wired CFL, 1-bi-ax 13W, 1-Mag | 15 | 670.905 | None
Hard-Wired CFL, 1-bi-ax 15W, 1-Mag | 17 | 778.77 | None
Hard-Wired CFL, 1-bi-ax 16W, 1-Mag | 18 | 833.085 | None
Hard-Wired CFL, 1-bi-ax 18W, 1-Elec | 19 | 1062.5 | None
Hard-Wired CFL, 1-bi-ax 18W, 1-Mag | 20 | 941.715 | None
Hard-Wired CFL, 1-bi-ax 20W, 1-Mag | 22 | 1049.58 | None
Hard-Wired CFL, 1-bi-ax 22W, 1-Mag | 23 | 1158.21 | None
Hard-Wired CFL, 1-bi-ax 23W, 1-Mag | 24 | 1211.76 | None
Hard-Wired CFL, 1-bi-ax 24W, 1-Mag | 25 | 1266.075 | None
Hard-Wired CFL, 1-bi-ax 26W, 1-Elec | 27 | 1530 | None
Hard-Wired CFL, 1-bi-ax 26W, 1-Mag | 27 | 1374.705 | None
Hard-Wired CFL, 1-bi-ax 27W, 1-Mag | 28 | 1428.255 | None
Hard-Wired CFL, 1-bi-ax 28W, 1-Mag | 29 | 1482.57 | None
Hard-Wired CFL, 1-bi-ax 32W, 1-Elec | 33 | 2040 | None
Hard-Wired CFL, 1-bi-ax 32W, 1-Mag | 36 | 2040 | None
Hard-Wired CFL, 1-bi-ax 42W, 1-Elec | 43 | 2720 | None
Hard-Wired CFL, 1-bi-ax 42W, 1-Mag | 46 | 2720 | None
Hard-Wired CFL, 1-bi-ax 55W, 1-Mag | 54 | 2677.5 | None
Hard-Wired CFL, 1-bi-ax 65W, 1-Mag | 63 | 3213 | None
Hard-Wired CFL, 1-bi-ax 85W, 1-Mag | 82 | 4207.5 | None
----------------------------
Hard-Wired CFL, 2-bi-ax 5W, 2-Mag | 14 | 475.83 | None
Hard-Wired CFL, 2-bi-ax 7W, 2-Mag | 18 | 691.56 | None
Hard-Wired CFL, 2-bi-ax 9W, 2-Mag | 22 | 908.82 | None
Hard-Wired CFL, 2-bi-ax 10W, 2-Mag | 26 | 1017.45 | None
Hard-Wired CFL, 2-bi-ax 11W, 2-Mag | 28 | 1124.55 | None
Hard-Wired CFL, 2-bi-ax 13, 1-Elec | 29 | 1530 | None
Hard-Wired CFL, 2-bi-ax 13W, 2-Mag | 30 | 1341.81 | None
Hard-Wired CFL, 2-bi-ax 15W, 2-Mag | 32 | 1557.54 | None
Hard-Wired CFL, 2-bi-ax 18W, 1-Elec | 35 | 2125 | None
Hard-Wired CFL, 2-bi-ax 18W, 2-Mag | 40 | 1883.43 | None
Hard-Wired CFL, 2-bi-ax 20W, 2-Mag | 42 | 2099.16 | None
Hard-Wired CFL, 2-bi-ax 22W, 2-Mag | 46 | 2316.42 | None
Hard-Wired CFL, 2-bi-ax 23W, 2-Mag | 48 | 2423.52 | None
Hard-Wired CFL, 2-bi-ax 24W, 2-Mag | 50 | 2532.15 | None
Hard-Wired CFL, 2-bi-ax 26W, 1-Elec | 52 | 3060 | None
Hard-Wired CFL, 2-bi-ax 26W, 2-Mag | 52 | 2749.41 | None
Hard-Wired CFL, 2-bi-ax 16W, 2-Mag | 56 | 1666.17 | None
Hard-Wired CFL, 2-bi-ax 27W, 2-Mag | 58 | 2856.51 | None
Hard-Wired CFL, 2-bi-ax 28W, 2-Mag | 58 | 2965.14 | None
Hard-Wired CFL, 2-bi-ax 32W, 2-Mag | 64 | 3398.13 | None
Hard-Wired CFL, 2-bi-ax 32W, 1-Elec | 68 | 4080 | None
Hard-Wired CFL, 2-bi-ax 42W, 1-Elec | 93 | 5440 | None
----------------------------
Hard-Wired CFL, 1-2D 16W, 1-Elec | 15 | 803.25 | None
Hard-Wired CFL, 1-2D 21W, 1-Elec | 21 | 1032.75 | None
Hard-Wired CFL, 1-2D 28W, 1-Elec | 28 | 1568.25 | None
Hard-Wired CFL, 1-2D 38W, 1-Elec | 37 | 2180.25 | None
----------------------------
Hard-Wired CFL, 2-2D 16W, 1-Elec | 30 | 1606.5 | None
Hard-Wired CFL, 2-2D 21W, 1-Elec | 42 | 2065.5 | None
Hard-Wired CFL, 2-2D 28W, 1-Elec | 56 | 3136.5 | None
Hard-Wired CFL, 2-2D 38W, 1-Elec | 74 | 4360.5 | None
===========================
Screw-In CFL, 1-3W capsule, 1-Mag | 3 | 128 | None
Screw-In CFL, 1-5W capsule, 1-Mag | 5 | 213 | None
Screw-In CFL, 1-7W capsule, 1-Mag | 7 | 255 | None
Screw-In CFL, 1-7W spiral, 1-Mag | 7 | 383 | None
Screw-In CFL, 1-9W spiral, 1-Mag | 9 | 340 | None
Screw-In CFL, 1-10W, 1-Mag | 10 | 450 | None
Screw-In CFL, 1-11W spiral, 1-Mag | 11 | 550 | None
Screw-In CFL, 1-13W spiral, 1-Mag | 13 | 680 | None
Screw-In CFL, 1-14W spiral, 1-Mag | 14 | 720 | None
Screw-In CFL, 1-2D 15W, 1-Elec | 15 | 640 | None
Screw-In CFL, 1-15W spiral, 1-Mag | 15 | 791 | None
Screw-In CFL, 1-16W, 1-Mag | 16 | 833.085 | None
Screw-In CFL, 1-18W modular-spiral, 1-Mag | 18 | 978 | None
Screw-In CFL, 1-20W spiral, 1-Mag | 20 | 1020 | None
Screw-In CFL, 1-22W circline, 1-Mag | 22 | 1020 | None
Screw-In CFL, 1-2D 22W, 1-Elec | 22 | 1105 | None
Screw-In CFL, 1-22W, 1-Mag | 22 | 1158.21 | None
Screw-In CFL, 1-23W spiral, 1-Mag | 23 | 1190 | None
Screw-In CFL, 1-24W bi-ax, 1-Mag | 24 | 1290 | None
----------------------------
Screw-In CFL, 1-25W spiral, 1-Mag | 25 | 1360 | None
Screw-In CFL, 1-26W modular-spiral, 1-Mag, "Wall Pack" | 26 | 1488 | None
Screw-In CFL, 1-27W spiral, 1-Mag | 27 | 1488 | None
Screw-In CFL, 1-28W bi-ax, 1-Mag | 28 | 1482.57 | None
Screw-In CFL, 1-30W circline, 1-Mag | 30 | 1530 | None
Screw-In CFL, 1-32W modular-spiral, 1-Mag, "Wall Pack" | 32 | 1785 | None
Screw-In CFL, 1-36W circline, 1-Mag | 36 | 1785 | None
Screw-In CFL, 1-2D 39W, 1-Elec | 39 | 2360 | None
Screw-In CFL, 1-40W circline, 1-Mag | 40 | 2380 | None
Screw-In CFL, 1-42W spiral, 1-Mag | 42 | 2380 | None
Screw-In CFL, 1-44W bi-ax, 1-Mag | 44 | 2040 | None
----------------------------
Screw-In CFL, 1-55W spiral, 1-Mag | 55 | 2975 | None
Screw-In CFL, 1-65W spiral, 1-Mag | 65 | 3570 | None
Screw-In CFL, 1-85W spiral, 1-Mag | 85 | 4675 | None
Screw-In CFL, 1-105W bi-ax, 1-Elec | 105 | 5865 | None
===========================
MH Pulse Start, 1-PS 300W, 1-LLRPSL, 277V only, low voltage swing tolerance | 324 | 24400 | None
MH Pulse Start, 1-PS 300W, 1-SCWA typical ballast | 342 | 24400 | None
MH Pulse Start, 1-PS 320W, 1-LLRPSL, 277V only, low voltage swing tolerance | 349 | 26400 | None
MH Pulse Start, 1-PS 320W, 1-SCWA typical ballast | 370 | 26400 | None
MH Pulse Start, 1-PS 350W, 1-LLRPSL, 277V only, low voltage swing tolerance | 380 | 29600 | None
MH Pulse Start, 1-PS 350W, 1-SCWA typical ballast | 400 | 29600 | None
MH Pulse Start, 1-PS 400W, 1-Elec | 425 | 36120 | None
MH Pulse Start, 1-PS 400W, 1-LLRPSL, 277V only, low voltage swing tolerance | 435 | 31500 | None
MH Pulse Start, 1-PS 400W, 1-SCWA typical ballast | 455 | 31500 | None
MH Pulse Start, 1-PS 400W, 1-RPB handles voltage swings | 467 | 31500 | None
MH Pulse Start, 1-PS 450W, 1-LLRPSL, 277V only, low voltage swing tolerance | 485 | 40000 | None
MH Pulse Start, 1-PS 450W, 1-SCWA typical ballast | 514 | 40000 | None
MH Pulse Start, 1-PS 450W, 1-RPB handles voltage swings | 530 | 40000 | None
MH Pulse Start, 1-PS 750W, 1-SCWA is the only option | 818 | 60000 | None
MH Pulse Start, 1-PS 875W, 1-SCWA is the only option | 940 | 80500 | None
MH Pulse Start, 1-PS 1000W, 1-SCWA is the only option | 1080 | 96000 | None
===========================
Ceramic Metal Halide, 1-Single End 20W, 1-Elec | 28 | 1100 | Great option for retail display lighting - ie. track or recessed can
Ceramic Metal Halide, 1-Single End or Double End 39W, 1-Elec | 45 | 2600 | Great option for retail display lighting - ie. track or recessed can
Ceramic Metal Halide, 1-Single End or Double End 70W, 1-Elec | 80 | 5200 | Great option for retail display lighting - ie. track or recessed can
Ceramic Metal Halide, 1-Single End or Double End 150W, 1-Elec | 168 | 10200 | Great option for retail display lighting - ie. track or recessed can
Ceramic Metal Halide, 1-Bulb 50W, 1-Elec | 55 | 2640 | Great option for general retail lighting
Ceramic Metal Halide, 1-Bulb 70W, 1-Elec | 80 | 4700 | Great option for general retail lighting
Ceramic Metal Halide, 1-Bulb 100W, 1-Elec | 112 | 6800 | Great option for general retail lighting
Ceramic Metal Halide, 1-Bulb 150W, 1-Elec | 168 | 9920 | Great option for general retail lighting
Ceramic Metal Halide, 1-PAR 39W, 1-Elec | 45 | 1600 | Great option for retail display lighting - ie. track or recessed can
Ceramic Metal Halide, 1-PAR 70W, 1-Elec | 80 | 3840 | Great option for retail display lighting - ie. track or recessed can
Ceramic Metal Halide, 1-PAR 100W, 1-Elec | 112 | 5440 | Great option for retail display lighting - ie. track or recessed can
===========================
Induction, 1-QL 55W, 1-RF Generator | 55 | 2800 | Great option for Street & Area lighting - 100,000 hr life
Induction, 1-QL 85W, 1-RF Generator | 85 | 4800 | Great option for Street & Area lighting - 100,000 hr life
Induction, 1-Icetron 100W donut, 1-RF Generator | 157 | 5920 | Great option for Street & Area lighting - 100,000 hr life
Induction, 1-QL 165W, 1-RF Generator | 165 | 9600 | Great option for Street & Area lighting - 100,000 hr life
===========================
New Exit Sign, 1 face Cold Cathode, 4W, no ballast | 4 | 2 | None
New Exit Sign, 1 face LED, 1.5W, no ballast | 1.5 | 2 | None
New Exit Sign, 2 faced Cold Cathode, 4W/face, no ballast | 8 | 2 | None
New Exit Sign, 2 faced LED, 1.5W/face, no ballast | 3 | 2 | None
New Exit Sign, 2 faced LED with battery back-up, no ballast | 9 | 2 | None
===========================
Note on B301: Add additional fixture types in this area.