REFERENCE DESIGN

For Programmable Communicating Thermostats

Compliant with Title 24-2008

Version 1.00

March 26, 2007

Editor:  Erich W. Gunther (erich@enernex.com)

Table of Contents

1. Introduction	4

1.1	The Title 24 PCT Code Language (Rev 29f)	4

1.2	The Virtual Operation Model for Thermostats	6

1.2.1 Required Functional Resources	7

1.2.2 Required Functional Behavior	8

2. The HVAC System Interface	11

2.1	Minimal Direct Control Interface	11

2.2	Advanced Thermostat Direct Control Interface	12

2.3	Digital Control Interface	13

3. Expansion Interface	15

4. Communications Interface	17

4.1	Logical Information and Transaction Model	17

4.2	PCT Functions	18

4.3	PCT Messages and Attributes	18

4.3.1 Event Modes	19

4.3.2 Common Data Classes	19

4.3.3 Message Commands for Minimum Title 24 PCT Functionality	21

4.4	PCT Transactions	23

4.5	Implementation Profiles	25

4.6	Security	25

4.6.1 Fundamental, Strategic Objectives	25

4.6.2 Assumptions	25

4.6.3 Risk Management Approach	27

4.6.4 Possible Attacks	27

4.6.5 Non-Cryptographic Mitigation Methods	29

4.6.6 Message Content	31

4.6.7 Cryptographic Mitigation Approaches	32

4.6.8 Remaining Issues	38

5. Human-Machine Interface	39

5.1	Terminology	39

5.2	Next Steps and Issues to be Resolved	40

5.2.1 Interaction with “Hold” Functions	40

5.2.2 Recovery from “Off” State within an Active Event	40

5.2.3 Standardization of Colors, Indicators, and Icons	40

Annex A: PCT Use Cases	44

Annex B: Glossary	48

Annex C: UC Berkeley PCT Research Report	50

Annex D: Other Publications	51

Annex E: Title 24 Language 	(Final Draft – Rev 29f)	52

Annex F: The PCT Vision Document and Related Scenarios	54

Eliminating the Need for Rotating Outages  through Statewide Air-Conditioning Load Control with Programmable Communicating Thermostats (PCTs)	54

Scenario 1- Residential, Low User, Minimum Functionality, Special Exemptions	58

Scenario 2 - Residential, High User, High End Options, Advanced Functionality	70

Scenario 3 - Large Commercial / Industrial	76

Scenario 4 – Utility Company	80

Scenario 5 – California ISO	82

Scenario 6 – California Public Utilities Commission	85

Annex G: Material related to Joint IOU PCT Specifications using Two-Way Communications for Extended Functionality	89

Annex G1: Digital Control Interface	90

Annex G2: Reliability Event Commands	91

Annex G3: Message Commands for Joint IOU PCT Functionality using Two-Way Communications	92

Annex G4: Message Responses for Joint IOU PCT Functionality using Two-Way Communications	94

# Introduction

This document provides a Reference Design for a programmable communicating thermostat (PCT) that is compliant with the 2008 Update to the Title 24 Building Energy Efficiency Standards.  The Reference Design focuses on four interfaces that the CEC has determined must be supported by all PCTs:

- HVAC System Interface

- Communications Interface

- Expansion Interface

- Human-Machine Interface

Sections within this document address each interface in terms of its hardware and software characteristics.  In general and unless otherwise specified, this reference design is compatible with NEMA Standards Publication DC 3-2003 – “Residential Controls – Electrical Wall-Mounted Thermostats”.

In particular, note that the Communications Interface is defined as a set of logical services that may be performed either over the mandatory wide area communications interface (e.g. Radio Broadcast Data System -RBDS- or paging system) of the PCT, or over an optional external physical network interface connected to the Expansion Interface.

These interfaces are designed to permit a variety of intended uses for PCTs that have been defined in other publications (see references in Annex D).  To the extent possible, this document strives to be upward compatible with related efforts underway (e.g. the Joint CA IOU PCT effort) that intend to construct extended capabilities on the Title 24 foundation. Upward compatibility will be facilitated by not specifying any capability or feature that can be foreseen to contradict or impede the clear direction of those related efforts.

The reference design specified in this document is compatible with the architectural principles set forth in the CEC PIER Strawman Reference Design for Demand Response Information Exchange.

## The Title 24 PCT Code Language (Rev 29f)

This Reference Design document is guided principally by the content of Title 24 (rev 29f / final draft), the California legislative code defining mandated use of Programmable Communicating Thermostats (PCTs).

The following is a summary of requirements affecting PCT product design and use that this Reference Design document has interpreted from Title 24.  The full text of Title 24 appears in Annex E.

- PCTs shall provide a customer-settable temperature setpoint for heating and a customer-settable temperature setpoint for cooling (as applicable to the local HVAC capabilities) for each of four or more time periods spanning each 24-hour day.  These settings, in conjunction with customer use of other supplier-determined features and options, will determine how the thermostat operates in the absence of price events and emergency events.

- PCTs shall provide a customer-settable temperature offset for heating and a customer-settable temperature offset for cooling (as applicable to the local HVAC capabilities). The appropriate offset shall be used by a PCT to make a temporary adjustment to the prevailing, customer-programmed temperature setpoint during price events, unless an event is specifically overridden by the customer.

PCTs shall be shipped with default offsets of +4oF for cooling and -4oF for heating. These shall also be reinstated anytime a device reset occurs. These default offsets shall remain in effect until the customer changes the settings.

- PCTs shall provide a clock mechanism for coordinating transitions of temperature setpoints, responding to events, and measuring delay times.

- PCTs shall provide a non-removable communications capability that is compatible with the default statewide Demand Response (DR) communications system (to be determined).  The default communications system will be one-way, whereby utilities issue messages to PCTs. Utilities shall use the default communications system to notify customer PCTs about price events and emergency events.

A price event is issued when energy supplies become tight when compared with energy demand.  Each customer PCT receiving a price event may use the pre-programmed temperature offset (described above) to lower energy usage for the event’s duration.  In such cases, the PCT uses the temperature offset to temporarily adjust the prevailing temperature setpoint (described above).  A customer is allowed to selectively override individual price events, so that no adjustment in operation is made.  Price events last for a specified period of time, which may vary for individual events, unless cancelled by the utility before that time has expired.  Once a price event has expired or is cancelled, the PCT shall continue enforcing the event constraints on temperature for a random period of time ranging from 0 to 30 minutes.  This eases system recovery.  In the future, once a smart meter has been installed at the customer’s premises, energy charges may be raised during price events to reflect higher energy costs that the utility must pay to increase energy supply.

An emergency event is issued when energy system reliability problems require a curtailment of residential energy use through temporary adjustment of thermostat settings. Emergency events may be used to either impose a utility-specified temperature setpoint or impose a utility-specified temperature offset to the customer’s prevailing temperature setpoint.  Customers and their PCTs must involuntarily comply with these directives, and customer-initiated changes to thermostat settings are not allowed to go into effect while an emergency event is in progress.  Emergency events last for a specified period of time, which may vary for individual events, unless cancelled by the utility before that time has expired.  Once a price event has expired or is cancelled, the PCT shall continue enforcing the event constraints on temperature for a random period of time ranging from 0 to 30 minutes.  This eases system recovery.

- PCTs shall provide capability for the installer (or user) to enter some input to the PCT during or after installation to establish addressing. The required input could be a character string provided by customer service that locates the PCT within the system and establishes desired programming options.  It’s also possible that such inputs could be provided through a memory card inserted into the PCT’s Expansion Port.

- Aside from the default communications capability, PCTs shall provide three other interfaces as described below:

HVAC Interface: This interface provides connection to 24 Vac power (for the PCT) and connections to HVAC equipment controlled by the thermostat.  The minimum interface is a standardized, 9-position terminal block. It must support heat pumps with resistance heat strips and a reversing valve in both residential and small commercial units.

Expansion Interface: This shall be an industry-standard interface. Insertion of a utility-specific communications module shall disable the default statewide communications hardware built into the PCT until the module is either removed or no longer receives a signal. This interface may be used for other purposes as well, such as additional memory.

Human-Machine Interface: This interface provides display and control capabilities supporting customer-interaction. Customers require it for (a) entering thermostat and time settings, (b) viewing event information, communications status, and maintenance-related information, and (c) using other features provided by the PCT supplier.

- Certain specified types of HVAC equipment are not required to comply with Title 24. Consult the full Title 24 text in the annex, referencing Exceptions 1 and 2 to Section 150(i).

## The Virtual Operation Model for Thermostats

The virtual operation model for thermostats is an operational representation of a class of devices used to monitor, control, and automate the operation of external heating, ventilation, and air conditioning (HVAC) system components. It is virtual in the sense that it represents the functional resources and behavior required of such devices without prescribing any particular form of implementation. That said, compliance with specific standards may be necessary to meet regulatory or interoperability requirements.

Because there is a wide range of product possibilities and expectations, a virtual operation model (VOM) for PCTs needs to be developed around a core statement of requirements. For this document, that statement is framed by the CEC’s Title 24 Code Language for PCT devices. The result is called the Title 24 PCT VOM (Virtual Operation Model for Programmable Communicating Thermostats Compliant with Title 24-2008).

An integral part of the VOM for PCTs is an abstract description of the essential human interface characteristics required by Title 24 code. As long as they conform to these characteristics and the other VOM requirements, suppliers may design their PCT products with confidence, providing any additional features they choose. The only remaining prerequisite is that the VOM be accepted by the user and supplier communities. Finally, note that the VOM may also be used as a tool for developing an information model to support data communications, if appropriate.

It is expected that this model can and will be expanded in a consistent manner (as specified in a separate document) to meet the objectives set forth by the Joint CA IOUs. Those objectives envision use of two-way communications in lieu of the one-way communications specified by the Title 24 requirements.

Beyond complying with this model, suppliers are free to extend their designs in any manner they see fit. Users, on the other hand, will be free to choose the products that best meet their needs.

The Title 24 PCT VOM is described in the two subsections that follow.

### Required Functional Resources

The following PCT functional resources are either implicitly or explicitly required by the Title 24 PCT Code Language (refer to Section 1.1):

- A default, non-removable, one-way communications device that is compatible with the statewide DR communications system (to be determined).

- An industry-standard Expansion/Communication port.

  - This port is available to be used by either a memory module or a module supporting two-way communications with the statewide DR communications system (to be determined). Refer to Section 3 for more information.

- An industry-standard display facility that shall be used to display the following:

  - The current communications status, indicating whether status is normal or abnormal (always displayed).

  - The type of event in progress: Emergency event, price event, or no event (always displayed).

  - Maintenance-related information: Icons and/or error codes (always displayed).

  - The current temperature (always displayed)

  - Thermostat settings (under customer control)

  - Hex character strings (as they are entered by a customer or installer to represent the PCT’s system address, elected DR options, and possibly a public security key). Such strings may be 26 characters long (perhaps extended to 28 for convenience); it is recommended that these strings be broken into 4 character fields separated by spaces to aid readability and verification.

- One or more setting mechanism(s) that allow a customer to change the following thermostat settings at any time except during emergency events:

  - A temperature setpoint and associated starting time 
(used during normal operation).

The PCT shall provide a separate pair of parameters for at least four operating periods that collectively govern thermostat operation during the 24-hour day.

  - Temperature offsets (used during price events)

The PCT shall provide one price-event offset for heating. The PCT shall be shipped with a default value of -4oF. Only negative values are allowed.

The PCT shall provide one price-event offset for cooling. The PCT shall be shipped with a default value of +4oF. Only positive values are allowed.

- An entry mechanism for hex character strings, used to represent the PCT’s system address, elected DR options, and possibly a public security key.

- A clock mechanism that allows the PCT to execute temperature setpoints scheduled by the customer and to respond to events.

- A data entity representing the currently sensed temperature.

### Required Functional Behavior

The following describes how the PCT needs to behave and use the functional resources specified above to comply with Title 24 requirements.

- One-Way Communications Device

The PCT shall receive incoming messages from the statewide DR communications system through its one-way communications device. The PCT shall follow the instructions in those messages to perform temperature control during price events and emergency events.

  - A PCT shall be addressable by utility, area, substation, feeder, billing point, or demand response (DR) program.

  - A PCT shall automatically disable operation of the default, one-way communications device if a communications module occupies the Expansion Interface and the PCT detects a received communications signal.

- Clock Operation

The clock mechanism enables the PCT to execute temperature setpoints scheduled by the customer. It also supports other timing functions (e.g. start- and stop-time coordination for events; delay measurements after events expire).

Accuracy to a precision of one minute is acceptable for this operating environment and the applications being considered.

The PCT clock may be set and resynchronized by two means: (1) through system communications messages and (2) by the customer, using the PCT’s human interface. Such action by either source will override a prior setting, regardless of which source set it. So in practice they override each other, an approach that serves the needs of the system and the customer in a balanced way. Either method may be used at any time, although the system will likely do so infrequently, one to four times a day. One system update time should be 2 AM, as that is frequently the official time used for changes to and from daylight-savings time.

The system may also elect to update PCT clocks just prior to an event and perhaps at intervals during an event, to prevent customers from gaming the system.

- Normal Operation

Normal operation is defined to be the PCT’s prevailing mode of operation as determined by the customer’s prior settings and use of features provided by the PCT vendor’s design. Aspects of normal operation may be modified or interrupted while price events or emergency events are in progress, but only to the extent required by those events.

To the extent such actions are not prohibited by event requirements or the PCT vendor’s design, a customer may change PCT settings or use other features of a PCT vendor’s design during an event. Those changes may alter what is considered to be the prevailing mode of operation when an event is terminated and the PCT returns to normal operation.

The PCT is mandated to provide a mode of operation whereby it controls temperature by following the scheduled temperature setpoints. Because price events and emergency events use this mode, the PCT shall require the customer to provide initial settings for temperature setpoints covering the full 24-hour day and temperature offsets (heating and cooling, as applicable) before PCT operation is allowed to commence. This requirement shall be re-imposed following any loss of PCT settings.

- Price Events

Upon receiving a price-event signal, the PCT shall normally adjust the currently applicable temperature setpoint by the number of degrees indicated in the temperature offset (heating or cooling, as appropriate) for the duration of the event.

Exception: Title 24 allows a customer to override any individual price event through use of an override function provided by the PCT vendor’s design. If so used by a customer, the override shall be reset when the PCT returns to normal operation.

Summarizing, price events only constrain the operating range of the thermostat. They do not otherwise affect the operation and use of features provided by the vendor’s design.

When the price event expires, the PCT shall return to normal operation after a delay. The delay shall randomly occur between 0 and 30 minutes, determined by a process that yields a uniform distribution of return times for a large number of PCTs.

- Emergency Events

Upon receiving an emergency signal, the PCT shall respond to commands contained in the emergency signal, including (a) adjusting the PCT’s currently applicable temperature setpoint with a signal-specified offset or (b) overriding the PCT’s currently applicable temperature setpoint with a signal-specified temperature setpoint.

A PCT vendor’s design may allow customers to specify new thermostat settings (i.e. temperature setpoints and temperature offsets) during emergency events, but the new settings shall not take effect until the PVT returns to normal operation. In such cases, it is the vendor’s responsibility to determine how prevailing and pending settings are displayed.

Protective rules for remotely operating thermostats:

- For heating, a PCT shall ignore an emergency signal that specifies a temperature setpoint higher than the prevailing temperature setpoint entered by the customer.

- Similarly for cooling, a PCT shall ignore an emergency signal that specifies a temperature setpoint lower than the prevailing temperature setpoint entered by the customer.

- Any temperature offset provided by an emergency signal shall be specified as an unsigned value and always interpreted by a PCT as a change to the prevailing temperature setpoint in the direction that saves energy, regardless of whether heating or cooling mode is in effect.

This deals with the situation where some PCTs receiving an emergency signal are heating and others are cooling, particularly where the PCTs reside in different microclimates.

- Additionally, thermostats shall not be remotely set above (TBD)oF or below (TBD)oF. This measure protects customer premises from extreme temperatures that might otherwise be imposed using emergency offsets, should the customer already have a very high or low temperature setpoint in effect.

Summarizing, emergency events only constrain the operating range of the thermostat and prevent the customer from putting new thermostat settings (i.e. temperature setpoints and temperature offsets) into effect while an event is in progress. They do not otherwise affect the operation and use of features provided by the vendor’s design.

When an emergency event expires, the PCT shall return to normal operation after a delay. The delay shall randomly occur between 0 and 30 minutes, determined by a process that yields a uniform distribution of return times for a large number of PCTs.

# The HVAC System Interface

The physical connector on the PCT to be presented to the HVAC system shall be one or two industry standard screw terminal block headers for direct control applications.  Future versions of this reference design will require a new connector design allowing easy installation/removal by the end user.  Alternatively, a PCT may present a digital interface.  The following sections describe each interface.

## Minimal Direct Control Interface

The PCT is required to support at least one 5 terminal connector for basic HVAC and heat pump systems.  The terminal numbering and definitions for this connector is shown in Table 2-1.  The terminal designations are from NEMA DC 3-2003.

Table 2-1: Terminal Block 1 - Basic Thermostat Terminal Mapping (Required)

| Term # | Signal Name | Normal Color | Notes |
| --- | --- | --- | --- |
| 1 | (Conventional) Y: Cooling | Yellow | Conventional - First stage cooling Heat Pump - First stage compressor. Will heat and cool based on the output of terminal 2 - O/B |
|  | (Heat Pump) Y: Compressor |  |  |
| 2 | (Conventional) W: Heating | White | Conventional - First stage heating Heat Pump – Configurable option to energize the terminal for cooling (O option) or heating (B option) |
|  | (Heat Pump) O/B: Compressor |  |  |
| 3 | G: Fan | Green | Fan switch on thermostat or on a call for cooling or heat pump |
| 4 | C: 24 Vac Common | Black | 24Vac transformer neutral |
| 5 | R: 24 Vac Power | Red | 24Vac transformer power. In a two source transformer installation, this terminal becomes Rh. |
| 6 (opt) | Rc: 24 Vac Power | Red | OPTIONAL. Cooling transformer power for two source transformer installations. This terminal can be tied to terminal #2 in single transformer installations. |

## Advanced Thermostat Direct Control Interface

Thermostats designed to support advanced HVAC systems such as multi-stage configurations will support a second terminal block. The terminal numbering and definitions for this connector are shown in Table 2-2.  Note that the terminal numbering starts with 7 to minimize confusion with the mandatory terminal block. This will also facilitate use of a single, standardized connector in the future.

Table 2-2: Terminal Block 2 - Advanced Thermostat Terminal Mapping (Optional)

| Term # | Signal Name | Normal Color | Notes |
| --- | --- | --- | --- |
| 7 | (Conventional) W2: Second Stage Heating | Various | Conventional - Second stage heating Heat Pump – Auxiliary and emergency heating control relay. |
|  | (Heat Pump) Aux/E: Auxiliary Heating |  |  |
| 8 | Y2: Second Stage Cooling | Blue or Orange | Second stage cooling for both Conventional and Heat Pump configurations |
| 9 | L: Equipment Fault | Various | Installed as an input based on equipment type. When configured as in input, activation of the external generated signal informs the user via icon or LED enunciation, that the heat pump system is not available. Installed as an output based on equipment type. This output is used to “inform” zoning equipment that the system is in emergency heat mode. In this situation the secondary piece of equipment (zoning panel) will disable a call for heat pump. |
| 10 | (Conventional) W3: Third Stage Heating | Various | Conventional - Third stage heating Heat Pump – Second stage auxiliary heating |
|  | (Heat Pump) Aux2: Second Stage Auxiliary Heating |  |  |

Note that the optional connector may be extended in a vendor-dependent manner to support additional functionality.  These terminals should use industry standardized designations, if appropriate, from those defined in Table 2-3 below.

Table 2-3 – Terminal Markings for Low-Voltage Class 2 Controls3

## Digital Control Interface

This interface definition is preliminary and advisory only.  It is anticipated that it will be defined in more detail in future revisions of this document.  This interface supports 48 VDC power and balanced, full duplex serial transmission.  The precise uses of these serial lines are PCT vendor specific at this time.  Vendors should consider using IEEE 802.3af Power over Ethernet standard in Mode B.  An example of this configuration is shown in Table 2-4.

Table 2-4 – Power over Ethernet Interface

| RJ45 Pin # | Wire Color (T568A) | Signal | PoE |
| --- | --- | --- | --- |
| 1 | White/Green | Transmit+ | Mode A + |
| 2 | Green | Transmit- | Mode A + |
| 3 | White/Orange | Receive+ | Mode A - |
| 4 | Blue | Unused | Mode B + |
| 5 | White/Blue | Unused | Mode B + |
| 6 | Orange | Receive- | Mode A - |
| 7 | White/Brown | Unused | Mode B - |
| 8 | Brown | Unused | Mode B - |

# Expansion Interface

The expansion interface shall be available to extend the communication capabilities of the thermostat as well as to provide an external means of memory storage / logging.  The physical interface (Figure 1) shall be implemented by using the Multi-Media Card (MMC) format as defined in the MMC System Specification Version 3.31.  The logical interface shall utilize the Serial Peripheral Interface (SPI) standard as defined in the MMC System Specification version 3.31). The MMC System Specification indicates that the SPI is optional for MMC devices, but it will be mandatory for the PCT Expansion Interface. PCT manufacturers may optionally support other physical and logical interfaces that provide backwards compatibility with the MMC version 3.31. Examples are MMC version 4.1 and SDIO version 1.1.

Figure 1 MMC Interface and Card Examples

The interface shall be capable of recognizing whether a communications network interface MMC card or a memory card has been placed in the Expansion Interface.   It shall also be able to identify which type of communications interface is installed.

If a communications MMC card has been inserted and found to be valid and operational by the PCT, this interface shall be used in lieu of the internal, default, one-way communications capability in the PCT itself.  Regardless of whether communications takes place over an internal or external interface, the communications shall take place in accordance with the specifications set forth in section 4. Communications Interface.

Table 3-1 – MMC Pin assignment for SPI Mode4

# Communications Interface

The overall architecture of the PCT is designed to be compatible with the architecture defined in the CEC demand response reference design mentioned earlier.  The architectural framework for this Demand Responsive Infrastructure (DRI) is depicted in the CEC report using the figure replicated here as Figure 2.

Figure 2  DRI Function Services Framework

The architecture separates the physical infrastructure (e.g. a wireless network) from the applications (e.g. the logical information model of the PCT and the functions it performs) via a service model.

The physical communications interface is has two components – a mandatory, internal interface supporting a widely available wireless communications technology such as the US Radio Broadcast Data System (RBDS) standard; or an optional one- or two-way communications interface connected through the Expansion Interface as selected and specified by a load serving entity.

## Logical Information and Transaction Model

This section defines the logical attributes and transactions that are necessary to represent and alter the internal state of the PCT.  This model determines how the PCT behaves when attributes are read or updated, describes the meaning of those attributes, and specifies the sequences of events (transactions) necessary to support the desired functionality.  The model is capable of exposing all of the attributes and functionality that can be achieved through direct interaction with the PCT’s local human interface. The essential human interface requirements are described by the Virtual Operation Model (VOM) in Section 1.2.

This section will represent the static portion of the information model (i.e. its attributes) using the Extensible Markup Language (XML).  The semantics of this model are derived from numerous existing standards and industry agreements in an effort to be as consistent and compatible with existing technology and implementations as possible.  Note that for all communications interface implementation profiles other than the mandatory RBDS system, the XML representation of the model is a logical representation only (i.e. it only defines the information exchanges; not the actual form of the exchange itself).

The transaction aspects of the information model are represented by UML activity diagrams to illustrate the transaction sequence that must occur to carry out specific functions of the PCT.

## PCT Functions

This section enumerates the minimum functions to be carried out by the PCT.

Programmability – The PCT shall support at least a weekday and weekend schedule (5-2 schedule) and each schedule shall have at least four programmable periods (typically morning, day, evening, and night). The schedules and time periods shall be independent for heating and cooling modes of operation unless the PCT is operating in a dual operation mode.

Communications – The PCT shall support messages from Section 4.3.3 to enable CEC Title 24 compliance using one-way communications.

## PCT Messages and Attributes

This section describes the messages and associated data payloads necessary to implement the functionality of the PCT as described in CEC Title 24 PCT specifications (revision 29f) while being upwardly compatible with the joint IOU PCT business requirements (revision 7).

Each of the documents describes different sets of messages.  The CEC Title 24 PCT specification is used as the base document for the purposes of describing the minimum functionality of a one-way DR system.  The functionality described in the Joint IOU PCT document extends the Title 24 requirements to include usability features which can increase the response to calls for short-term energy conservation.  Proposed messages necessary to support additional functionality are included as an informative annex to this document.

If a message is received and validated, but it conflicts with a prior message, the newer message is executed and any continuing action for the prior message is automatically terminated by the PCT.

### Event Modes

The PCT specifications recognize the following two basic system event modes:

- Price Events, which can be overridden by the customer

- Emergency Events, which may force an involuntary reduction in load.

In order to facilitate future changes in tariffs and regulations, the messages and data payloads that support these events have been designed to provide sufficient flexibility and information to handle such changes. To provide this flexibility, while ensuring consistency, several common data classes are defined below. These data classes are used by most messages for addressing, event identification, and time stamping.  Event ID’s are particularly important, because they are used to cancel events and to allow multiple event transmissions for message-transport reliability purposes.  The addressing scheme may be used to enable regional or even PCT-level control resolution.

#### Price Events

Initially, it is foreseen that a utility will wish to send a signal that indicates that a super peak rate period is in effect. The utility may wish to simply send a message that a peak price is in effect or send an explicit price.  The price event message defined below specifies a start and stop time for which the price event is in effect as well as the price itself.  If the price field is set to zero, then this is a generic super-peak event with no specific price.  The customer’s PCT will have a default response to receiving a price event, but the owner may override that programming. PCT vendors are free to provide whatever flexibility they desire in allowing the owner to respond to the event alone or to the event and price.

#### Emergency (Grid Reliability) Events

This event class allows the utility to issue specific directives to the PCT in order to address a grid reliability situation.  These events provide a start and stop time as does a price event which allows them to be scheduled in advance.  There are two flavors of the basic reliability event – change temperature and set temperature.  Basically this allows the utility to specify an arbitrary temperature increase or decrease from the PCT’s current setpoint or simply specify a specific set point.  The ability to specify an explicit setpoint is required by Title 24 to avoid the situation where customers change the setpoint just prior to the start of a reliability event in order to “game” the system.

### Common Data Classes

All of the defined messages below make use of one or more common data classes.  These common classes (types) are used to represent addressing information, date time stamps, and other common information.

Addressing <ADDR>

| Common Addressing Information <ADDR> |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Source Utility | INT8U | Identifies the utility / DisCo that controls the PCT (Ex: 5=SCE) | M |
| DR Program | INT8U | Demand response program identifier (Ex: 3=CPP, 1=non-curtailable) | M |
| Area / Sub Ident | INT16U | Locates customer (Ex:0=ALL, 1..999 identifies an ‘area’, 1000 up identifies a substation) | M |
| Feeder Identifier | INT8U | Feeder number within a substation (0 = all feeders, 1..N = feeder) | M |
| Billing Point Ident | INT64U | Identifies individual customer | O |

Note: This addressing scheme may be updated to coordinate with IPV6 terminology and be suitable for use as a subset of a valid IPV6 address.

Date/Time Stamp <DTIME>

| Common Date/Time Information <DTIME> |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| NTP_Seconds | INT32U | Seconds since 0h January 1, 1900 UTC | M |
| NTP_Fraction | INT32U | Fractional seconds | O |

Note:  All time stamps are in Universal Coordinated Time (UTC) using the SNTP Version 4 format as defined in RFC 4330.  SNTP uses the NTP timestamp format which is represented as a 64-bit unsigned fixed-point number, in seconds relative to 0h on 1 January 1900. The integer part is in the first 32 bits and the fractional part in the last 32 bits. In the fractional part, all bits should be set to 0.

Message Identification <MSG_ID>

| Common Event Identifier <EV_ID> |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | INT16U | Used to uniquely identify each message and prevent replay. | M |

Event Identification <EV_ID>

| Common Event Identifier <EV_ID> |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Event_ID | INT16U | Used to provide a single, unique event identifier for all messages associated with the same event. Cancellation events will reference this ID. | M |

Event Price <PRICE>

| Common Event Identifier <EV_ID> |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Event_Price | INT16U | $ / KWH * 0.0001 (Ex:2000 = $0.20 / KWH) | M123 |
| Event_Price_Ratio | INT16U | Event price is normal price x this_value / 100 (i.e. 200 means 2x price) | M123 |
| Event_Price_Tier | INT8U | Indicator of relative price (ex:1=normal, 2=high, 3=very high, >1000 is a Tier ID) | M123 |

Note:  One of the three M123 elements is mandatory

Cryptographic Hash Value <CRYPTO>

| Common Crypto Hash Value <CRYPTO> |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Function ID | INT8U | 1=SHA-1 (FIPS 180-2), 2=SHA-224, 3=SHA-256, 4=SHA-384, 5=SHA-512 | M |
| Hash_Value | INT512U | 160 bits for SHA-1 hash value, etc. | M |

Note:  The use of the cryptographic hash is optional in all messages in this reference design but may be made mandatory in the future.

### Message Commands for Minimum Title 24 PCT Functionality

Clock Set Command

| Clock Set Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | Clock set command (ex: 1) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Now | <DTIME> | Present time (Universal Coordinated Time – UTC) | M |
| DST_Next | <DTIME> | Time of next DST/SummerTime shift (ex:2006 302 7200) | M |
| DST_Offset | INT8S | Number of minutes (ex: -60 for USA change away from DST) | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Price Event Command

| Price Event Notification |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 2) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Start_Time | <DTIME> | Event begin time | M |
| Stop_Time | <DTIME> | Event end time | M |
| Event_ID | <EV_ID> | Identifier of this price event (used for cancellation) | M |
| Event_Price | <PRICE> | One of three possible price options – see <PRICE> | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Price Schedule Command

| Price Schedule Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 23) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Number_of_Prices | INT8U | number of triple entries | M |
| 1st_Price | <PRICE> | One of three possible price options – see <PRICE> | M |
| 1st_Start_Time | <DTIME> | Time that this price become effective | M |
| 1st_End_Time | <DTIME> | Time that this price is no longer effective | M |
| 2nd_Price | <PRICE> |  | O |
| 2nd_Start_Time | <DTIME> |  | O |
| 2nd_End_Time | <DTIME> |  | O |
| …. |  |  | O |
| Crypto | <CRYPTO> | Message integrity value | O |

Change Temperature Command

| Change Temperature Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 5) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Start_Time | <DTIME> | Event begin time | M |
| Stop_Time | <DTIME> | Event end time | M |
| Event_ID | <EV_ID> | Identifier of this price event (used for cancellation) | M |
| Temp_Change | INT8U | Amount to change setpoint in 0.1 degree Celsius | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Note:  Setpoint change sign is not specified – the thermostat knows which direction to change based on current mode for energy savings. Some PCTs receiving the message may be in heating mode while others are in cooling mode, particularly where the PCTs reside in different microclimates.

Set Temperature Command

| Set Temperature Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 6) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Start_Time | <DTIME> | Event begin time | M |
| Stop_Time | <DTIME> | Event end time | M |
| Event_ID | <EV_ID> | Identifier of this price event (used for cancellation) | M |
| New_Temperature | INT16U | New temperature setpoint, in tenths of a degree Celsius | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Display Message Command

| Display Message Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 7) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Message Length | INT8U | Number of characters in message | M |
| Message | STRING[n] | Message to display on display | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Cancel Event

| Cancel Event |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 9) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Event_ID | <EV_ID> | Identifier of this price event (used for cancellation) | O |
| Crypto | <CRYPTO> | Message integrity value | O |

Keep Alive

| Keep-alive Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 21) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Crypto | <CRYPTO> | Message integrity value | O |

## PCT Transactions

This section describes the transaction sequence necessary to implement the PCT functions defined in section 4.2 using the attributes defined in section 4.3.

Figure 3  One-Way Critical Peak Price Event

Figure 4 One-Way Emergency Events

## Implementation Profiles

An implementation profile for a communications interface describes how the logical information models and transactions necessary to support it are actually implemented using a specific standard via the enabling services layer.  The logical information models specify the attributes that can be read and written from the PCT and their expected behavior when transactions occur.  The implementation profiles define the details of how the underlying protocol is used to implement the model, services, and transaction model.  This reference design does not specify a particular implementation profile – this is described in a separate CEC publication.

## Security

The PCT system will be a large and valuable asset to the state of California.  In order to ensure the system is able to perform in the intended manner for the long term, protective measures must be engineered into the solution from the beginning.  A defense-in-depth strategy leveraging risk management techniques is described herein, including recommendations regarding the appropriate deployment of security mechanisms at all levels to maximize effectiveness.

### Fundamental, Strategic Objectives

The PCT system must be designed to resist attacks, prove resilient in the face of attack, and allow for expedient and effective recovery from attack.

- Resistance

Security measures must provide the system with a robust means to resist attacks.  The foremost priority in this regard is to protect the ability to access and control the operation of PCT devices. Loss of access and control poses a huge risk to operational integrity and further risk of incurring large remedial costs.

- Resilience

Security measures must provide the system with a means to withstand and respond to attacks.  The foremost priority in this regard is to limit damage and loss if PCT access or control is compromised.  Minimizing damage and loss is of benefit to system effectiveness as well as public safety.

- Recovery

Security measures must provide the system with a means to recover from attack.  The foremost priority in this regard is the recovery of PCT access or control in the event of compromise.  The ability to quickly regain confidence in the safe and reliable operation of the system as intended is of paramount importance.

### Assumptions

The following constraints are assumed in considering security solutions for the PCT system:

- Human Factors

Although sophisticated technology can be applied to realize security objectives, the largest security risks are posed by inadequate or compromised security procedures within the responsible human organizations.  Accountability and safeguards are essential at every level of the human security structure to avoid compromising critical system information (e.g. cryptographic keys).  Organizational lapses can result from carelessness, negligence, complacency, poor judgment, poor human communication, inexperience, ignorance, collusion, and revenge, not to mention bribery, blackmail, and coercion.

- Practical Recovery

Security measures must be built into the PCTs and the head-end system from the beginning, anticipating different kinds of loss and appropriate system responses. Viable approaches cannot include travel to customer sites.  Should recovery prove impossible for even a moderate number of PCTs (say 1,000), the replacement/repair costs and negative publicity are likely to be prohibitive.

- Security Priorities

Of the four major communication security issues - availability, integrity/authenticity, confidentiality, and non-repudiation - the PCT system needs to focus first on authentication of message senders and second on the integrity of the message.  For the one-way (broadcast) system, availability is a lower priority since lost messages can be repeated, and confidentiality is not a priority at all. While cryptographic measures may be used in support of authentication mechanisms, encryption is not necessary for confidentiality purposes.  Non-repudiation may need to be addressed to the extent of  preventing customers from simply claiming their equipment was malfunctioning during an event.

- Distribution Channels

PCTs may be distributed through manufacturer, utility, or retail channels. Each approach can pose distinct advantages and drawbacks, spanning a range of security considerations.

The first impact of this range of distribution mechanisms is that the installation process for the PCTs must be kept as simple as possible.  Manufacturing workers, home contractors, and customers cannot be expected to have security expertise.  Nor can they be reasonably expected to read a manual for this product.

The second issue is that cryptographic materials associated with individual PCTs or groups of PCTs must be handled in a procedural manner.  The process must protect critical, complementary pieces of cryptographic material from ever being exposed to the same person or stored in a common location.

To the extent possible, PCTs should be manufactured and distributed as part of multiple groups that have unique security credentials. This approach will lessen the risk associated with any single point of compromise.

- Feedback

Even when using one-way communications, utilities may benefit from PCT feedback when malfunctions or potential threats arise.  PCT manufacturers can be encouraged to employ software techniques that recognize certain kinds of communications attacks. These in turn can invoke defensive measures to ignore questionable commands or prompt customers to report associated error codes through an automated phone system. The information reported from an incident might include the following, although a lot of this information could be captured during the PCT registration process at time of installation:

  - PCT model number

  - PCT serial number

  - Customer’s name

  - Customer’s zip code

  - Customer’s phone number

  - Error code

  - Date and time of occurrence (tagged by the PCT)

### Risk Management Approach

Security for the PCT system should be evaluated using a risk management approach.  Such an approach includes:

- Delineating assets to be protected, including their relative value and their sensitivity to attack.

- Identifying threats, including their possible source, intent and strength.

- Enumerating vulnerabilities, including their possible frequency and serverity.

- Mapping specific threats through vulnerabilities to assets

- Determining appropriate mitigation techniques

The following sections illustrate how this approach was followed.

### Possible Attacks

To determine the assets, threats and vulnerabilities of the PCT system, the task force considered several scenarios. These scenarios fall into several categories depending on the communications layer affected:

The task force has identified the following scenarios for possible application layer attacks:

- Attacker turns on all air-conditioning units, causing a sudden, excessive, unexpected load, possibly leading to blackouts or grid instability.

- Attacker recalls an authentic emergency signal, preventing the required reduction in load and forcing utilities to take other measures such as blackouts or buying energy at higher costs.

- Attacker shuts down all air conditioning units, causing annoyance and possible health concerns among some customers.  Would be of more concern in states with more severe weather conditions.

- Attacker downloads new software into the PCT or the PCT communications module.  This attack will be nullified on the Title 24 PCTs by simply not acting on these messages if they come over the broadcast network.

- Attacker sends false acknowledgements.  Not an issue on the broadcast network.

- Attacker issues false time synchronization, potentially causing events to occur sooner or later than they normally would have.

- Attacker causes false messages to appear on the thermostat display, misleading customer and perhaps causing incorrect behavior that could affect load or cause overload of utility customer service, e.g. “Please call utility now.”

- A customer decreases the air conditioner setpoint prior to an expected event, or changes the time locally, causing air conditioning to run normally during the event.

The task force has identified the following scenarios for possible network or transport layer attacks:

- Attacker takes control of head-end radio system through the initiating organization’s internal network or its interfaces with third parties.

- Attacker causes denial of service by flooding the head-end IP network with acknowledgements (from the two-way IOU networks) or other valid messages.

- Attacker intercepts wireless messages.

The task force has identified the following physical layer attacks:

- Attacker jams or sends false messages from a ground station or vehicle, affecting a limited number of thermostats

- Attacker jams or sends false messages from a balloon or other aircraft, increasing range of the attack.

- Customer disables thermostat antenna.

Figure 5 summarizes the goals, threats, type of attack, and mechanism for each of these scenarios.   In doing so, it maps the threats through vulnerabilities to the system assets as discussed above.

Figure 5 – Summary of Possible Attacks on the PCT System

### Non-Cryptographic Mitigation Methods

The task force determined that these threats were most effectively addressed through a comprehensive defense-in-depth approach, as illustrated in Figure 6.

Most modern information systems tend to focus on the use of cryptography as the primary defense against attacks.  However, cryptography is only one possible mitigation technique.  The unique design, characteristics, and constraints of the PCT system provide opportunity to leverage several non-cryptographic techniques.  The principles involved in these techniques include:

- Using time as an ally, slowing the capability of an intruder to use PCT resources

- Limiting the allowable behavior of the PCT to prevent it from performing actions that, while theoretically possible, would never be used for beneficial purposes in actual practice.

- Relying on detection as well as prevention mechanisms as deterrents.

Figure 6 – Mitigation Measures for the PCT System showing Defense-in-Depth

#### Business Logic

- Thermostats shall not accept remote commands to increase energy usage except the cancel event message, discussed below.

- Thermostats shall have hard-coded limits on what setpoints will be accepted via remote commands, to prevent unsafe setpoints.

- Thermostats shall randomly delay for up to 30 minutes after being instructed to normally end or cancel an energy reduction event, avoiding sudden increases in load on the grid.  The display of the thermostat shall not indicate the end of the event until after the random delay.

- Thermostats will never automatically increase energy usage at the end of an event by any more than they originally reduced it.

- Time synchronization commands received via the remote network shall override any time set locally.

#### Detection and Environment

The working group has no authority over the transmission end of the network, but can only define a reference design for the thermostats themselves.    However, it has identified the following recommended security measures for the network as a whole, plus two detection requirements for the PCTs:

- Create an intrusion detection system for the broadcast network.  Such a system might consist of receivers spaced over the service territory that can compare the received broadcast messages with what was actually transmitted, and thus identify a false transmitter.

- Change the thermostat time frequently enough to reduce the effectiveness of time change attacks.

- Use historical energy usage data from the metering system to detect when a customer has disabled the thermostat’s antenna or is attempting to “game” the system.

- If private cryptographic material (e.g. a secret key) is stored for long periods of time in the thermostat, the thermostat must provide a tamper detection mechanism, e.g. per FIPS 140-2 standards.  This requirement would not apply if public keys are used since this information can be made freely available.

- Thermostats must include a non-modifiable, timestamped log of received messages.  An example of such a mechanism would be a non-volatile memory card inserted in the expansion slot.

### Message Content

Certain fields within the message may be handled in specific ways that will augment the security of the overall solution.  Two fields that are particularly relevant are the timestamp and message identifier.  The timestamp is necessary to link the message to a specific point in time, yet it can be easily accommodated (predicted) by an attacker wishing to inject an unauthentic message.  It is important that the message identifier cannot also be predicted in a similar fashion.  For this reason the recommended solution does not employ sequential message identifiers, but rather uses elements similar to the cryptographic nonce.

A cryptographic nonce is a value used only once, and is frequently either random or pseudo-random in nature.  By comparing the identifier of an incoming message to a list of previously received identifiers, the PCT can easily detect if an impostor is attempting to re-use a message at a later time.  While the PCT may not be able to store the identifier of every message it ever receives, it can easily store a significant number and scan them for duplicates upon receipt of a new message.  By establishing a range of valid message identifiers that is only slightly larger than the quantity stored in the PCT, one can ensure that it is difficult for an attacker to guess an unused identifier.  Thus, the difference in the size of the valid identifier range and the PCT store should be large enough to provide reasonable random or pseudo-random selection, but no more, as the ratio of unused to recorded quantities is directly reflected in the odds of an attacker guessing a valid (unused) identifier.

Together, the timestamp and the message identifier reflect information that will change from one message to another, regardless of message instruction.  By also removing predictable characteristics from the message identifier, the recommended solution forms the basis for strong resistance to replay attacks.  This defense is complimented by use of a MAC (message authentication code) or an HMAC (keyed-hash message authentication code).  These cryptographic techniques allow for easy detection of message manipulation, and present the attacker with a particular challenge in replicating the process to produce a plausible message.

### Cryptographic Mitigation Approaches

The task force originally considered two primary categories of cryptographic security solutions.  The first option that the task force considered focused around the use of asymmetric cryptography.  While this option was heavily favored among the cryptographic experts that the task force consulted, the option also depended upon the up-front definition of roles and responsibilities for all entities before key material could be generated and distributed.  The second option that the task force considered utilized a “secret-sharing” approach (also sometimes referred to as “key-splitting”) with symmetric algorithms.  This option alleviated the manufacturing / key material / distribution dilemma, but was less preferred from a cryptographic standpoint and not as efficient in regards to long term key management.

Ultimately, the task force devised a third solution which combined select features from each of the two previous options.  In short, the solution leverages the strength and key management advantages of the asymmetric approach with the organizational and logistical flexibility of secret-sharing.

(Note: It is assumed that authentication and integrity checking are provided through a Message Authentication Code (MAC) included in each message.  Alternately, the entire message could be encrypted for the same effect.)

#### Roles and Responsibilities

For the purposes of discussion the following terms shall be used to refer to the various entities involved in communication sequences:

| System Owner | The entity responsible for oversight and control of the entire PCT system. This represents the highest and broadest level of authority. Any messages from the System Owner to the PCT must go through the System Operator. |
| --- | --- |
| System Operator | The entity responsible for operation and control of a specific and defined geographic / service area. This entity will be responsible for sending messages to the PCT. |
| Manufacturer | The entity responsible for production of the PCT. This entity must have the capacity to build all required cryptographic capability into the PCT. |
| Installer | The entity responsible for placing the PCT in service within the home. This entity may or may not have technical training or expertise. |
| PCT | The Programmable Communicating Thermostat in the home. |

#### Concepts, Challenges, and Solution Approach

The general concept behind the recommended solution is to put a unique, random number into each PCT at the time of manufacture.  This number is subsequently used in the installation process to register the PCT, as well as facilitate the transmission of cryptographic key information to the device.  The recommended solution uses Elliptic Curve Cryptography (ECC), which represents a recent and powerful generation of asymmetric cryptographic algorithms.

Asymmetric algorithms utilize a set of mathematical formulas that are relatively easy to calculate in one direction, but feasibly impractical to calculate in reverse.  This is manifested by the use of two keys that are related, but not the same.  Information encrypted by one key can only be decrypted by the other key.  In the scenario of authenticating broadcast information, this allows the message to be encrypted or signed using a single, closely guarded private key, and then decrypted or verified using a freely available and copied public key.  The private key is at no practical risk of compromise from the public key due to the one-way nature of the relationship between the two – an attacker cannot feasibly calculate the private key even if they have unfettered access to the public key.  By simply being able to decrypt the message with the public key, the recipient verifies that the message must have come from the holder of the corresponding private key.

Figure 3 – Asymmetric Cryptographic Key Relationship

The primary challenge in the case of the PCT is the distribution of key material.  Cryptographic keys are represented digitally by a very long string of alphanumeric characters, and as such would be difficult to manually enter into a PCT by any practical means.  It would be relatively easy for the manufacturer to embed key material in the device, however in order to produce a public key one must also produce a corresponding private key.  This brings up the question of handling and storage of the private key.  Until the governing body defines exactly which entity shall be responsible for which role in the system and these entities are adequately prepared to handle cryptographic secrets, private keys may simply not be produced.  Thus, any practical solution must not depend upon keys being produced before distribution and deployment of PCTs may begin.

One particular cryptographic technique that may be employed to resolve such a dilemma is “secret sharing.”  This model uses the concept of dividing critical information up where no single entity possesses enough information by itself to re-construct the secret.  This can be applied to the PCT by placing a large random number in each thermostat along with an out-of-band communications channel for initialization / installation / activation.  The out-of-band communications channel could be a phone number or website where the Installer could achieve a sufficient level of confidence regarding the identity of the activating entity (either the System Owner or the System Operator).

#### PCT Registration Use Case

Primary Actor: Installer

Goal: Register a Programmable Communicating Thermostat with the Title 24 One-Way Broadcast System.

Stakeholders and Interests:

Installer: Wants confirmation of successful PCT registration with minimal time and hassle.

System Owner: Wants to have primary and backup public keys installed in the PCT.

System Operator: Wants to have public key installed in the PCT.  Wants to be able to place PCT in a specific operational group (e.g.: region, substation, neighborhood, etc…).

Initial Conditions:

- The PCT is physically located inside a residence and has yet to be activated.

- The Manufacturer has embedded a 160-bit random number in the PCT.

- The System Owner has primary and backup public/private key pairs, and is known to the System Operator.

- The System Operator has a public/private key pair, and is known to the System Owner.

- The Installer has access to the out-of-band communications channel.

Minimal Guarantees:

- PCT remains capable of being registered on the system.

- No private keys are compromised.

- The PCT does not have increased vulnerability.

Success Guarantees:

- PCT is capable of receiving price or emergency signals.

- PCT can determine signals are authentic.

- PCT can be re-registered.

- System Owner and System Operator may distribute new public keys to the PCT.

Trigger: Homeowner summons Installer to residence (or becomes Installer) for the purpose of installing a PCT.

Main Success Scenario:

- Installer retrieves random number from PCT.

- Installer contacts System Operator via out-of-band channel.

- Installer relays PCT random number to System Operator.

- System Operator relays PCT random number to System Owner.

- System Owner performs two XOR operations:

- With PCT random number and System Owner’s primary public key

- With PCT random number and System Owner’s backup public key.

- System Owner sends results of XOR operations to System Operator.

- System Operator performs XOR operation with PCT random number and System Operator’s public key.

- System Operator transmits registration signal including the labeled results of all three XOR operations to PCT.

- PCT performs XOR operation with its random number and each of the three result numbers received via registration signal, recovering three labeled public keys.

- System Owner encrypts activation message with System Owner’s primary public key.

- System Owner sends (encrypted) activation message to System Operator.

- System Operator encrypts activation message with System Operator’s private key.

- System Operator transmits (double encrypted) activation message to PCT.

- PCT decrypts activation message: first with System Operator’s public key; second with System Owner’s primary public key.

- PCT activates.

Figure 4 – Installation Message Sequence

#### Key Management

In comparison to other technological environments, the use of keys in the PCT system is very infrequent, and any direct monetary value is quite low.  Indirect value may be higher for certain malicious parties, although this is debatable and may not be evaluated without some degree of speculation and subjective assumptions.  However, due diligence dictates that a solution accommodate the possibility that keys may be compromised at some point.  Therefore, the solution described herein provides a moderate degree of risk mitigation by utilizing a three-tiered hierarchy of keys and minimizing the use (and exposure) of keys with greater authority.

In this design, the System Owner would possess two separate public/private key pairs – one primary and one backup.  The sole purpose of the backup public key would be to distribute a new primary public key in the event the original primary private key had been compromised.  If the primary private key is never compromised, then the backup private key is never used and may be kept in a secure location for the duration of the PCT program.  The primary keys shall be used by the System Owner to authenticate the public key of the System Operator, and to send authenticated system-wide messages (i.e.: emergency event).

For any single PCT, the System Operator will also have a public/private key pair.  These keys shall be used for all PCT communications, as the System Operator shall maintain control of the physical communications link to the PCTs.  Messages from the System Owner (utilizing the System Owner key as well) would be passed through the System Operator, and ideally would be kept to a minimum.  The System Operator keys shall actually be used alone for the vast majority of PCT communications.

The System Operator may, however, posses any number of public/private key pairs in total.  While there would be only one System Operator public key for a given PCT, the System Operator could maintain several sets of public/private key pairs representing the different operating regions, substations, or service territories, and assign a specific public key to a PCT accordingly at the time of registration/installation.

Figure 2 – Key Hierarchy

### Remaining Issues

An industry organization must be formed to complete this reference design and to choose an appropriate security solution.  The task force has decided that the following steps still need to be resolved:

- Finalize the appropriate algorithms to use.  While ECC is recommended for asymmetric algorithms, any necessary hashing or key wrapping algorithms are still to be determined.

- Finalize the number of levels and groups of keys.  It is desirable that multiple groups be defined and distributed among the thermostats so that the compromise of any given key may have a limited impact.

- Determining how often to change the time and/or send a heartbeat message.  These factors have an impact on installation.

# Human-Machine Interface

This section discusses the interface between humans and the PCT.

## Terminology

The task force agreed that at this point in the development of the PCT system, the only human-machine interface standardization required to support the Title 24 requirements is a clear definition of terminology.   All other standard features of the PCT are up to the discretion and innovative talents of the thermostat manufacturers.  NOTE: Minimum programming requirements shall meet the current Energy Star specifications.

PCT user interface and documentation shall use the following terminology.

| Reliability Event / Emergency Event | Refers to a Stage 1 Emergency or Stage 2 Emergency message from the utility. Upon receiving an emergency event, the PCT shall adjust its settings according to the Title 24 requirements. |
| --- | --- |
| Price Event | Refers to a change in pricing sent to the PCT from the utility. |
| Stage 1 Emergency | The lowest level of the emergency events. |
| Stage 2 Emergency | The highest level of the emergency events. |
| Critical Peak Pricing Event (CPP) | A type of price event. When a CPP is received by the PCT, the device should take appropriate behavior as defined by the settings configured by the customer. |
| Over-Ride | Refers to a person adjusting the functional behavior of the PCT to ignore a State 1 emergency message. Upon receiving a Stage 2 emergency message, a PCT shall act normally and ignore the Over-Ride setting. |
| Provision | Describes the commissioning or binding process of connecting a PCT to the wide area network or to an in-premise network. NOTE: This process depends critically on the data security solution chosen, as described in section 4.6. |
| Pending Event | Refers to a price event or emergency event that is scheduled but has not yet happened. |
| Active Event | Refers to a price event or emergency event that is underway. |

## Next Steps and Issues to be Resolved

An industry organization must be formed to complete this reference design and to discuss further possibilities for user interface standardization.  This section discusses some of those issues.

### Interaction with “Hold” Functions

There is some concern how the Emergency Events interact with temperature “hold” functions that may be implemented by some PCTs. A philosophy that has been suggested is that after all events are complete, the PCT should restore the state that existed prior to any of the events, including any “hold” settings.

### Recovery from “Off” State within an Active Event

The system must consider the person who comes home from a vacation and finds the home is at a high temperature because the system was OFF.  The person may find they are in a Stage 2 Emergency and cannot turn on any cooling.  It has been suggested that the PCT should permit cooling or heating to take place during an emergency event up to the setpoints associated with the event currently in progress.

### Standardization of Colors, Indicators, and Icons

Icons and symbols can provide a distinct advantage over text, because they have the power to instantly convey an associated meaning and to overcome language barriers. Overuse of symbols and color, however, can create more confusion than clarity. Suppliers and users would benefit greatly from adoption of common usage.

Typical uses of symbols and icons are event notification, pending event notification, and state or status indicators.  Some possible examples are included in the following sections.  None of these examples have yet been agreed upon; the issues must be addressed by the proposed industry organization.

#### Example Colors

The following suggestions have been made for standardized colors based on common usage in user interface design:

- BLUE symbols indicate COOL or decreasing temperature.

- RED symbols indicate HEAT or increasing temperature.

- YELLOW symbols indicate status.

- GREEN represents power-on or operational status.

#### Example Indicators

The following suggestions have been made for standardized indicators:

- The green indicator shows operational status for a PCT device.  When running properly and ready to communicate with the utility company, this indicator will be ON, signaling that the PCT is healthy and ready to performs its designated functions. In this case it will indicate RF communication is active and the device is ready to receive or transmit (in two-way operation) data.  Upon RESET (if equipped), this indicator should turn off, and then re-illuminate once the system has rebooted and is ready.

- The amber or yellow indicator shows that the PCT is communicating with the utility company.

- The blue indicator shows a pending or present price event. When flashing, it indicates that a pending price event will occur within the next 24hrs. When the indicator is solid, the price event is in progress.

- The red indicator shows an emergency event. When flashing, it indicates that a Stage1 emergency event is in progress. When solid, it indicates that a Stage 2 emergency event is in progress.

#### Example Icons

The icons in Table 1 have been suggested as possibilities for standardizing PCT icons.

Table 1  Examples of Possible Standard Icons

| Function | Example Icon |
| --- | --- |
| OFF |  |
| POWER |  |
| FAN |  |
| COOL |  |
| HEAT |  |
| AUTO MODE |  |
| BATTERY INDICATOR |  |
| UP |  |
| DOWN |  |
| LOCK |  |
| UNLOCK |  |
| CPP Indicator | $ |
| EMERGENCY STAGE 1 OR 2 INDICATOR LABEL | ! |
| LIGHT |  |

#### Example Displays

Error! Reference source not found. and Figure 10 illustrate how standardized colors and icons could be used by PCT suppliers to create distinctive displays.  The examples in Figure 10 might be used by touch-screen models.

Annex A: PCT Use Cases

Scenario 1: Customer Installs PCT

| 1 | Installer installs PCT in a new home or a qualifying re-model. |
| --- | --- |
| 2 | Installer connects any required devices (antenna, external communication module, etc.) to PCT to support one-way communications |
| 3 | Installer puts PCT into Provisioning Mode to receive security and address information |
| 4 | Installer calls phone number to initiate PCT security and address registration |
| 5 | Installer provides the PCT’s unique identifier number to automated system or phone service personnel |
| 6 | Utility system transmits PCT specific data in a Provisioning Message over the Utility Communication Infrastructure which is only acted on by the PCT being installed |
| 7 | PCT receives Provisioning Message and uses message data to complete configuration of security keys and address information |
| 8 | PCT provides visual feedback to Installer that provisioning is successful |
| \ |  |
| Notes | Installer can be home builder, contractor, customer or other. |

Scenario 2: Customer programs PCT

| 1 | Customer can set the time on the PCT but the time should be changed upon receipt of a valid time signal from the Utility Communication Infrastructure |
| --- | --- |
| 2 | Customer programs PCT for normal desired temperature for different times of day and for different days. (This is functionally identical to current programmable thermostats) |
| 3 | Customer can optionally change the default PCT program on its response to Price Events and Stage 1 Emergency Events |
| 3.1 | Customer can change the temperature offset for cooling upon receipt of a Price Event |
| 3.2 | Customer can change the temperature offset for heating upon receipt of a Price Event |
| 3.3 | Customer can change the price level response based on the signals that the customer's utility sends and the capabilities of the specific model of PCT |
| 3.4 | Customer can change the temperature offset for cooling upon receipt of a Stage 1 Emergency Event |
| 3.5 | Customer can change the temperature offset for heating upon receipt of a Stage 1 Emergency Event |
| 4 | Customer pushes "Run Program" button to activate normal PCT schedule |
| 5 | PCT sets temperature according to the day and time of the programmed schedule |
| 6 | PCT adjusts time when it receives a Clock Set message from the Utility Communication Infrastructure |
| Notes |  |

Scenario 3: PCT responds to ‘Price Event’ message

| 1 | Utility sends Price Event message |
| --- | --- |
| 1.1 | Utility includes at least one form of pricing information in Price Event message (price / kW hour, price ratio, price tier) |
| 2 | PCT receives Price Event message from the Utility Communication Infrastructure |
| 3 | PCT responds to the Price Event message based on pricing information and the PCT's programmed response (Many options here. Assuming a basic response) |
| 4 | PCT adjusts the thermostat setting equal to the programmed temperature offset setting for a Price Event |
| 5 | PCT remains responsive to customer input to override the setback temperature setting |
| 6 | PCT waits until the Event End Time as indicated by the Price Event message |
| 7 | PCT returns to the operating state that existed prior to the Price Event message (Could be normal programmed schedule, holding a specific temperature, etc.) |
| Notes | PCT will also respond to a Cancel Event message prior to the Event End Time |

Scenario 4: PCT responds to ‘Price Event’ message based on price

| 1 | Utility sends Price Event message |
| --- | --- |
| 1.1 | Utility includes at least one form of pricing information in Price Event message (price / kW hour, price ratio, price tier) |
| 2 | PCT receives Price Event message from the Utility Communication Infrastructure |
| 3 | PCT responds to the Price Event message based on pricing information and the PCT's programmed response |
| 4 | PCT chooses not to respond to Price Event because the programmed response is to ignore events under a specific threshold price |
| 5 | Utility measures response to Price Event and determines that it does not meet the Utility's needs |
| 6 | Utility has to purchase additional power at higher prices to meet demand |
| 7 | Utility sends new Price Event message with increased pricing level information |
| 8 | PCT receives Price Event message from the Utility Communication Infrastructure |
| 9 | PCT responds to Price Event message based on pricing information and the PCT's programmed response |
| 10 | PCT now chooses to respond to Price Event message because the programmed response's threshold has been met |
| 11 | PCT adjusts the thermostat setting equal to the programmed temperature offset setting for a Price Event |
| 12 | PCT remains responsive to customer input to override the setback temperature setting |
| 13 | PCT waits until the Event End Time as indicated by the Price Event message |
| 14 | PCT returns to the operating state that existed prior to the Price Event message (Could be normal programmed schedule, holding a specific temperature, etc.) |
| Notes | For a customer to realistically respond to different price levels received from the one way communication system, the customer will need to have an installed Time of Use meter |
|  | PCT will also respond to a Cancel Event message prior to the Event End Time |

Scenario 5: PCT responds to Reliability Event message

| 1 | Utility sends Reliability Event messages |
| --- | --- |
| 1.1 | Utility sends Reliability Event - Change Temperature message that includes a temperature offset change value |
| 1.2 | Utility sends Reliability Event - Set Temperature message that includes an absolute temperature set point value |
| 2 | PCT receives Reliability Event message from the Utility Communication Infrastructure |
| 3 | PCT responds to the Reliability Event message based on the PCT's programmed response |
| 4 | PCT adjusts the thermostat setting to save the most energy based on the received Reliability Event messages (default response) or to the customer's programmed response for a Reliability Event |
| 5 | PCT remains responsive to customer input to override the Reliability Event temperature setting |
| 6 | PCT waits until the Event End Time as indicated by the Reliability Event message |
| 7 | PCT returns to the operating state that existed prior to the Reliability Event message (Could be normal programmed schedule, holding a specific temperature, etc.) |
| Notes | PCT will also respond to a Cancel Event message prior to the Event End Time |
|  | With two temperature setting messages, the desired default response and acceptable programmable responses need to be well defined |

Scenario 6: PCT does not respond to Reliability Event message

| 1 | Utility sends Reliability Event messages |
| --- | --- |
| 1.1 | Utility sends Reliability Event - Change Temperature message that includes a temperature offset change value |
| 1.2 | Utility sends Reliability Event - Set Temperature message that includes an absolute temperature set point value |
| 2 | PCT receives Reliability Event message from the Utility Communication Infrastructure |
| 3 | PCT responds to the Reliability Event message based on the PCT's programmed response |
| 4 | PCT chooses not to respond to the Reliability Event because the programmed response is to ignore Reliability Events |

Scenario 7: PCT responds to Emergency Event message

| 1 | Utility sends Emergency Event messages |
| --- | --- |
| 1.1 | Utility sends Emergency Event - Change Temperature message that includes a temperature offset change value |
| 1.2 | Utility sends Emergency Event - Set Temperature message that includes an absolute temperature set point value |
| 2 | PCT receives Emergency Event message from the Utility Communication Infrastructure |
| 3 | PCT adjusts the thermostat setting to save the most energy based on the received Emergency Event messages |
| 4 | PCT is not responsive to customer input to override the Emergency Event temperature setting |
| 5 | PCT waits until the Event End Time as indicated by the Emergency Event message |
| 6 | PCT returns to the operating state that existed prior to the Emergency Event message (Could be normal programmed schedule, holding a specific temperature, etc.) |
| Notes | PCT will also respond to a Cancel Event message prior to the Event End Time |
|  | With two temperature setting messages, the desired default response and acceptable programmable responses need to be well defined |

Scenario 8: PCT receives Event message with address information

| 1 | Utility sends Event Message(s) with Addressing data in the message body (The exact message type is irrelevant for this use case) |
| --- | --- |
| 2 | PCT receives Event Message with Addressing information from the Utility Communication Infrastructure |
| 3 | PCT compares received Addressing data with the PCT's stored address information |
| 4 | PCT determines that it is an intended Event Message recipient |
| 5 | PCT responds to Event Message according to the message type and the PCT's programming |
| Notes | Title 24 indicates that accepting and acting on Addressing data is mandatory for the PCT. The utility is not required to send Addressing data. |
|  | "Addressing data" refers to the Common Data Class that is included as part of messages sent by utilities to invoke a power saving response |
|  | "address information" refers to the information that must be input into a PCT that defines a particular PCT's actual address |

Annex B: Glossary

Acronyms

- A/C		Air Conditioning

- ACSI		Abstract Communications Service Interface

- AMI		Advanced Metering Infrastructure

- AW		Advisory Warning

- CDC		Common Data Class

- CEC 		California Energy Commission

- CI		Commercial / Industrial

- CIS		Customer information System

- CPP		Critical Peak Pricing

- CPUC		California Public Utility Exchange

- DES		Data Encryption Standard

- DR		Demand Response

- DRI		Demand Responsive Infrastructure

- EE		Energy Efficiency

- HVAC		Heating, Ventilation, and Air Conditioning

- IETF		Internet Engineering Task Force

- IOU		Investor Owned Utility

- ISO		Independent System Operator

- LCD		Liquid Crystal Display

- LED		Light Emitting Diode

- MD5		Message Digest 5

- MMC		Multi-Media Card

- NEMA		National Electrical Manufacturers Association

- NRSC		National Radio Systems Committee

- NTP		Network Time Protocol

- PAM		Price Alert Map

- PCT		Programmable Communicating Thermostat

- PRD		Price Responsive Device

- RFC		Request for Comments

- SDIO		Secure Digital Input / Output

- RBDS		Radio Broadcast Data System

- RX		Receive

- SHA1		Secure Hash Algorithm 1

- SNTP		Simple Network Time Protocol

- SPMS		Statewide Power Management System

- SPI		Serial Peripheral Interface

- TX		Transmit

- UCI		Utility Communications Interface

- UML		Unified Modeling Language

- XML		eXtensible Mark-up Language

Terms

  - Attribute:

  - California State Reliability Exchange:

  - Critical Peak Advisory:

  - Critical Peak Price Event:

  - Emergency Event: An emergency event is issued through the utility communications network to PCTs when energy system reliability problems require a curtailment of residential energy use through temporary adjustment of thermostat settings. Emergency events make a temporary adjustment to a customer’s temperature setpoint to lower energy use during a specified period.

  - Hash: A hash value (or simply hash), also called a message digest, is a number generated from a string of text. The hash is substantially smaller than the text itself, and is generated by a formula in such a way that it is extremely unlikely that some other text will produce the same hash value.

  - Heat Pump: A device that warms or cools a building by transferring heat from a relatively low-temperature reservoir to one at a higher temperature.

  - Implementation Profile:

  - Price Event: A price event is issued through the utility communications network to PCTs when energy supplies become tight when compared with energy demand. Customer PCTs receive this event and use pre-programmed adjustments provided by customers to lower energy use during such periods.  In the future, once a smart meter has been installed at the customer’s premises, energy charges may be raised during price events to reflect higher energy costs that the utility must pay to increase energy supply.

  - Protocol-Level Services:

  - Reliability Event:

  - Service Model:

  - Stage 0 Event:

  - Stage 1 Event:

  - Stage 2 Event:

  - Stage 3 Event:

  - Stage 4 Event:

  - Transaction:

  - Transaction Sequence:

Annex C: UC Berkeley PCT Research Report

“Summary of HVAC and Expansion Port Analysis”

Annex D: Other Publications

Annex E: Title 24 Language
	(Final Draft – Rev 29f)

The full text of the Title 24 follows …

(i) Thermostats – All heating and/or cooling systems shall have a Programmable Communicating Thermostat (PCT) that meets the requirements of Subsections 112(c)(1) and 112(c)(2) below:

(1) Setback Capabilities - All PCTs shall have a clock mechanism that allows the building occupant to program the temperature set points for at least four periods within 24 hours. Setback thermostats for heat pumps shall meet the requirements of Section 112(b).

(2) Communicating Capabilities – All PCTs shall be distributed with a non-removable Radio Data System (RDS) communications device that is compatible with the default statewide DR communications system, which can be used by utilities to send price and emergency signals. PCTs shall be capable of receiving and responding to the signals indicating price and emergency events as follows.

Price Events – The PCT shall be shipped with default price-event offsets of +4°F for cooling and -4°F for heating enabled; however, customers shall be able to change the offsets and thermostat settings at any time during price events. Upon receiving a price-event signal, the PCT shall adjust the thermostat setpoint by the number of degrees indicated in the offset for the duration specified in the signal of the price event.  The PCT shall also be equipped with the capability to allow customers to define setpoints for heating and cooling in response to price signals as an alternative to temperature-offsetting response, as described in Reference Joint Appendix 5.

Emergency Events – Upon receiving an emergency signal, the PCT shall respond to commands contained in the emergency signal, including changing the setpoint by any number of degrees or to a specific temperature setpoint. The PCT shall not allow customer changes to thermostat settings during emergency events.

PCTs shall also have the following capabilities.  Technical detail of items A though E below shall be included in Reference Joint Appendix 5:

- Include at least one industry standard expansion/communication port. Insertion of a utility-specific communications module shall disable the default statewide communications hardware built in to the PCT unless the utility module is removed or is no longer receiving a signal.

- Provide user information regarding communications system connection status, type of event (price or emergency), and other maintenance-related information.  This information shall be on the standard PCT display, using a Liquid Crystal Display, standalone indicator using Light Emitting Diodes, or other means.

- At a minimum, standardize terminal mapping of terminal numbers 1-9.  This approach must include 24 volt power supply, both analog and digital PCTs, and must support heat pumps with resistance heat strips and reversing valve in both residential and small commercial packaged units.

- Include the capability to randomize, over a 30-minute period after the end of an event, the time at which the thermostat returns to the programmed setpoint.

E.  Through user input be capable of addressability at the substation level or finer including individual PCT.

EXCEPTION 1 to Section 112(c): Gravity gas wall heaters, gravity floor heaters, gravity room heaters, non-central electric heaters, room air conditioners, wood stoves, fireplaces, and room air-conditioner heat pumps need not comply with this requirement. Additionally, room air-conditioner heat pumps need not comply with Section 112 (b). The resulting increase in energy use due to elimination of the setback thermostat shall be factored into the compliance analysis in accordance with a method prescribed by the Executive Director.

EXCEPTION 2 to Section 112(c):  Other devices within the heating and cooling system, other communications systems or methods, or utility specific devices determined to be capable of providing equivalent demand response functionality described in Section 112(i) that is approved by the Executive Director.

Annex F: The PCT Vision Document and Related Scenarios

(California Energy Commission – Sept. 14, 2006)

Eliminating the Need for Rotating Outages 
through Statewide Air-Conditioning Load Control
with Programmable Communicating Thermostats (PCTs)

The California Energy Commission is planning to mandate programmable communicating thermostats (PCTs) for all central air-conditioning units through building standards, appliance standards, load management standards, or some combination thereof. This effort is being undertaken to reduce or eliminate the need for rotating outages through temporary reductions in air-conditioning services during Stage III system emergencies. In addition, customers could use this same technology to voluntarily and automatically reduce load in response to dynamic rates and incentive programs. An important aspect of this goal is that the PCTs be compatible statewide, such that customers can purchase equipment irrespective of utility service territory.

Introduction and Overview

Under the authority of Sections 25402 and 25403.5 of the Public Resource Code, the California Energy Commission (Energy Commission) is charged with the responsibilities to develop and maintain standards for building and appliance efficiency and load management. Under these authorities, the Energy Commission is planning to mandate programmable communicating thermostats (PCTs) to enable load control of air-conditioning (AC) during Stage III emergencies. The “partial outages” (i.e. raising thermostat setpoints) made feasible by this emergency program would reduce or eliminate the need for full rotating outages. As currently planned, the PCTs would also provide customers with the capability to automatically reduce AC electricity use in response to dynamic rates and incentive programs, where available. The recently completed Statewide Pricing Pilot (SPP) and related pilots with San Diego Gas & Electric (SDG&E) and Southern California Edison (SCE) have demonstrated the effectiveness of communicating thermostats in achieving these goals.

PCTs or analogous technologies are envisioned to support system reliability, dynamic pricing, and incentive programs, as follows.

- Mandatory Load Control – PCTs provide the option for electric service providers to exercise control over AC loads in all non-exempt customer facilities as a last resort to avoid rotating outages. Customers cannot override mandatory load control events.

- Dynamic Pricing – Should critical-peak pricing (CPP) or real-time pricing (RTP) tariffs become available to small customers, PCTs would provide customers the option to reduce their electricity bills by voluntarily responding to CPP events or designated RTP thresholds.

- Incentive Programs – PCTs would provide customers the option to earn money through voluntary participation in load control and other demand response programs that pay for participation and/or performance.

Why partial outages?

Partial outages are more economically efficient than rotating outages because the effects of the outage are limited to the reduction of a single discretionary service (in this case AC) rather than elimination of all services (as occurs in rotating outages). As penetration of enabling technologies increases, partial outages can also be more equitable than full outages, which do not affect customers on exempt circuits. (About half of circuits are exempt, with non-discretionary loads like hospitals and police stations.)

Why AC load control?

- AC load control has long been considered a viable strategy for reducing peak demand.

- AC is a large system load made up of many small individual loads, so load drops can be very small, very large (up to 30% of California peak load) and anywhere in between.

- AC is generally considered a discretionary load. For most homes and businesses, an increase of a few degrees will not significantly impact comfort or economics, particularly if it happens only during extreme emergencies (less than once per year).

- AC programs can potentially target all sectors (residential, commercial and industrial).

Why a thermostat?

PCTs can provide two benefits generally unattainable with conventional AC-cycling programs:

- PCTs allow customers to automate preferences for response to dynamic pricing.

- Temperature-based control strategies are expected to equalize comfort impacts across customers, whereas cycling can unduly affect those with smaller AC units.

How would the envisioned system work?

Customers with PCTs could participate in dynamic pricing and AC load control programs offered by their service providers. In addition, PCTs could be used to quickly drop AC load to avoid rotating outages. Following is a description of how the system might work with 5 million PCTs and a peak load of 50 GW.

- Customers take service under a critical peak pricing (CPP) rate. The underlying time-of-use rate provides customers with incentives to program the PCT to shift load from more expensive to less expensive time periods every day. When wholesale market prices meet designated thresholds, “critical-peak” prices are dispatched, automatically initiating any price-event control strategies programmed by the customer. Customers may choose not to respond to price-events. Together, these automated actions lower everyday peaks and initiate significant demand response when wholesale costs are high, helping to avoid Stage 1 emergencies. Potential load drop: ~1-4% of peak load statewide.

- Expected supply shortages trigger (a) public appeals for conservation and (b) CPP events if wholesale prices have not already triggered an event. Potential load drop: ~1-4% of peak load statewide.6

- Shrinking reserves trigger voluntary curtailment (non-firm load reduction), including interruptible and AC load control customers. Potential load drop: ~3% of peak load statewide.

- Further supply shortages trigger mandatory curtailment (firm load reduction) in the following order:

    - PCT temperature setup: ~1-15% potential load drop statewide

    - Rotating outages: 100% circuit load drop; ~1-4% load drop statewide

What are the design requirements for PCTs?

The PCTs are envisioned to have the following features: (see also Appendix A)

- Standard connector to a wall-plate, to eliminate future needs for professional installation

- Communications for control inbound to thermostat (one-way communications)

  - Optional outbound (two-way) to service provider

  - Optional outbound (three-way) to other appliances in the home

- Addressable by utility, program and geographic area

- Customer interface indicates system protection and bill management events

  - Optional display of pricing and control levels

- Allows signaling of continuous 1° load drops during events for maximum flexibility

- Manages load rebound after control events

What are the next steps?

There are several technical issues that need to be addressed before a PCT system can be finalized.

Choose a statewide communications system

To ensure that PCTs are compatible statewide, a default statewide communication system must be determined so manufacturers can design the PCT hardware.

Choose a standard protocols for activating control

To ensure that PCTs are compatible statewide, standard protocols for activating control must be determined so manufacturers can design the PCT software.

Determine addressability needs

For mandatory load control, PCTs must be addressable in a way that is compatible with ISO/utility control areas. For dynamic pricing, PCTs must be addressable at the utility level, since tariffs are utility specific. Future pricing schemes may require addressability at the nodal level. To allow voluntary load control programs, PCTs must be addressable at the program/utility level, since signals must activate only those individual customers who have signed up for the program.

Plan for management of load impacts at the onset and conclusion of events

Some events will warrant gradual load impacts while others might require immediate response. In both cases a smooth return of AC load to the system is likely to be desirable. If these strategies are to be part of the PCT software, they must be determined before PCTs can be produced.

Choose a mandatory load control strategy

There are currently two options for mandatory control being discussed. One involves increasing PCT setpoints by a certain number of degrees (e.g. +4°F), while the other option involves setting all PCTs to the same setpoint (e.g. 80°F).

A Vision of Demand Response – 2015

Scenarios

California Energy Commission (CEC)

A Vision of Demand Response – 2015

Scenario 1- Residential, Low User, Minimum Functionality, Special Exemptions

At 78 years old, Meg A Watts was excited about moving into her new condominium in the Shady Acres Lawn Bowling and Mahjong Retirement Community.  Widowed a little over three years ago, her long-time home of the past 35 years was just too large and too difficult and expensive to maintain.  Her grown children arranged to move her to a new home in the southern part of California’s central valley, where she would have warmer weather and would be near her grandchildren.   The cold Idaho winters and high winter utility bills were difficult to manage on a fixed income.  Recent health problems that now required on-site 24-hour remote monitoring equipment linked to her doctor’s office just added to her budget difficulties.

Her new condominium was substantially smaller than her old house in Idaho.  According to her son Less, the reduced size of her new condo combined with all of the new energy efficient appliances, should lower her utility bills substantially and make it much easier to live within her budget.  Less had called the utility in advance to arrange service for his mother.  They asked a few questions regarding her basic lifestyle and home features and whether she qualified for any special exemptions.  As a result of that call, they mailed Less an information packet and setup checklist.

Day #1:  Normal Operations / Anticipated Critical Peak Conditions

Scenario – Testing the PCT

Preconditions: PCT is installed and receiving communications from the Utility Communication Infrastructure (UCI). Yellow light is lit indicating successful communication.

- Customer presses and holds override (or dedicated test) button on PCT for 3 seconds.

- PCT activates internal test routine.

- PCT blue light turns on and flashes indicating a future economic critical price event. (Example duration: approx. 5 seconds.)

- PCT blue light stops flashing and remains steadily on indicating economic critical price event is underway. (Example duration: approx. 5 seconds.)

- PCT blue light remains on and red light begins to flash indicating Stage 1 emergency. (Example duration: approx. 5 seconds.)

- PCT blue light remains on, red light stops flashing and remains steadily on indicating Stage 2 emergency. (Example duration: approx. 5 seconds.)

- PCT blue and red lights turn off.

- PCT test is complete.

Scenario – Customer programs the PCT

Preconditions: PCT is installed

- Customer selects the pre-defined lifestyle schedule that is closest to their own schedule.

- Customer selects the desired comfort/economy setting.

- Customer modifies as necessary the schedule and heating/cooling levels.

- Customer modifies as necessary the pre-programmed critical pricing response.

- Customer disables, if authorized, the Stage 2 emergency response by using a code provided by the utility or other authorized personnel.

Tuesday, July 21, 2015, 10:00am

What the Customer Sees

Meg and her son Less made a pre-move in visit to her new home to setup the various utility, communication, and other accounts and to acquaint her with the operation of her new appliances.  Meg was not a big fan of computers and automation and was initially overwhelmed by the many automation features of her new home, especially this new thermostat she read about.  Less, assured her it was all quite simple, led her to the wall where the thermostat was mounted, took out the checklist provided by the utility and proceeded to show her how it worked.

Her son Less explained that about ten years ago the CPUC adopted new rate structures that charged customers what he called a critical peak rate (CPP).  Most of the time she would be charged under a simple time-of-use rate augmented by a supplemental charge that reflected high utility cost or emergency situations.  He assured Meg that it was actually a pretty good deal. As he explained it, during the summer months, her electric utility costs would be significantly lower during late evening to early morning hours and higher during the mid-afternoon period when most people were cooling their homes.  If the demand for energy ever got high enough to trigger a high-cost situation or threatened the utility’s ability to provide power, they would send out a signal alerting all customer automation and notification devices to a critical peak price.  Less explained that most of the time customers were given 12-24 hours advanced notice of any pending critical peak prices, however, sometimes during emergencies customers were given no advanced notice – which was the reason customers automated their response through the new thermostat.

Less explained how her thermostat would automatically receive critical peak price and emergency signals and automatically make minor adjustments based on her comfort settings.  As part of his explanation, Less pointed out the three LED displays on her thermostat and explained to Meg what each light meant.  The yellow light, which was currently lit, indicated that the thermostat was active, working properly and currently receiving a utility test and price signal.  He showed her the little sticker attached to the thermostat that provided instructions for calling the manufacturer if the yellow light should ever go out or if the thermostat malfunctioned in any other way.

Using the checklist, Less instructed Meg to push the Override button and hold it for a few seconds to trigger a test routine.   A blue light next to the yellow light came on and slowly started flashing.  Following the checklist, Less explained this light would be activated when the utility knew in advance, like the next day, that there would be a critical peak price.  After a few seconds, the blue light stopped flashing and stayed lit – he explained that a solid blue light meant the critical peak price was actually in effect.  Finally, after a few seconds a third red light started to slowly flash.   Less explained that this meant there was something the checklist referred to as a Stage 1 system emergency.  This also triggered a critical peak price and the same pre-programmed reaction from her thermostat.  Finally, the red light stopped flashing and stayed lit.  Less explained that a steady red light meant there was a very serious Stage 2 power emergency, which meant that the utility was just one step away from rotating outages - when all of her power would be turned off.  Meg did not need a more detailed explanation.  She had been visiting Less and his family in the summer of 2000 and vividly remembered the blackouts.

After Less finished his explanation of her thermostat display, he proceeded to the next section of the checklist and told her she had three options to choose from in setting up her thermostat.

- Option 1:  Accept with the Default Settings – Less explained that these new thermostats were a little different than what she had in her old home.  According to Less they pre-programmed and ready to go out of the box with default lifestyle (time), comfort and economy schedules.   As he explained it, lifestyle schedules used pre-set time settings to reflect typical work, stay at home or holiday operating times.  Comfort schedules would maintain a default 750 temperature setting unless Meg pushed the “Warmer”  or “Cooler” arrow buttons.  Pushing these buttons would raise or lower her thermostat settings for each lifestyle time block in fixed increments until she got her comfort to an acceptable level.  Less explained that the economy schedule was a way for Meg to balance her comfort settings with potential bill savings.  Economy settings determined how much her thermostat setting would change in response to the critical peak and emergency Stage 1 alert signals.  If she did nothing the defaults would automatically change her thermostat setting by a minimum two degrees in summer months or lower it by the same amount in winter months in response to critical peak price or an emergency signals.  Less showed Meg the information on the comfort-bill savings information provided on the utility checklist.  According to the utility, the default economy settings should provide the typical customer with a 5% reduction in their monthly bill with no noticeable comfort impacts.  In Meg’s case, the utility estimated that a 5% savings would translate into $3.00 to $4.00 each month.  Changing to the “Moderate” economy setting would raise average monthly savings to 7-8% and result in a few hours of warmer or cooler conditions.  The “Super Saver” economy setting could produce savings as high as 15% but would also result in a little greater discomfort.

- Option 2:  Modify the Default Lifestyle Settings -  Less pushed the override button one more time and scrolled through the lifestyle settings pre-programmed into the thermostat.  The lifestyle settings provided several common work, vacation, and other schedules.  Because this was a retirement community, the thermostat default was pre-programmed by the builder for a weekday and weekend “At Home” schedule, with the minimum critical peak price response.  Meg could easily change the start and end time of any schedule to suit her needs or change the thermostat response if she wanted to increase or decrease her critical peak savings on her electric bill.

Less also showed Meg that the setup routine allowed her to push the override button and automatically disable the critical peak price and Stage 1 emergency response indicated by the blue and red warning lights.  Disabling the price response option during the setup process meant her thermostat and appliances would operate normally all the time and she would pay whatever it cost for the energy.  Less also pointed out that she could leave the automatic price response program alone and just push the override button if she ever became uncomfortable or inconvenienced during a pricing event.

Less noticed that the utility provided checklist also included estimated billing information for his mother’s new condo, apparently based on information he provided during his phone call to activate her new account.  The utility estimated that his mothers new home would probably be classified as a “low user” under the 130% of baseline legislation.  As a result of an innovative change to the legislation Meg’s monthly bill would charge her either the subsidized capped rate or the CPP rate, whichever was lower.  The utility called this the Low Bill Guarantee Option.

Meg took Less’ recommendation and decided to try the default CPP pre-programmed lifestyle settings.  Pushing a single button to override any automated CPP response was easy enough and the Low Bill Guarantee Option provided reasonable financial protection.  Meg stood to gain financially if everything worked right.  With the minimal response settings pre-programmed into her thermostat, the utility estimates Meg should pay about 15% less than she would under the subsidized 130% baseline rate.

- Option 3:  Disable the Stage 2 Emergency Setting - According to the setup checklist, Less noticed that this option was limited to individuals with health and other disabilities that might be adversely impacted by any of the Stage 2 emergency response actions.  According to the checklist, the information he provided to the utility regarding his mothers medical monitoring and alert equipment during the account setup process qualified her for the exemption.  With her medical conditions, exposure to extreme heat situations that might result from any prolonged loss of use of her air conditioning, might pose a health problem.

Less explained to Meg that during a Stage 2 alert, the utility could substantially curtail everyone’s air conditioner or heating systems for brief periods of time if necessary to avoid rotating outages.  However, Less also explained that Meg’s medical monitoring equipment qualified her for an exemption.

The checklist included a highlighted box with what looked like a special bar code printed in one corner.  Following the instructions, Less was directed to hold the bar code within six inches of the thermostat, hold down the override button and wait for an acknowledgment signal, indicated when all three check lights would flash once, stay lit for about three seconds and then go back to their normal mode.  According to the checklist, the bar code was really a printed radio frequency identification tag that was programmed for a one-time exemption.  Less followed the instructions and noticed that the yellow, blue and red lights flashed once, stayed on for about 2-3 seconds and then went back to a normal mode, with the yellow light on and the red and blue lights off.

What the Customer Did Not See

When Less Watts called the utility to activate his mother’s account, the customer service representatives automatically went through an automated pre-service interview.  The interview gathered the basic information to support their billing process.  It also asked a few very simple questions to identify any medical or other special circumstances that might exempt the customer from the Stage 2 involuntary curtailment of their HVAC systems.  Identifying customer locations with critical medical information also allowed the utility to assign a higher priority to preventative maintenance and outage incidents.

When Less indicated that medical monitoring equipment would be present, the customer service representative authorized a medical exemption to Stage 2 involuntary curtailment of Meg’s HVAC systems.  This authorization caused a capacitor-activated radio frequency identification (RFID) tag to be printed on the new customer Service Initiation Checklist.   This RFID tag was designed to be good for one use after which it would become inactive and unusable.   The RFID tag functioned like an exemption key, however it would not become active until the PCT received its first “Price/Test Signal”.

The Price/Test Signal was dispatched by the utility several times each hour.  This signal provided the actual price included in the default CPP rate, so in effect it acted like a real-time price.  The signal also included location specific information designed to allow the targeting of control and price/emergency actions on individual substations and feeders, a time stamp to continually synchronize the PCT and data concentrators supporting their advanced metering (AMI) data collection effort, and other maintenance information used by utility field crews to support preventative and outage restoration.    The price signal information also was used to support utility and third party information services like real-time customer displays of usage and actual cost.

The use of PCT’s and the ability to assign individual exemptions provided the utility with tremendous flexibility to dispatch very limited HVAC curtailments, control a substantial amount of load and generally avoid supply or congestion induced events that in the past might require rotating outages.  The involuntary HVAC curtailments dispatched in prior Stage 2 alerts rarely reduced customer usage as much as the original air conditioner load control programs.

Using basic occupancy information and Meg’s address, the utility was also able to call up the electricity usage history from her condo’s prior owner.  This information provided them with the information they needed to include estimated billing and savings information on the Service Initiation Checklist they would send to Meg.

Tuesday, July 21, 2015, 10:20am

Just as Less and his mother were finishing up at the thermostat, they saw the flashing blue light come on.  Meg looked at Less and asked if that was something he did or was that a signal from the utility that tomorrow could potentially be a critical peak price day.  Less responded that he was pretty sure it was a utility critical peak price alert, although he said he had a way to confirm the signal.  Less pulled out his pocket communicator, a small hybrid device a little larger than the size of a deck of cards that included voice, video, calendaring, email, several entertainment options and electronic e-commerce applications.  The top portion of Less’ display, reserved for high priority messages, was flashing with a critical peak alert for Less’ house from his utility.  Less held out the pocket communicator to show his mother the flashing message.  He mentioned that he had programmed his home systems to automatically forward all critical messages to him via his pocket communicator.

Less told his mother there were other ways she could confirm the price signal if he wasn’t around.  He told her the utility also had an arrangement with local television news services and newspapers to publish or announce information on pending critical peak periods and other emergency situations.  Local television stations usually displayed a utility icon somewhere on the screen during their news broadcasts.  Newspapers usually published the same icon in a banner at the top of the front page.

Day #2:  Critical Peak / Emergency Conditions

Scenario – Critical peak pricing (One way communications)

Preconditions: PCT is installed and programmed. PCT is receiving communications from the Utility Communication Infrastructure (UCI). PCT blue light is flashing indicating an upcoming critical peak pricing event.

1a.	Utility transmits critical peak pricing message with a temperature setback using the UCI to groups of customers.

OR

1b.	Utility transmits critical peak pricing message with energy pricing data using the UCI to groups of customers.

- PCT receives message via UCI indicating critical peak pricing is now in effect.

- PCT waits a random period of time between 0 and 15 minutes.

4a.	PCT changes temperature setting according to the received message. (e.g. The utility price message requests a 2 degree setback.)

OR

4b. PCT changes temperature setting according to the PCT’s programmed price message response. (e.g. A 4 degree setback is the default PCT response, but the customer has changed it to 3 degrees for higher comfort.)

5.	PCT emits a beep and sets the blue light to be constantly on.

6.	PCT remains responsive to customer input to override the utility setback.

7.	PCT adjusts temperature according to normal customer schedule maintaining the programmed price responsive temperature setback.

8.	PCT waits for a period of time as indicated by the received message.

- PCT returns temperature setting to customer’s normally scheduled setting and turns off the blue light.

Alternate Steps

3a.	PCT does not wait random period of time due to nature of received message or receipt of multiple utility messages that indicate an immediate start.

4c.	PCT does not change temperature due to customer’s modification of PCT critical peak price response.

8a.	PCT receives message from utility via UCI indicating the end of the critical peak pricing period.

Scenario – Stage 1 emergency (One way communications)

Preconditions: PCT is installed and programmed. PCT is receiving communications from the Utility Communication Infrastructure (UCI).

1a.	Utility transmits a Stage 1 emergency message with a temperature setback using the UCI to groups of customers.

OR

1b.	Utility transmits a Stage 1 emergency message with an absolute temperature setting using the UCI to groups of customers.

- PCT receives Stage 1 emergency message via UCI.

3.	PCT changes temperature setting according to the received message. (e.g. The utility emergency message requests a 4 degree setback or the absolute temperature is set to 79 degrees.)

4.	PCT emits a beep and sets the red light to flash on and off.

5.	PCT remains responsive to customer input to override the utility setback.

6.	PCT adjusts temperature according to normal customer schedule maintaining the programmed Stage 1 emergency temperature setback.

7.	PCT waits for a period of time as indicated by the received message.

- PCT returns temperature setting to customer’s normally scheduled setting and turns off the red light.

Alternate Steps

3a.	PCT does not change temperature due to customer’s modification of PCT Stage 1 emergency response.

7a.	PCT receives message from utility via UCI indicating the end of the Stage 1 emergency period.

Scenario – Stage 2 emergency (One way communications)

Preconditions: PCT is installed and programmed. PCT is receiving communications from the Utility Communication Infrastructure (UCI).

1a.	Utility transmits a Stage 2 emergency message with a temperature setback using the UCI to groups of customers.

OR

1b.	Utility transmits a Stage 2 emergency message with an absolute temperature setting using the UCI to groups of customers.

- PCT receives Stage 2 emergency message via UCI.

3.	PCT changes temperature setting according to the received message. (e.g. The utility emergency message requests a 4 degree setback or the absolute temperature is set to 80 degrees.)

4.	PCT emits a beep and turns the red light on.

5.	PCT becomes unresponsive to customer input to override the utility setback.

6.	PCT waits for a period of time as indicated by the received message.

- PCT returns temperature setting to customer’s normally scheduled setting and turns off the red light.

Alternate Steps

3a.	PCT does not change temperature due to customer’s modification of PCT Stage 2 emergency response. (e.g. Medical exemption)

6a.	PCT receives message from utility via UCI indicating the end of the Stage 2 emergency period.

Wednesday, July 22, 2015, 8:30 am

Reading the local newspaper and watching the early morning news on TV while enjoying breakfast in her new home, Meg noticed a small banner in the upper right corner of the front page announcing that today would be a critical peak day.  There was even a reference to a later section of the newspaper that provided a “Helpful Hints” list of things people could do to save money.  The TV weather report indicated that the heat wave was continuing, forecasting another day with temperatures exceeding 1000.  As she watched the weather report Meg noticed a similar “Critical Peak Alert” banner superimposed in a corner of the TV screen.

When she checked the LEDs on her thermostat she noticed that the blue light was still flashing.  Although she still felt a little uncertain regarding how this new automated response stuff would work, the information provided by the newspaper and local TV station seemed to demonstrate a rather comforting level of coordination.  It seemed like the whole community was pulling together to help keep down costs and avoid problems.  Meg was feeling pretty comfortable with her new home.

Wednesday, July 22, 2015, 2:30 pm

What the Customer Sees

Meg had just retuned from the local grocery store and was unpacking when she heard a brief audible “beep” that appeared to come from her thermostat.  When she checked, she noticed that the blue LED had stopped flashing and was now fully lit.  According to Less, this meant that the critical peak prices were now in effect, which should trigger an automatic response from her air conditioning system.  From the checklist that Less left with her she knew that her thermostat was set to 750 but now it read 760.  Meg was actually pretty impressed, the thermostat had automatically responded just as Less had described.  Meg went back to unpacking her groceries but mentally reminded herself to take another look a little later to make sure everything was still working right.

What the Customer Did Not See

Meg’s thermostat was responding to a single secure virtual public network (VPN) Internet signal that originated over 400 miles away generated by the California ISO in a signal to her local utility when the wholesale cost of energy exceeded a distribution area critical peak threshold value for the Southern region of her central valley community.  The ISO was not only monitoring wholesale prices, it and Meg’s local utility were also simultaneously using the Statewide Power Management System (SPMS) to monitor in real-time the actual load and system harmonics on almost all major substations and distribution circuits.  The ISO critical peak price signal was automatically dispatched based on algorithms that balance the wholesale costs with other information regarding congestion and potential reliability features for each monitored substation and distribution circuit.   The California ISO signal was received almost instantaneously by Meg’s host utility and was instantaneously passed through to their critical peak broadcast system which uses a side band of several public radio and television stations to trigger customer thermostats and other price responsive devices.  Passing the critical peak signals through each utility provides local utilities with an opportunity to intervene and adjust the dispatch for any maintenance or other special activity that might be jeopardized by an untimely price or reliability signal.  Utility operators had not flagged any of the target areas for intervention, consequently the ISO signal was passed through without delay.

Within 3-5 seconds the critical peak price signals had been received by approximately 1.5 million residences and businesses, representing approximately 12 GW of HVAC load.  Price and reliability conditions were not yet considered sever.  Isograms established over several years of real-time load monitoring indicated that voluntary customer price response should provide more than sufficient load relief to mitigate current problems.  Consequently the ISO dispatch was statistically targeted to dynamically configured groups of customers within the target area to produce a minimum 10 change in HVAC setting at any customer site.  ISO algorithms were designed to dynamically configure customer groups and the control intensity to just meet the system need.  Real-time monitoring creates a closed-loop response that either ratchets the control strategy up or down based on actual measured customer response.

The critical peak signals dispatched by the ISO and local utility trigger a minimum one-hour control strategy from each thermostat and price responsive device based on CEC design guidelines incorporated into the Building and Appliance Standards.  The design guidelines specify two basic parameters that each device must meet, specifically:

- A minimum one-hour average control response.  Specifying a 60-minute average control period minimizes the number of signals that need to be communicated and also avoids unnecessary short cycling of customer loads.  In addition, the control period is internally randomized to average 60-minutes in duration, however, actual durations will vary between 45-75 minutes.  Randomizing the duration of control helps balance returning load at the conclusion of each control event.

- Randomized control strategy start times.  Normal critical peak price signals are received by each controllable thermostat and price responsive device almost instantaneously, however, activation of the device response is internally randomized over a 15-minute period.  Randomizing the start times of each customer device helps balance both the initial load impacts and returning load at the end of the control period.  In emergencies, multiple simultaneous signals from the ISO or local utility will trigger an immediate, non-random instantaneous activation of the control strategy for all customer devices.

Wednesday, July 22, 2015, 4:00 pm

What the Customer Sees

While entertaining several of her new neighbors, Meg heard another audible beep coming from her thermostat.  When she checked, the blue LED was still lit and now the red LED was flashing.  While it was still reasonably comfortable in her home, the thermostat now showed a setting of 770.  One of Meg’s new neighbors explained that the local utility must be having some problems.  Meg remembered that the flashing red LED meant that the utility was experiencing something called a Stage 1 system emergency.  One of Megs new neighbors then stated that she had programmed her thermostat to the “Super Saving” setting during these critical peak events because of the money it saved on her monthly bill.  She said when it gets too warm, I just go to the clubhouse or mall for a few hours.  Meg decided to wait and see whether her home would become uncomfortable.

Just as she was about to rejoin her new friends, there was another audible beep from thermostat.  Now the red light stopped flashing and stayed lit.  Meg knew from Less that this meant there was a much more severe Stage 2 emergency.  However, Meg also noticed that although her thermostat setting did not change from 770  the numbers were now flashing.   One of her neighbors said something must be wrong with Meg’s thermostat because when she gets a solid red light her thermostat displays a flashing emergency symbol instead of a temperature setting.

One of Megs other neighbors chimed in and said, the flashing temperature setting means that Meg must have a medical or other exemption.  Meg confirmed that indeed that was the case because of the medical equipment she had in the bedroom that let her doctor and hospital remotely monitor her heart conditions.

Once Meg’s neighbors figured out that a Stage 2 emergency had been called, they also realized that their air conditioning systems would automatically be curtailed until the utility problems were corrected.  None of Meg’s neighbors had a medical exemption.  Reluctant to return to homes that would soon be getting a little uncomfortable, Meg offered and they all unanimously decided to stay a little longer.  Besides, Meg’s home was a comfortable 770.

Then they all started talking about how complex all this technology stuff was.  Meg was still confused and amazed over how what looked like a bar code on a piece of paper could actually be a miniature radio.

What the Customer Did Not See

At 3:59 pm the Statewide Power Management System (SPMS) registered a forced outage on a major supply point feeding the Southern central valley area.  Dispatch algorithms at the California ISO automatically adjusted for the loss of load by instantaneously ramping up the customer price response signals.  The ramping process generated multiple radio activation signals that (1) automatically bypassed local utility intervention and (2) instantaneously realigned customer groups and synchronized another round of 20 HVAC temperature increases from all controllable thermostat and price response devices.  This latest round of emergency signals overrode the internal randomizing routines in customer control devices to intensify the load response.  The dynamic realignment of the customer groups allowed the ISO to focus more voluntary price response on the most congested areas.  Reserve margins were now below 7% in certain geographic areas but holding steady.

At 4:03pm another forced outage triggered a Stage 2 alert.  This time ISO dispatch algorithms substantially ramped up the control algorithms to temporarily impose mandatory reliability overrides on all non-exempt customer HVAC loads.  In this case, a severe distribution problem required the HVAC loads in the target area to be locked out entirely for the duration of the event.  Almost instantly, the SPMS registered an additional 2 GW of load relief on the impacted circuits, pushing system reserve margins back above 7%.

Simultaneously, local utility systems dispatched electronic explanatory warning messages to all major commercial and industrial customers as well as others who had signed up for the notification service.  Announcements were also automatically dispatched to all radio and television stations.  Repair crews were also receiving information from both the utility advanced metering (AMI) network and SPMS regarding isolated customer and distribution feeder outages.  Select crews received emergency electronic work orders on Internet connected field tablets that directed them to specific GPS coordinates corresponding to the location of each outage.

Wednesday, July 22, 2015, 6:35 pm

What the Customer Sees

Meg’s first mahjong game was breaking up and her new neighbors were starting to leave when there was another beep from her thermostat.  The yellow LED was now the only one of the three that was still lit.  Both the blue and red LED’s were now off.  Meg’s thermostat was registering an internal reading of  770  but her internal setting was now back to 750 .  Apparently both the critical peak and emergency situations were over.  Meg and her neighbors just shrugged and went about their business.

What the Customer Did Not See

Both forced outage situations were quickly resolved by emergency utility crews.  By 5:45 pm power had been restored to all customer locations reporting problems.  Declining commercial loads combined with voluntary and mandatory price/reliability response brought reserve margins back to normal levels.  Based on forecasts from the SPMS, Stage 2 emergency signals were discontinued at 5:50pm.  Forecasts showed that all customer loads would return to their normal local operating state starting around 6:30pm.

No major outages were reported.  Utility customer operating centers reported no significant increase in call volume.

A Vision of Demand Response – 2015

Scenario 2 - Residential, High User, High End Options, Advanced Functionality

Less Watts is a 42-year-old electrical engineer.  For the last 6 years he has worked for the NanoScience Particle Energy Research and Popsicle Company (NSPERPC), a high-tech manufacturing company he started with his brother.  He and his family live about five miles from his mother’s new condominium in a 4,200 square foot custom built home in an exclusive neighborhood.   Less is a true high-tech gadget guy.  Much to the consternation of his wife and children, Less has automated and monitored every aspect of his home.

It turns out that Less’ infatuation for technology is actually secondary in importance to his quest to save money.  When his utility introduced critical peak pricing (CPP) about nine years ago and advertised how much money customers could save, Less took it as a personal challenge.  While his initial efforts with utility recommended control devices produced reasonable bill savings and few noticeable impacts on his family’s lifestyle or comfort, Less was convinced he could do better.

Less eventually discovered that his utility offered quite a few information and technology options to assist with his Less could access through any Internet connection, or (2) a hardware and software package being made available   through local branch libraries.  Out of curiosity Less decided to try the loaner package available from the library.  The package included a wireless tablet and several devices that looked like extension plugs.   According to the literature, the wireless tablet was a full-fledged computer with several built-in communication links.  With a supplemental subscription fee, the display tablet provided access to a near real-time utility database that included his household energy usage and actual cumulative billing / cost information.  Analysis and modeling applications included with the tablet will allowed him to graphically display his usage information, customize the analysis by inputting more detailed house and appliance information, and benchmark his usage with like homes in his own community.  One of the most interesting applications makes it possible for Less to monitor each major appliance one-by-one and perform sophisticated economic evaluations that identify when he should consider a more efficient replacement.  This utility provided application also creates a list of certified local suppliers and installers.  Applications included with the electronic tablet also automatically complete and transmit electronic applications for special rebates on new appliances that Less wants to purchase.

According to the literature, the plug extension devices represent an innovative new technology.  By plugging these plug extension devices into the electrical socket and then plugging in his electric appliances, Less could monitor in real-time, the load for anything that has an electric cord.  Each plug extension device had a letter code stenciled on one surface.  Plugging an appliance into a plug extension device automatically brings up a window on the wireless tablet labeled with the letter code corresponding to the stenciled code.  The window displays in real-time how much energy is being used by that appliance at that moment.  By choosing the right options, Less can integrate these individually monitored loads with his total house load.  Less is also provided with options to download all the data and reports wirelessly to his own computer.

The first time Less checked out the electronic tablet and load monitoring package, he was almost beside himself with excitement.  First he monitored the big things like the refrigerator, furnace, washer and dryer.  He then monitored everything that was plugged into the wall including his beside lamp, toaster oven, electric toothbrush and his wife’s lava lamp.  Based on a rate analysis using the utility provided applications, Less discovered that properly managing his cooling zones and shifting load to off-peak time periods would substantially reduce his electric bills.  The display table also allowed Less to preview and model new state-of-the-art high-tech appliances with built in demand management features that could be wirelessly linked with a whole-house energy management system.    As a result of this evaluation, Less upgraded his HVAC, refrigerator, washer, dryer and hot water heater.  He also subscribed to the advanced energy management, monitoring and information services provided by the appliance manufacturer, which was part of a real-time maintenance contract (described below).

The new HVAC system employed wireless technologies that eliminated the need for a conventional wall-mounted thermostat.  Instead, his new HVAC system came with little stick-on temperature sensors about the size of a quarter that he could mount anywhere in his house.  The system also came with a wireless display/control panel that could sit on a counter or mount to a wall bracket.  Besides managing his home energy use, the display panel provided a wireless link to the Internet along with several news and entertainment options.  What most excited Less was the fact that neither the display panel nor any of the remote sensors used batteries – all were using a new energy scavenging technology based on visible light, temperature variations and vibration.

The HVAC system that Less purchased included a redesign of the home duct system.  Less divided his house into four zones and then retrofitted his ductwork with controllable dampers and remote temperature sensors that allowed him to establish different comfort settings for each zone.  A wireless display touch panel displayed a schematic of his entire house with real-time monitoring of each zone.  The compressor and heating units came equipped with fully integrated electronics and internal programs necessary to provide full compliance with the CEC price responsive Building and Appliance standards.  When he purchased the new HVAC system, Less opted for a vendor offered premium monitoring, preventative maintenance and home automation package.  This advanced package required a special hybrid Wimax bi-directional communication capability that would allow the vendor to support remote system diagnostics, off-site remote maintenance and a range of other appliance applications, as well as enhancements to the State required price responsive and emergency response functions.

For all of his other major appliances, Less opted for models that were wirelessly linked to and controlled by the home energy monitoring and maintenance package provided by his HVAC vendor.  Linkages between the appliances and the home automation system provided support for pre-cooling, shifting water heater use to off-peak hours and low-power critical peak interlocks for the washer, dryer and dishwasher.  According to the simulations provided by the HVAC vendor, Less could theoretically reduce his peak summer month electric bills by up to 40%.

Day #1:  Normal Operations / Anticipated Critical Peak Conditions

Tuesday, July 21, 2015, 10:20am

Scenario – Critical peak pricing notification (Two way communications)

Preconditions: Customer has a PCT/home energy management system able to receive advanced Utility or Qualified Signal Provider communications.

- Utility transmits critical peak pricing alert to customers and other Qualified Signal Providers that provide customer notification services.

- Qualified Signal Provider transmits critical peak pricing alert and additional value added data to Customer.

- Customer’s PCT/home energy management system receives critical peak pricing alert.

- Customer’s PCT/home energy management system confirms receipt of alert message to Qualified Signal Provider.

- Customer’s PCT/home energy management system provides notification to Customer using displays and other communicating devices.

What the Customer Sees

Less’ wife Lesley was in the kitchen paying bills and monitoring local news updates from a wireless display monitor when a blinking critical peak alert appeared in the upper portion of the screen.  The message included a small icon provided through their appliance vendor home energy management subscription.  When Lesley tapped the message with her finger, a window with supplemental information appeared.  The message indicated that the critical peak period was most likely to occur tomorrow, Wednesday, July 22nd and start between 2:00 to 3:00pm and would last for about 120 minutes.  The message also indicated that all in-home systems and control settings were operational.  There was also a status message indicating that the operating systems, environmental controls and energy management functions at Less’ business (NSPERPC) were online and also operating as planned.  Lesley knew that Less would get these messages automatically since he programmed the wireless display to forward all messages to his pocket communicator.

What the Customer Did Not See

By 5:30am each morning the ISO operations center has received the first of several real-time updates from the Statewide Power Management System (SPMS).  Real-time substation and feeder data, together with weather forecasts, monitored system harmonics, historical circuit loading and current trading data produce a forecast of potential system cost, market price and system reliability conditions for a range of geographical and critical transmission / distribution locations throughout the statewide electrical network.  With a continuing heat wave, several forced outages and other supply constraints; the forecast anticipates potential critical price conditions for the next day during the later afternoon hours.  As a result, by 10:00am that morning, the ISO has provided each local utility with a critical peak alert and detailed forecast for Wednesday, July 22nd.

After processing the ISO information, the local utility dispatched a system wide critical peak alert through their communication providers that are automatically received by all CEC compliant controllable thermostats and price responsive devices.

Less Watts purchased appliances and subscribed to information and management services that require a more sophistical communication capability than that mandated in the basic CEC compliant devices; consequently his systems do not receive the standard utility “Critical Peak Alert”.  Less’ vendor provides their own communication network that receives the utility “Critical Peak Alert” and then passes it through to each of their subscribers along with additional information necessary to manage Less’ preferences.  Less’ vendor received their certification as a Qualified Signal Provider from the CPUC only after demonstrating they could meet a specific list of performance criteria.

Day #2:  Critical Peak / Emergency Conditions

Wednesday, July 22, 2015, 8:30 am

Scenario – Critical Peak / Emergency Event (Two way communications)

Preconditions: Customer PCT/home energy management system able to receive advanced utility or vendor communications.

- Utility transmits a Stage 1 emergency message with a temperature setback to customers and other Qualified Signal Providers that provide customer notification services.

- Qualified Signal Provider transmits Stage 1 emergency message to Customer.

- Customer’s PCT/home energy management system receives Stage 1 emergency message.

- Customer’s PCT/home energy management system confirms receipt of Stage 1 emergency message to Qualified Signal Provider.

- Customer’s PCT/home energy management system changes temperature setting according to received message

- PCT remains responsive to customer input to override the utility temperature setback.

- Utility transmits a Stage 2 emergency message with a temperature setback to customers and other Qualified Signal Providers that provide customer notification services.

- Qualified Signal Provider transmits Stage 2 emergency message to Customer.

- Customer’s PCT/home energy management system receives Stage 2 emergency message.

- Customer’s PCT/home energy management system confirms receipt of Stage 2 emergency message to Qualified Signal Provider.

- Customer’s PCT/home energy management system changes temperature setting according to received message

- Customer’s PCT/home energy management system prevents changes to temperature setting for a specified period of time or until emergency event has ended.

- Customer’s PCT/home energy management system waits for specified period of time or until a emergency event message is received and then returns temperature setting to the normal program.

Less and Leslie Watts left for work around 7:30am a few minutes after their kids ran out the door to catch the school bus.  Although the house was now empty, Less’ energy management program is beginning the second phase of his bill management routine.  Phase 1 began around 4:00am, when the water heater began pre-heating water in anticipation of the family’s regular morning schedule.  Before she left for work, Leslie placed a load of dirty clothes in the washing machine and filled the dishwasher.  Timers on both appliances were pre-set to start and complete their cycles before the peak rating period began at 11:30am. Phase 2 of the energy management schedule included the following:

8:30am – The dishwasher starts its 90-minute cycle and the HVAC system begins pre-cooling Zone 1, which includes the kitchen and family dining areas.  Pre-cooling lowers the temperature in Zone 1 from its normal 780 set point to  720  and then establishes a maximum set point of 800 for the peak hours of 11:30am to 6:00pm.    The pre-cooling start time is automatically determined by the home energy management system.  The system automatically monitors inside and outside temperatures and determines that precooling will take about three hours and conclude just before the peak rating period begins at 11:30am.  The dampers and sensors in HVAC Zones 2-4 have been programmed to keep temperatures at or below 760 during. the pre-cooling period.  The dampers will be closed and no cooling load will be provided to  Zones 2-4 during the peak hours unless temperatures exceed 840.  The precooling schedule and minimum-maximum temperature settings were established by iterative routines in the vendor provided home energy management system.

9:45am - The water heater begins a heating cycle both to supply the washing machine that is scheduled to come on at 10:00am and to pre-heat water for the post peak period hours when the Watts family kids are cleaning up and preparing their evening meal.

10:00am – The washing machine automatically begins its 45-minute cycle.  Less used the home energy management system to interlock the operating times of the clothes washer and dishwasher to prevent them from coming on at the same time.  While Less’ utility rate doesn’t provide any financial incentive to minimize off-peak demands, it seemed like the efficient thing to do.

11:30am  The dishwasher, clothes washer and water heater are interlocked to stay off during the entire peak period.  The HVAC system has completed its pre-cooling cycle with Zone 1 reporting a temperature of 720 and Zones 2-4 reporting 760 .  The refrigerator automatically goes into low power mode.  A light on the refrigerator lets the user know it is in a low power mode and to minimize how many times they open the door.

By 11:30 am, the Watts household load has been minimized and is registering about 0.5kW, where it will stay until the peak period concludes at 6:00pm.  Zone temperatures, the status of each appliance and the household load are displayed on the monitor sitting on the kitchen counter.

Wednesday, July 22, 2015, 2:30 pm

The Watts house is quite.  The display monitor emits an audible beep and the message in the upper portion of the screen changes to report that a critical peak period is now in effect.

Wednesday, July 22, 2015, 4:00 pm

The Watts house is still quite.  The display monitor emits an audible beep and the message in the upper portion of the screen now reports that the local utility has called a Stage 1 system emergency.  The Watts home energy management system verifies that the appliance interlocks are still active and all Zone temperatures are within the established settings – no action is required.

At 4:01pm the display monitor emitted a series of beeps.  The message in the upper screen begins flashing that a Stage 2 emergency is now in effect.  The Watts home energy management system, in compliance with State code, automatically places a minimum 60-minute non-over-rideable lock on the HVAC system.

Wednesday, July 22, 2015, 6:15 pm

At 6:15pm Less Watts and his two children arrive home.  Both kids are hot and dirty from after-school activities.  They dash off to their rooms to change into their bathing suits and then head out to the pool.  Temperatures in their bedrooms, in Zone 3, are registering 840.  On their way through the kitchen to the pool both kids complain to their father of being too hot.   Less notices that the monitor is reporting a Zone 1 (kitchen)  temperature of 810.  He also notices the flashing message in the upper portion of the screen reporting that a Stage 2 emergency is still in effect.  Less grabs a cold drink from the refrigerator and joins his kids in the pool.

At 6:35pm the display monitor emitted another audible beep and the message changed to report that the Stage 2 emergency was over.  The Watts home energy management system slowly brought up the HVAC system, first in Zone 1 and then progressively in Zones 2-4.  The refrigerator went back to normal operation and immediately began making ice and cooling water.

When Leslie retuned home at 6:45pm, the kitchen temperature was registering 790.  She quickly joined the rest of her family at the pool.

A Vision of Demand Response – 2015

Scenario 3 - Large Commercial / Industrial

MegaOffice is one of the largest high-rise commercial office complexes in the downtown area.  It provides premium office, conference and limited retail space for top financial, legal and other service organizations.  In 2005 MegaOffice volunteered to participate in a field trial for a demand response program referred to as “AutoDR”.   They were concerned about the mandatory CPP rates being adopted as part of a CPUC regulatory proceeding and wanted to investigate potential options that might provide them with better energy cost management capabilities.  Participation in the AutoDR program turned out to be much more productive than they anticipated.

As part of the recommissioning step, where all of their environmental, internal operating systems and energy management system were tuned up and recalibrated, they discovered a number of operating inefficiencies that when corrected immediately resulted in substantial energy and bill savings.  They also were able to identify relatively easy measures to support short-term price-based demand response that included resetting cooling tower temperature set points, modulating air handling equipment and temporarily turning off decorative and unnecessary lighting.  The AutoDR approach worked so well that MegaOffice expanded the automated control systems to include more of their lighting and air handling equipment.

In 2006 the distribution circuits supplying MegaOffice and other major business establishments in the area encountered congestion problems that resulted in several emergency calls from their utility warning of potential short-term outages.  Instead of just arbitrarily dropping load or closing parts of their facilities as they had in the past, MegaOffice and several other businesses activated their preprogrammed AutoDR response.  The resulting load reductions proved effective, buying sufficient time for their utility to complete system upgrades and avoid any disruptive outages.

Following those events, MegaOffice’s utility instituted a revised AutoDR package linked to CPP and to local system emergency conditions.  By 2009 most business establishments with energy management systems had established AutoDR programs capable of responding to CPP price or utility emergency calls.

As part of their utility service package, MegaOffice was provided with wireless access to the 15-minute interval data from the half-dozen meters serving their facility.  Internet links to a utility application database also provided them with capability to monitor their actual bill in near real-time.  This information was linked into MegaOffice EMS and simultaneously provided to both the corporate offices in Minnesota and to the corporate energy consultants in Georgia.

Access to other utility provided applications and databases provided MegaOffice with technical and financial tools for evaluating the latest lighting, building automation and environmental systems.

Day #1:  Normal Operations / Anticipated Critical Peak Conditions

Tuesday, July 21, 2015, 5:30am

MegaOffice building supervisor was just completing his review of the energy management system (EMS) daily diagnostic reports and their latest quarterly corporate evaluation of the facility energy costs.  All systems were operating within acceptable parameters.  Enhanced automation systems installed last year now provided detailed diagnostics for every major control point in the facility.  These new systems also included several automated ‘self-healing’ routines that automatically kept systems properly calibrated.

10:20am, Tuesday, July 21, 2015:

MegaOffices’ building supervisor logged in a utility provided critical peak alert for Wednesday, July 22nd .  To make sure they were prepared, he initiated a diagnostic test of their new multi-level AutoDR response strategies.  Expanded automation of building systems now made it possible for them to identify separate price and emergency response protocols.  Due to contractual requirements in their tenant leases, MegaOffice price response strategy was designed to produce no more than a 10-15% reduction in facility load.  Iterative testing over the years showed that a 10-15% short-term reduction was possible without violating lease conditions or creating tenant discomfort or inconvenience.  MegaOffices emergency response strategies were designed to produce a much larger 20-30% reduction in facility load.  Supplemental ISO emergency surcharges added in to their underlying utility rate made it economically very attractive to increase their emergency load reductions.  MegaOffices’ reduction also improved the likelihood that any emergency would not progress to a full rotating outage, with much more severe economic and operating consequences.  EMS diagnostics indicated that all AutoDR routines were operating as planned.

Because of the day-ahead warning, the building supervisor activates a pre-cooling strategy for the following day.  Enthalpy controls will start bringing in outside air to pre-cool the eastern zones of the building during the early morning hours.  Building HVAC systems will provide supplemental cooling based on weather forecasts to bring the zone temperatures to pre-defined set points that should be sufficient to let MegaOffice substantially reduce demand through the peak period and coast through at least part of the late afternoon critical peak hours.

Day #2:  Critical Peak / Emergency Conditions

Wednesday, July 22, 2015, 5:30 am

MegaOffice building supervisor has been monitoring the pre-cooling effort that started about one hour earlier.  Enthalpy controls started bringing in cooler outside air lowering internal building space temperatures from their standard 750 to 700.  The eastern facing zones are being pre-cooled first because they get the morning sun.  All remaining building zones will be rotated in until the pre-cooling routine shifts over to building mechanical systems sometime before 9:00am.

Wednesday, July 22, 2015, 8:30 am

By 8:30am the entire MegaOffice facility has been pre-cooled to the target set point.  Email alerts from their local utility appear on the supervisor display monitor confirming a critical peak likelihood later in the afternoon.

By 10:00am, building mechanical systems are providing the first cooling to some of the eastern facing retail areas which are experiencing higher than expected foot traffic.

By 11:30am, the building EMS has settled into its normal peak-off peak building management pattern.

Wednesday, July 22, 2015, 2:30 pm

At 2:30pm a message from the local utility alerts the building supervisor that the critical peak price is now in effect.

MegaOffice AutoDR program began to slowly ramp down lighting levels in most of the building public and private areas starting at 2:00pm so that by 2:30pm most non-critical lighting was operating at about  65% of its regular load.  Under the AutoDR operating strategy, cooling tower set points were raised, several of the less necessary elevator banks and  all decorative lighting and fountains have been curtailed.  According to the EMS, building load is leveling off at between 88-90% of the previous days load.  Temperatures in portions of the western zones are beginning to rise above the normal set point target.  Because of the critical peak, temperatures will be allowed to rise to 770 or 20 above their normal set point.  The EMS forecasting applications project that because of the outside heat, building mechanical systems will have to ramp back to full capacity by 4:00pm.

Wednesday, July 22, 2015, 4:00 pm

At 4:00pm MegaOffice building supervisor received the Stage 1 emergency message from his local utility.  The Stage 1 alert automatically triggered MegaOffice Phase 2 AutoDR energy management strategy.  Additional banks of non-essential lighting were turned off while others were reduced to roughly 50% of their normal level.  Cooling tower set points and interior temperatures were raised another  20 .

Within two minutes, the MegaOffice building supervisor received the Stage 2 emergency message.  The EMS automatically switched substantial portions of the MegaOffice load to onsite gas powered emergency generators, dropping the building load to roughly 45% or its normal 4:00pm demand.

By 4:30pm, the end-of-day routine was well under way with approximately 20% of the building tenants headed home.  Building loads started their normal late afternoon decline.  By 5:30pm approximately 40% of the building tenants were gone, load had declined substantially, interior temperatures had stabilized and the emergency generators were being ratcheted back to about 50% of their previous operating level.

Wednesday, July 22, 2015, 6:15 pm

At 6:35pm the Stage 2 alert ended, all the emergency generators were shut down and MegaOffice EMS went into a recovery mode.  All interior temperatures and other building operating systems were back in full evening operation by 8:00pm.

A Vision of Demand Response – 2015

Scenario 4 – Utility Company

AMI systemwide implementation together with development of the SPMS has provided the investor-owned and municipal utilities with a wide range of system operating and customer service applications.  As a result, customer information systems (CIS), billing, outage management, maintenance management, trading, and forecasting have all undergone major application changes.

A variety of customer information services have been introduced, including graphical bill analysis and Internet and hard copy subscription-based load data and cost analysis.  One of the more innovative services is a wireless display that can be rented from local utility and local community library facilities that provides customers with near real-time load monitoring and billing information for their account.  Customers usually subscribe to this information service for one or two months at a time when they have a billing problem due to a unexplained usage patterns or when replacing a major appliance.  Embedded applications and data bases, accessible through the display device can be used to help customers evaluate the potential bill impacts of various appliance upgrade and other efficiency alternatives.  Applications actually allow customers to model the potential energy and cost impacts on their facility, to identify potential rebates, store locations, installers and financing options.  Printed reports can be downloaded to their own computer or mailed by the utility.  Customers can also link into the same utility databases and applications using their own wireless displays or home computers and subscribe to the service for a nominal cost.

Day #1:  Normal Operations / Anticipated Critical Peak Conditions

10:00am, Tuesday, July 21, 2015:

As part of their normal daily operating procedure, customer service representatives, distribution engineers and trading staff review the forecasts of yesterday’s operations along with 24, 48 and 72-hour forecasts of weather and system load conditions at all major transmission and distribution locations within their service territory.  ISO Advisory Warnings (AW) are also noted and logged.

Customer service representatives notice the forecasts predict a continuation of the heat wave through the end of the week.  Internal supplemental forecasts identify a higher than acceptable potential for critical peak cost increases.  In addition, data monitoring activities indicate that certain feeders are approaching threshold conditions that might lead to unacceptable voltage and other reliability problems.

10:15am, Tuesday, July 21, 2015:

While reviewing the daily operating reports, customer service representatives received the ISO critical peak advisory for their Southern Central Valley region.  This automatically triggered a utility generated “Critical Peak Alert”.  Critical peak alerts are broadcast through their communication provider to all PRD’s in the targeted portion of their service area, posted to the utility web site, reported in a banner in local newspapers and distributed to targeted critical customer lists by email.  Critical peak alerts provide customers with advance notice of expected critical peak pricing events.  They also encourage customers to review their facility operating systems and make sure their backup generation and AutoDR emergency response options are in good working order.  These alerts also provide customers with PRD devices advance notice that higher prices may be forthcoming.

SPMS reports also highlighted several distribution feeders that were potential candidates for heat and cooling load problems.  As a result, tree trimming and maintenance crews were redirected today to accelerate scheduled work on the most severely impacted areas.

Day #2:  Critical Peak / Emergency Conditions

11:01am, Wednesday, July 22, 2015

Critical peak price alerts for Thursday, July 23rd are automatically received by the customer operations center.  Critical peak price alerts automatically generate a series of computerized action plans that identify price alert maps (PAM) by substation and feeder.  Price alert maps identify which groups of substations and feeders should receive critical peak price alerts based on their relationship to supply, T&D and existing system maintenance activity.  Price alert maps also identify and recommend customized dispatch strategies by substation and feeder locations to account for the potential duration and intensity of potential critical peak price alerts.

Operators carefully review the price alert maps and modify the recommended strategies to reflect more current information regarding distribution and other system maintenance activity.  Ongoing transformer replacement and tree trimming activities in two critical areas necessitate modifications to the PAM to balance loads and avoid interfering with critical upgrades.

12:00 noon, Wednesday, July 22, 2015

Operations supervisors have reviewed and approved PAM’s for Thursday, July 23rd.  Operators activate the PAM and critical peak price alerts are automatically dispatched through a sideband of the State broadcast system and through all registered signal providers to the targeted substation and feeder locations as well as to licensed third-party signal providers.

A Vision of Demand Response – 2015

Scenario 5 – California ISO

Each morning, analysis models, linked into the real-time database maintained by the Statewide Power Management System (SPMS) produce dynamic reports comparing transmission, substation and selected feeder loads for the previous five days with forecasted loads for the next three days.  The SPMS was actually designed as a series of independent systems and databases that are maintained by each utility (investor owned and municipal) linked through the Internet.

Analytical models at both the ISO and utilities, continually integrate and evaluate generator availability, maintenance schedules, and outage information together with weather, actual load, voltage and frequency, and measurements of other system harmonics into hierarchical reports to support resource trading desk and other system operating and emergency activities.  The SPMS reports provided to ISO system engineers include substantially refined estimates of expected supply, demand and the status of reserves throughout the state.

Automated routines under the SPMS conduct daily system tests to calibrate PRD emergency capability by substation and select-feeder locations.  Equivalent to the notch tests conducted for the original air conditioning load control programs back in the early 1980’s and 1990’s, SPMS PRD daily tests randomly dispatch a minimized emergency signal that either increases (summer) or decreases (winter) residential and CI HVAC settings by two degrees (20), just enough to temporarily drop each connected load to allow measurement by real-time metering located on each substation and feeder circuit.  SPMS PRD test signals occur at different times each day and at most last for minimum HVAC cycles, which is usually less than 10 minutes.  Interval load, temperature, voltage, frequency and other system harmonics are automatically archived in a master databases maintained by each utility.  Utility master databases are linked into the ISO via secure high-speed wireless Internet connections.

The database of SPMS PRD test results accumulated over the last five years provides the ISO with the capability to construct isograms that estimate the emergency load available by hour and temperature at each major feeder location.  The database of isograms plotting PRD controllable load are dynamically integrated into emergency dispatch algorithms that allow system operators to target and scale emergency load relief to specific feeder and delivery point needs.

Dynamic algorithms link to real-time monitoring of each targeted area provide a closed loop confirmation and adjustment function to assure achievement of emergency load objectives.  Using threshold criteria to trigger activation, dynamic algorithms use historical isograms to automatically determine the optimum control strategy for each feeder.  Control strategies balance the HVAC temperature change and available customer load necessary to protect the system.  With real-time monitoring, the dynamic algorithms can compare the actual load reductions achieved with the load reductions needed and instantaneously adjust the control strategies automatically upward or downward to maintain system balance.  Because of the large amount of load under control, emergency PRD operations only rarely result in HVAC temperature changes of more than one degree during a typical two-hour event and generally no more than two degrees during a four-hour event.

Dynamic algorithms under ISO supervision, can automatically schedule emergency PRD load reductions hours in advance to anticipate potential loading problems due to supply demand imbalances or voltage and frequency problems.  Real-time monitoring under the SPMS also allows fully automatic PRD dispatch based on threshold criteria during system emergencies.

Day #1:  Normal Operations / Anticipated Critical Peak Conditions

10:00am, Tuesday, July 21, 2015:

As part of their normal daily operating procedure, system engineers review the forecasts of yesterday’s operations along with 24, 48 and 72-hour forecasts of weather and system load conditions at all major transmission and distribution locations.

Although parts of the state have been experiencing a prolonged heat wave, forecasts do not yet highlight any immediate system imbalances or potential emergency situations.  Although supplies are tightening and reserve margins and system costs are still within acceptable limits, forced outages of several utility and customer resources are highlighted by SPMS reports as a potential problem area.  As a result, the forecasts indicate that load, weather and supply conditions could trigger a critical peak price event in the Southern Central Valley regions during the hours from 3:00 to 5:00pm on. Wednesday, July 22nd.

Because of the tightening supply conditions and projected load forecasts, at 10:05am the ISO authorized the issuance of critical peak advisories through the California State Reliability Exchange (Reliability Exchange) for all utilities in the affected regions  Critical Peak Advisories encourage utilities and customers to prioritize critical system maintenance activities and tune up internal systems that might be needed should prices and reliability conditions worsen.  The ISO critical peak advisories were dispatched through a secure Internet connection to all utilities and other load serving entities.

Day #2:  Critial Peak / Emergency Conditions

10:00am, Wednesday, July 22, 2015:

Due to restricted supply conditions, Cal ISO forecasts estimate 200-400 percent increases in peak hour prices for Thursday afternoon, July 23, 2015.  Reserves on Tuesday briefly dipped below 10%.  With today’s expected high temperatures and critical peak prices forecasts don’t look good for Thursday.  Reserves are projected to be very close to the 7% threshold and SPMS reports indicate that any additional forced outages would trigger reliability events.  SPMS monitoring shows that critical congestion has now spread out of the Southern Central Valley region into the entire Central Valley, the Southern desert and throughout the entire LA basin.

Cal ISO system operation models estimate that customer price response will produce peak load reductions of 8-12 percent, which should be more than adequate to maintain system reserves.  Continuously updated load and system harmonic data from the real-time SPMS confirm that up to 25% of targeted substation loads are available through the emergency PRD system should supply and/or other system conditions worsen.  Forecasts target and identify specific substations and distribution points where supply / congestion problems will be most severe.

11:00am, Wednesday, July 22, 2015:

Cal ISO 24-hour price forecasts and a critical peak price alert for Thursday, July 23rd are automatically posted and dispatched via the Internet to the California State Reliability Exchange (Reliability Exchange).  The  Reliability Exchange is a secure Internet site maintained by the ISO that provides open access to ISO price and reliability forecasts on a weekly, daily and hourly basis accessible to energy utilities, consumers and energy / demand response providers.  Secure portions of the Reliability Exchange provide automatic notification and coordination between the State investor owned and municipal utilities and licensed third-party signal providers.

A Vision of Demand Response – 2015

Scenario 6 – California Public Utilities Commission

As a result of the CPUC decisions in 2006 that made Critical Peak Pricing (CPP) the default tariff for all customers, demand response (DR) and energy efficiency (EE) were now fully integrated into all customer service agreements.  The CPUC also updated utility outage management plans to reflect the emergency system protection capability included under CEC Building and Appliance standards for price responsive devices (PRD) and functionality.

The time-of-use component of the CPP rate together with the critical peak prices during an expected average year, provide customers with clear incentives to evaluate efficiency investments.  Incorporating the critical peak prices in the tariff provides customers with clear incentives to consider major appliance and other purchases that accommodate load shifting and automatic reductions in response to either price or reliability events.

Establishing CPP as a default tariff also simplified what had been a twenty-year menu of continually changing utility sponsored DR programs.  Under the CPP tariff customer incentives come from avoiding the use of expensive energy during critical peak times.  Customer incentives are now directly related to how each customer changes their energy own usage pattern, not whether they sign up for a specific DR program.  Paying customer for performance rather than participation had several other major positive impacts.  First, because customers were now avoiding the use of high cost energy, utility revenue requirements and rates actually went down.  Paying customer incentives out avoided utility costs actually raised revenue requirements and rates.  Most significantly, the artificial boundaries imposed by previous rate DR program structures were now eliminated, allowing each customer to do as much or as little as they wanted in defining how they would respond.  The CPP tariff eliminated the overlapping incentives and restrictive participation rules that characterized the previous mix of a rate and DR programs.  Implementation of the CPP tariff also eliminated many of the utility sponsored EE subsidies.

A review of EE cost effectiveness revealed that CPP and the underlying time-of-use rate actually improved the return on investment and accelerated payback periods for most critical lighting and HVAC related applications.  As a result a variety of new subsidies were developed to overcome purchase resistance and financing rather than long run cost effectiveness.   Utilities efforts to integrate EE and DR were now much easier given the simplified price signals provided by CPP.  Utilities EE and DR activities switched from program management to customer education, customer information services, the evaluation of alternative automation and efficiency upgrades, and vendor and product referral services – efforts to emphasize and assist customer adaptation to the CPP tariff.

Rate impact studies showed that CPP rates were easier for customers to understand.  Rate stability over the last nine years also provided more certainty that made residential and commercial/industrial (CI) investment in EE less risky for all major lighting, HVAC and facility automation related modifications.  Targeted subsidies for renewable and distributed generation, facility automation, and other selected options continued to be supported on an as-needed basis.  A few ISO supported reliability-based options also received continuing support.

The integration of DR and EE under the CPP rate also eliminated the restrictions previously imposed on the Public Goods funds.  While the public goods charge was reduced by about two-thirds several years ago, the remainder was now directed to support utility directed customer education, information services, public interest research and product evaluation and certification tasks in support of both EE and DR.

A recently released CPUC report confirmed that the price responsive device (PRD) functionality standards imposed under the CEC Building and Appliance Standards was now producing substantial energy conservation as well as demand response impacts.  While prior studies showed that approximately 60-70% of all customers were not using the basic programmable capability of their existing thermostat, opting instead to manually control temperature settings, new utility studies now show that only 25% of the customer population continue to operate in the manual mode.  The remaining 75% have implemented one or more of the default lifestyle settings required by the Building and Appliance standards

Utility and ISO studies also conclude that customer price responsive, non-reliability capability under the CPP tariff is producing 6-8% reductions in gross summer peak system load in response to day-ahead notification.  Voluntary reliability responsive capability under the CPP tariff and PRD operation is producing 12- 18% reductions in gross summer system peak load in response to day-of notification.

Utility and ISO studies also confirm that system tests of PRD emergency, non-override operations can consistently produce 30-35% reductions in gross summer peak system load on selected feeders in high temperature zones and 8-15% reductions in peak load on selected feeders in winter.

Utility outage management reports show steady reductions in outage frequency, duration and better targeting of tree trimming and other general maintenance dollars – producing increases in net system benefits over original projections from AMI and related business case studies.  Utility reports indicate reductions of almost 50% in unserved kWh per outage due to faster recovery for the projected time period to-date.

Load and reliability analysis for selected feeders continue to show substantial potential for distributed generation at targeted office parks and retail centers, based on enhanced customer monitoring of AMI data.

As a result, CPUC decisions continue to authorize increases in the allowed contribution of DR as a reliability resource under resource adequacy guidelines.

Customer price response in conjunction with the use of PRD’s to manage distribution congestion resulted in much higher utilization rates for base load generation and the elimination of most peaker plants.  System reliability measurements based on customer minutes of outage per year showed almost continuous improvement over the last five years.

An emerging development was the recent formation of an industry driven organization to investigate the potential for DR reliability-based trading credits.  Worsening transmission and distribution congestion in several geographic areas spurred manufacturers and high tech companies to evaluate options for further improving system reliability and power quality.  An industry funded report highlighted the opportunity created by common transparent system wide rates and the success of PRD’s.  The report points out that corporate subsidies to further improve non CI price and reliability response on selected distribution circuits could be less expensive than investing utility ratepayer funds or paying to upgrade their own sites.  The industry organization has indicated they will be soon be filing an application for a targeted demonstration pilot on a critical feeder in Northern California.

Annex G: Material related to Joint IOU PCT Specifications using Two-Way Communications for Extended Functionality

Annex G1: Digital Control Interface

Annex G2: Reliability Event Commands

Reliability Event – Change Temperature

| Reliability Event (change temperature) Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Command Code | INT8U | (ex: 3) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Start_Time | <DTIME> | Event begin time | M |
| Stop_Time | <DTIME> | Event end time | M |
| Event_ID | <EV_ID> | Identifier of this price event (used for cancellation) | M |
| Temp_Change | INT8U | Amount to change setpoint in 0.1 degree Celsius | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Note:  Setpoint change sign is not specified – the thermostat knows which direction to change based on current mode for energy savings

Reliability Event – Set Temperature

| Reliability Event (set temperature) Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Command Code | INT8U | (ex: 4) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Start_Time | <DTIME> | Event begin time | M |
| Stop_Time | <DTIME> | Event end time | M |
| Event_ID | <EV_ID> | Identifier of this price event (used for cancellation) | M |
| New_Temperature | INT16U | New temperature setpoint, in tenths of a degree Celsius | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Price Event Command – Level Based

| Price Event Notification |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 22) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Current Price Level | INT8U | Example: 1=normal price, 2=peak price, 3=emergency price, etc. | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Note:  This message takes effect immediately – no intentional delay

Annex G3: Message Commands for Joint IOU PCT Functionality using Two-Way Communications

(Previously referenced in Section 4.3.4)

The Joint IOU document describes additional features beyond the Title 24 PCT requirements which enhance the user interface of the PCT. Two application enhancements are made: simple determination of the PCT installation, and a direct display of the current price.

Upon installation of the PCT, the installer will want assurances that the device is operating properly. The utilities are concerned that customers will contact them upon PCT installation to determine whether connectivity has been achieved. These calls can be avoided by having the PCT indicate connectivity. This connectivity is detected by the presence of received messages. The “connection operational” indicator on the PCT can be activated quickly if messages are sent periodically to the PCT (perhaps a few times per day). These are termed “keep-alive” messages.

The utilities have also recognized the fact that demand response can be increased if the customer has direct knowledge of the cost of energy. The concern, however, is that a display capable of indicating an exact price adds significant cost to the PCT. Therefore, the utilities believe that price levels (A-B-C), which are simpler to display, would be more useful for the price sensitive PCT applications.

Status Request

| Keep-alive Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 27) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Notes:  Request PCT response to confirm connectivity and availability

Update Firmware

| Keep-alive Command |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Message_ID | <MSG_ID> | Sequential ID for this message | M |
| Command Code | INT8U | (ex: 28) | M |
| Address | <ADDR> | Which PCTs should use this information (this may be ignored) | M |
| Event_ID | <EV_ID> | Event ID used to uniquely identify this firmware update | M |
| SW_Version | BSTR16 | 16 byte firmware version ID being uploaded | M |
| Num_Blocks | INT16U | Total number of blocks in firmware update | M |
| Block_ID | INT16U | This block number | M |
| Block_Data | BSTR1024 | 1024 byte firmware data block | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Notes:  This message is used to send new firmware to the PCT.  The contents of the firmware data blocks are proprietary to the vendor.  The PCT should be capable of buffering all blocks received until a complete new firmware image is received and validated at which point it will be installed and activated.  The PCT watchdog should be capable of reverting to the last known good firmware image if a newly uploaded image fails to operate properly upon activation.  The sending system should retransmit all blocks at least one – preferably several times – to ensure that all PCT’s have received the update.   The PCT will ignore update commands if already operating at that version.  In two way systems, the status message may be used to determine the currently running firmware version.

Annex G4: Message Responses for Joint IOU PCT Functionality using Two-Way Communications

The addition of two-way communication capability can increase the capabilities of the DR system. These improvements allow the utilities to observe the response to DR signals by individual users. These messages are transmitted from the PCT to the utility.

For example, the utility could receive a response when a valid request has been received by the PCT.  This response could include the actual customer response to the DR signal. Another use for two-way communications would be to indicate that communications had been restored to the utility.  This frequent occurrence of this signal would indicate a pending failure in the communications system.

Price Message Acknowledgement

| Price Acknowledgement |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Command Code | INT8U | (ex: 101) | M |
| Address | <ADDR> | This indicates the PCT address / Customer ID | M |
| Event_ID_Ack | <EV_ID> | Identifier of price event being acknowledged | M |
| Action_Taken | INT8U | Ex: 1=accepted, 2=overridden, 3=in progress | M |
| Action_Time | <DTIME> | Time stamp of action taken | M |
| New_Temperature | INT16U | New temperature setpoint, in tenths of a degree Celsius | O |
| Temp_Change | INT8S | Amount setpoint has been changed (in tenths of a degree Celsius) | O |
| Load_Reduction | INT16U | Estimated average amount of curtailed load in units of 100’s of watts | O |
| Crypto | <CRYPTO> | Message integrity value | O |

Reliability/Emergency Message Acknowledgement

| Emergency Acknowledgement |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Command Code | INT8U | (ex: 102) | M |
| Address | <ADDR> | This indicates the PCT address / Customer ID | M |
| Event_ID_Ack | <EV_ID> | Identifier of price event being acknowledged | M |
| Action_Taken | INT8U | Ex: 1=accepted, 4=exempt (e.g.: for medical reasons), 100=error_general, 101=error_energy_increase, etc. | M |
| Action_Time | <DTIME> | Time stamp of action taken | M |
| Load_Reduction | INT16U | Estimated average amount of curtailed load in units of 100’s of watts | O |
| Crypto | <CRYPTO> | Message integrity value | O |

Communications Established/Restored

| Restoration |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Command Code | INT8U | (ex: 103) | M |
| Address | <ADDR> | This indicates the PCT address / Customer ID | M |
| Crypto | <CRYPTO> | Message integrity value | O |

Note:  This can be used to verify initial enrollment as well as basic communications restoration logging.

Status Request Response

| Restoration |
| --- |
| Attribute Name | Attr. Type | Explanation | M/O |
| Data |
| Command Code | INT8U | (ex: 104) | M |
| Address | <ADDR> | This indicates the PCT address / Customer ID | M |
| Action_Taken | INT8U | Ex: 6=PCT OK, 7=Firmware upgraded OK, 100=error_general, etc. | M |
| Action_Time | <DTIME> | Time stamp of action taken | M |
| HW_Version | BSTR16 | 16 byte string representing hardware version | M |
| SW_Version | BSTR16 | 16 byte string representing software version | M |
| Available | INT16U | Estimated amount of curtailable load in units of 100’s of watts | O |
| Equipment_Type | INT8U | 0=unknown,1=furnace,2=airconditioner,3=furnace/AC,4=heat pump | O |
| Temperature | INT8U | Current temperature (in tenths of a degree Celsius) | O |
| Setpoint_Heat | INT8U | Current setpoint temperature (in tenths of a degree Celsius) | O |
| Setpoint_Cool | INT8U | Current setpoint temperature (in tenths of a degree Celsius) | O |
| Mode | INT8U | Current mode (0=off, 1=heating, 2=cooling, 3=auto) | O |
| InHold | INT8S | 0=PCT not in Hold Mode, 1=Hold button activated | O |
| Fan | INT8U | 0=off, 1=on, 3=auto | O |
| Running | INT8U | 0=off, 1=Fan, 2=Compressor, 3=Both | O |
| Crypto | <CRYPTO> | Message integrity value | O |

Note:  This can be used to verify available curtailable load and validate usage habits

Annex G5: 	Transaction Sequences for Systems 
using Two-Way Communications

(Previously referenced in Section 4.4.2)

Figure 11 Two-Way ‘Critical Peak Price’ Event

Figure 12 Two-Way Emergency Event

Annex G6: 	IOU Use Cases for PCTs 
using Two-Way Communications

Scenario 1 – PCT Installation, configuration and program enrollment

- The home builder or customer installs the PCT and an appropriate communications module in a new home being constructed or qualifying re-model.

- Customer moves into a new home.

- Customer contacts the local utility, the customer’s identity is confirmed and they are provided instructions to activate the communications aspect to the PCT.

Scenario 2 - Utility dispatches grid reliability DR program and controls the load by communicating with the PCT

- CAISO (electricity grid operator)/gas distribution system operator notifies utility of the need to drop load for grid reliability.

- Utility sends communications message via Utility Communication Infrastructure (UCI) to PCT.

- PCT acknowledges receipt of signal back to Utility and curtails load.

- PCT restores load to the user specified set points after an event has expired or a command is received via the UCI.

Scenario 3 - Utility dispatches for economics or calls a price responsive DR program and controls the load by communicating with the PCT

- Customer receives notification of event and for price response the appropriate pricing information

- Economic or price event is activated and load drop occurs.

- Customer chooses not to participate in economic or pricing event.

- PCT restores load to the user specified setpoints after an event has expired or a command is received via the UCI.

Scenario 4 - Customer receives utility bill and would like to confirm the correct credit/charge was applied

- Customer receives the bill, with credits/penalties applied.

- Customer views a log of events on the thermostat.

Scenario 5 - Customer confirms that the DR event has ended, but the A/C does not work.

- Customer attempts to turn on A/C but the HVAC does not respond.

- The PCT, after a configurable delay at the end of the DR event or a default time period from the start of the event, enables the override/restore button to reset the PCT defaults and restore normal operations.

- If step 2 fails, customer calls the utility to report problem. Utility confirms no event in progress, UCI or AMI indicates normal state, and recommends that the customer contact their thermostat manufacturer or HVAC installer to troubleshoot.

# Footnotes

E. W. Gunther, “A Strawman Reference Design For Demand Response Information Exchange”, CEC PIER Consultants Report, October, 2004

The specific design of such features (e.g. HOLD, OVERRIDE) is defined by individual vendors and not by this document.

NEMA DC 3-2003 - http://www.nema.org/redirect/redirectFile.cfm?ID=3528&user=109127&filename=/DC3.pdf

MultiMediaCard Specification Summary Version 3.31 March 2003 - http://www.mmca.org/compliance/buy_spec/MMC-System-Summary-v3.31.pdf

Developed by the Radio Broadcast Data System (RBDS) Subcommittee of the National Radio

Systems Committee (NRSC) - ftp://ftp.rds.org.uk/pub/acrobat/rbds1998.pdf

Average load response during the SPP was 0.56 kW per PCT. The estimate here uses a range of 0.1-0.4 kW per PCT to be conservative and also account for temperature variations (lower temperatures induce smaller response).

Assuming about 1500 MW of interruptible and AC load control programs.

Load drop depends on severity of temperature setup, with maximum of 15% being all central AC load statewide.

Based on estimated circuit load range of 500-2000 MW (I’m checking on these numbers)

# Text boxes

Figure 10  Further Examples of Possible Thermostat Displays

Figure 9  Examples of Using Standardized Icons to Create Alternate Displays