November 21, 1997

Contract # TW-0928

SPECIAL SPECIFICATION

SECTION 15495-S

LIQUID NITROGEN SYSTEMS

Page

PART 1 - GENERAL

1.01 	Materials and Operations	2

1.02	Applicable Specifications and Standards	2

1.03	Design	3

1.04	Submittal Drawings	3

1.05	Shop Drawings Submittals	3

1.06 	As-built Drawings	3

PART 2 - PRODUCTS

2.01	Piping	4

2.02 	V.I.P. Components	4

2.03 	Pressure Gauges	4

2.04 	Joints on Vacuum Insulated Pipe	4

2.05 	Ball Valves	5

2.06 	Vent Valve	5

PART 3 - EXECUTION

3.01 	General	6

3.02 	Workmanship	6

3.03 	Tests	8

SPECIAL SPECIFICATION

SECTION 15495-S

LIQUID NITROGEN SYSTEMS

PART 1 GENERAL

1.01	MATERIALS AND OPERATIONS

Material and operations required for the complete installation of piped cryogenic liquid nitrogen system using vacuum insulated pipe as shown on drawings, including design, shop drawings, equipment, piping, pipe fittings and components, operation instructions, identification, tests and sterilization.

Material required for a liquid nitrogen system using pre-insulated piping.

1.02	APPLICABLE SPECIFICATIONS AND STANDARDS

The following specifications and standards form a part of these Specifications.

Department of Transportation (DOT)

Department of Labor, Occupational Safety and Health Act (OSHA)

American Society for Testing Materials (ASTM)

American National Standards Institute (ANSI, B49.1, B57.1, CSA-B96)

Compressed Gas Association, Inc. (CGA)

National Bureau of Standards (Handbook 44)

National Association of Corrosion Engineers (NACE)

American Standard Code for Pressure Piping (ASA-B31.1.)

Ref.  SNL Specification Section 01700 “ Commissioning “.

1.03	DESIGN

The design and installation of the cryogenic liquid nitrogen piped system shall be complete with all necessary components and accessories for proper operation and delivery of product (LN2) and shall be accomplished according to the workmanship section of this Specification.  The installation shall comply with all mandatory advisory and recommended applicable rules of the latest editions of the drawings or specified herein. The Contract drawings are schematic only, indicating the piping sizes, the extent and general routing arrangement of the cryogenic liquid nitrogen piping systems.

1.04	SUBMITTAL DRAWINGS

These drawings shall follow as closely as possible the suggested routing of the Contract Drawings.  Any additional fittings or connections to facilitate easier installation shall be supplied by the Contractor at no additional cost.  These drawings and any changes are subject to approval by the SDR.  All submittals per 1300-S.

1.05	SHOP DRAWINGS SUBMITTALS

As soon as practical after award of Contract, and prior to fabrication, complete shop drawings of the LN piping system shall be submitted for approval.  No installation will be permitted prior to approval of complete shop drawings.  Submittal in sequence of complete shop drawings for individual or group installations may be permitted with proper programming and prior approval. All submittals per 1300-S.

1.06	AS BUILT DRAWINGS

Upon completion of the work, the Contractor shall revise all drawings to agree with the construction as actually accomplished and stamped “As-Built, No Change.”  The original “As-Built” drawings shall be delivered as directed.

PART 2  PRODUCTS

2.01	PIPING

V.I.P.:  Shall be a modular factory sealed high vacuum jacketed and all welded construction, schedule 5, type 304 stainless steel or invar-36% nickel alloy inner pipe and jacket pipe with multi-layer super insulation (alternating layers of glass fiber paper and aluminum foil).  Vacuum insulated pipe shall be of design and manufactured in accordance with ANSI Code Section B31.3.  V.I.P. shall have working pressure rating of 140 psig.  All vacuum jackets shall have molecular sieve, hydrogen getters or activated charcoal getter to assure vacuum longevity.  Evacuation pipe system shall be sealed at 10 microns or less in heated operating condition, without use of vacuum pump.  Pipe lengths shall be as per manufacturer’s standards.  Each pipe section shall have a vacuum test port with isolation valve.  The modular factory sealed high vacuum insulated pipe (V.I.P.) shall be as manufactured by the Cryogenic Energy Company of Minnesota Valley Engineering, Inc., Cryogen Services Inc., or CVI Inc.  Substitutions: only under provisions of Section 1600-S.

Pre-Insulated Piping:  3/4 inch, Type K copper tubing surrounded by 3 inch polyurethane foam insulation (factory applied).  “K” factory not to exceed 0.15 Btu-in/ft2 -hr-(F outer jacket to be PVC with a minimum of 110 mils thickness, all fittings to be pre-insulated.  Joints to be 45% silver soldered.  Southland cryogenics or approved substitute.

2.02	V.I.P COMPONENTS

Shall be of same manufacturer and specifications of V.I.P. used and ANSI Code, Section B31.3.  V.I.P. components such as “Bayonet Couplings,” “Flexible Sections, Etc., as determined by Contractor’s final design and layout.  Contract Drawings (being schematic only)  show minimum components required.

2.03	PRESSURE GAUGES

A.	Shall be suitable for cryogenic service, with range of 0-200 psig.

2.04	JOINTS ON VACUUM INSULATED PIPE

A.	Shall be as per manufacturer of (V.I.P.) pipe and fittings, standard band couplings and bayonet connectors, etc.  Covering of joints, elbows, tees, couplings, etc., shall be made in accordance with the manufacturer standard installation instructions and as indicated on Drawings.

2.05	BALL VALVES

Ball valves to have stainless steel ball and stem, brass body, polyfill seats, 7 inch stem extension solder joint end, 1.4 turn throttling range, 1,500 psi working pressure.  Worcester cryogenic ball valve, CVI, Inc., or approved substitute.

2.06	VENT VALVES

A.	A liquid/gas differentiating cryogenic control valve designed to vent generated gas without discharging the liquid.  The gas supply/pressure tap shall employ  rocess stream pressure to operate a pneumatic diaphragm of the normally closed cryogenic valve.

The liquid/gas differentiating cryogenic control valve shall be free from freeze-up.  CVI, Inc. GN2 Vent valve or approved substitute.

PART 3 - EXECUTION

3.01	GENERAL

The liquid nitrogen (LN2) modular factory seal high vacuum V.I.P.  system installation shall be coordinated with respect to space available with all other work to be performed by other trades on this occupancy.  In every instance where there is a conflict in the routing of  V.I.P. and other work, the V.I.P. shall  be coordinated with the other work. Installed V.I.P. shall not interfere with the operation or accessibility of doors or windows; shall not encroach on aisle, passageways, and equipment and shall not interfere with the servicing or maintenance of equipment.

It will be the V.I.P Contractor’s responsibility to make accurate measurements established at the construction site prior to placing order of V.I.P from approved supplier.  V.I.P. shall be factory fabricated and shall be worked into place without springing or forcing, properly clearing all openings and equipment.  Cutting or weakening of structural members to facilitate piping installations is not permitted.  Pipes shall be so installed as to permit free expansion and contraction without damage to joints or hangers.  Piping shall be run parallel with the lines of the building unless otherwise noted on the Drawings.  Unless otherwise shown on the Drawings, horizontal piping shall pitch down in the opposite direction of flow with grade of not less than 1/8” per foot.

3.02	WORKMANSHIP

General:  The vacuum insulated pipe manufacturer is required to prepare a written installation guide for use by the Contractor. These written instructions shall be approved by the SDR prior to installation of any vacuum insulated pipe.  The Contractor shall be entirely responsible for the quality of workmanship and for the satisfactory installation of the V.I.P. system.

The V.I.P. manufacturer shall assist the Contractor by training and instructing selected Contractor personnel in proper installation procedures and techniques.  Acknowledgment will be required in writing from the manufacturer listing the names of those individuals so qualified.  Personnel not qualified will not be permitted to work on V.I.P. systems.  Qualification can be obtained with training by manufacturer’s representative during installation of tracer line for V.I.P. system.  The V.I.P. Contractor’s project superintendent will assume the roll of coordinator between the manufacturer, his written instructions, and the project inspector.  He shall also be authorized by the Contractor and manufacturer to prepare and sign daily written reports during installation.  The reports shall cover unsatisfactory conditions, such as rejection of improperly factory sealed V.I.P. and improperly made up joints.  The Contractor shall take prompt action to return to the factory all damaged and defective materials and shall order prompt replacement of such materials.

Responsibility for Materials:  It shall be the Contractor’s responsibility to have V.I.P. manufacturer’s qualified representative at the construction site at the date of V.I.P. delivery to examine and inspect all vacuum insulated open products and materials delivered.  The Contractor and manufacturer’s representative shall read the vacuum on each section of pipe, using Hasting Vacuum Gauge Model TV-4A.  any section of pipe reading higher than 35 microns shall be replaced or repaired.  If field repaired, a written statement describing repair required will be submitted.  In addition, any pipe re-evacuated in the field will be monitored and recorded every other day for five working days.  If vacuum degrades to the disapproval of the SDR, the section will be replaced.  Upon verification of acceptable vacuum for all sections of V.I.P. system, each section will be numbered and the vacuum level records.  An additional vacuum check will be performed after installation, prior to filling with LN2.  This recording will be submitted, along with the received levels, for comparison and evaluation by the Contracting Officer.  Any installed sections 35 microns or greater will be subject to rejection.  A final vacuum reading will be taken when LN2   has activated the molecular sieve.  This reading of 10 microns or less shall be on the submittal report.

Handling of Pipe and Accessories:  Handling shall be done in accordance with manufacturer’s recommendation..

Pipe Size Reduction:  Reduction in pipe size shall be made with V.I.P. reducing tees and/or V.I.P. reducing sections.

Installation of Valves:  Valves shall be installed at location shown on the Contract Drawings of the type specified. All valves shall be installed with their stems vertical.

Pipe Hangers:  Unless otherwise noted on the drawings, horizontal overhead runs of pipe shall be hung with adjustable wrought-iron, the malleable-iron hanger, spaced not over 8’ apart.  Use J-hangers, U-bolts, split clamps,. Or roller type support.  Chain strap, perforated bar, or wire hangers will not be permitted.  Trapeze hangers may be used in lieu of separate hangers on pipes running parallel to each other and close together.  All hangers shall have short turnbuckles or other approved means of adjustment, and should be suspended form structural members.  Hangers and collars shall be a size proportional to the weight of the pipe supported.  Where the piping is attached to metal partitions, full-length through bolts should be used with large washers on both sides.  Copper pipe hangers shall be copper or copper plated.  Piping in tunnels or chases shall be supported on Unistrut using pipe clamps, or approved substitute.

H.	Joints:  All  V.I.P. shall be connected with couplings and bayonet connectors, as per V.I.P. manufacturer’s type and specification.

3.03	TESTS

A.	General:   All vacuum insulated piping, components, equipment and accessories installed under this Contract shall be inspected and tested by other than the Contractor and the V.I.P. manufacturer’s representative, through the entire duration of testing, in the presence of the SDR, and approved before acceptance.  All labor, material, and equipment required for testing shall be furnished by the Contractor.  The Contractor shall be responsible for all repairs and retesting as required.  All instruments and other equipment whose safe pressure range is below that of the test pressure shall be removed from the line or blanked off before applying the tests.  Prior to performing tests, all lines shall be “blown” free of all loose dirt and foreign particles.  The Lines shall then be thoroughly blown with dry nitrogen at a sufficient flow rate and period of time to ensure complete cleaning on the line of all dirt, scale, and foreign matter.  Cleaning of the lines shall be subject to approval.

B.	Testing:  The entire LN2  pipe systems shall be pressurized with dry nitrogen gas (furnished by Contractor) to and not exceed 1.25 times V.I.P. pressure rating.  The test duration shall be maintained at 100 psig minimum over a four-hour period.  If pressure drop occurs during the four-hour period, the entire system shall be leak-bubble tested with the Winston Products Co., Inc.  “Sherlock 5 second leak detector” o.a.e., until leak is located and repaired.  Repeat test procedures until pressure hold test successful.  A cool down test follows with the introduction of (cryogenic) liquid nitrogen into the LN2 pipe system from the LN2  pressure vessel supply tank, allowing gaseous nitrogen to flow until liquid nitrogen begins to issue from the valve.  Close valve and then repeat procedure at all use points unit entire system is cooled down to operating temperature.  The next step is to carefully and thoroughly visually inspect the entire V.I.P. section and shall be corrected or replaced as determined necessary.  All above testing procedures shall be accomplished to the satisfaction of the SDR.  The Contractor shall be responsible for all costs of testing,

correcting and/or replacing materials that may be defective. The Contractor shall also be responsible for system problems due to poor workmanship.

END OF SECTION