SPILL PREVENTION, CONTROL, AND COUNTERMEASURE PLAN

NATIONAL WEATHER SERVICE

Remote Data Acquisition Site

Washington County, Oregon

Original Date of Plan	:	March 31, 2000

Date of Last Plan Review:	:	March 31, 2000

Date of Last Amendment

and P.E. Certification:	:	March 31, 2000

Designated Person Responsible for Spill Prevention:

Brian Alley, Environmental/Safety Focal Point

Telephone: (503) 326-2340, Ext. 263 or Ext. 0

CERTIFICATION

I hereby certify that I have examined the facility, and being familiar with the provisions of Title 40 of the Code of Federal Regulations (CFR) Part 112, I attest that this SPCC plan has been prepared in accordance with good engineering practices.

Jerald I. Shuster

Printed Name of Registered Engineer

Signature of Registered Engineer and Date

Registration No. 18031PE              State OR

REVIEW DOCUMENTATION AND MANAGEMENT APPROVAL PAGE

REVIEW DOCUMENTATION

In accordance with Title 40 CFR Part 112.5(b), a review and evaluation of this SPCC Plan is conducted at least once every 3 years.  As a result of this review and evaluation, the National Weather Service will amend the SPCC Plan within 6 months of the review to include more effective prevention and control technology if:

- Such technology will significantly reduce the likelihood of a spill event from the facility, and

- If such technology has been field-proven at the time of review.

Any amendment to the SPCC Plan shall be certified by a Professional Engineer within 6 months after a change in the facility design, construction, operation, or maintenance occurs which materially affects the facility’s potential for the discharge of oil into or upon the navigable waters of the United States or adjoining shorelines.

| Review Date | Signature of Responsible Manager | Amended (Yes or No)? 1 |
| --- | --- | --- |

1	Amendment necessary and certified by a Registered Professional Engineer per Title 40 CFR Part 112.3(d)

MANAGEMENT APPROVAL

The National Weather Service is committed to the prevention of discharges of oil to navigable waters and the environment.  We maintain the highest standards for spill prevention, control, and countermeasures (SPCC) through regular review, updating, and implementation of this SPCC plan for the Remote Data Acquisition Site located in Washington County, Oregon.

Steve Todd, Meteorologist-In-Charge

Printed Name and Title of Responsible Manager

Signature and Date

CONTENTS

Section	Page

Certification	i

Review Documentation and Management Approval	ii

PART I -	GENERAL INFORMATION	1

A.	GENERAL	1

1.	Name	1

2.	Type	1

3.	Date of Initial Operation	1

4.	Location	1

5.	Name and Address of Operator	1

6.	Facility Contacts:	1

B.	SITE DESCRIPTION AND OPERATIONS	1

1.	Facility Location, Layout, and Operations	1

2.	Facility Storage	2

3.	Drainage Pathway and Distance to Navigable Waters	2

4.	Spill History	2

5.	Spill Potential, Volumes, and Rates	2

PART II -	DESIGN COMPONENTS AND OPERATIONAL PROCEDURES FOR SPILL PREVENTION AND CONTROL	3

A.	SPILL PREVENTION	3

1.	Bulk Storage Tanks and Facility Transfer Operations	3

2.	Tank Truck Unloading Operations	3

3.	Inspections And Records	4

4.	Site Security	4

5.	Training	5

B.	SPILL CONTROL	5

1.	Secondary Containment Designs, Construction Material, and Volume	5

2.	Spill Kits Type And Location	5

PART III -	SPILL COUNTERMEASURES AND REPORTING	6

A.	SPILL COUNTERMEASURES	6

B.	SPILL REPORTING	6

1.	General Notification Procedures For All Spills	6

2.	Federal Notifications	7

4.	State Notification	8

5.	Cleanup Contractor Notification	8

PART IV –	RECOMMENDED IMPROVEMENTS	9

A.	PHYSICAL UPGRADES	9

1.	Tanks	9

2.	Security	9

3.	Spill Kits	9

CONTENTS (Continued)

Section	Page

B.	PROCEDURAL CHANGES	9

1.	Tank Truck Unloading Procedure	9

2.	Inspections and Preventative Maintenance	10

3.	Training	10

Appendix

A	Tank Ullage/Fueling Log ANd FUeL UNLOADING PROCEDURE CHECKLIST

B	Inspection ChecklistS

C	Training Outline and Title 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.1-112.20-OIL POLLUTION PREVENTION

D	Spill RepoRtING form

E	CROSS REFERENCE OF THE REQUIREMENTS of TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.7, WITH THIS PLAN

FIGURES

Figure	Page

1	SITE LOCATION	11

2	SITE LAYOUT	12

TABLES

Table	Page

1	DESCRIPTIVE INVENTORY OF FACILITY STORAGE	13

2	POTENTIAL SPILL SOURCES AND VOLUMES	14

PART I - GENERAL INFORMATION

  - GENERAL

This section provides general information about the facility.

    - Name

National Weather Service (NWS)

Remote Data Acquisition (RDA) Site

    - Type

This facility is an onshore facility (non-production) that houses a RADAR dome for collecting atmospheric information.  The facility is automated and is visited by NWS staff at least once per week.

    - Date of Initial Operation

March 1995

    - Location

Washington County, Oregon

Latitude:  	45o 42’ 55” North

Longitude:	122o 57’ 49” West

    - Name and Address of Operator

National Weather Service

Western Region

125 S. State Street, Room 1311

Salt Lake City, Utah 84138-1102

    - Facility Contacts:

Name		Title					Telephone Number

Brian Alley	Environmental/Safety Focal Point	(503) 326-2340, Ext. 263

Steve Todd	Meteorologist-In-Charge		(503) 326-2340, Ext. 0

(24 hours a day)

  - SITE DESCRIPTION AND OPERATIONS

    - Facility Location, Layout, and Operations

The facility is located in the Tualatin Mountains of Washington County, Oregon, approximately 20 miles northwest of the Portland International Airport (Figure 1).  The nearest town is Scappoose, Oregon, approximately 4 miles northeast of the site.  Figure 2 shows the layout of the facility, including location of the 1,000-gallon aboveground storage tank (AST) connected to two 250-gallon generator day tanks.  The fuel in the tanks is used to power an 80-kilowatt emergency backup power (electric) generator.  The surrounding area is undeveloped and wooded.

The estimated fuel usage is approximately 600 gallons per year.  This estimate is based on an automatic test of the generator once per week for 45 minutes.  Fuel consumption would increase based on the frequency and duration of any power outages.

    - Facility Storage

The main storage tank is a 1,000-gallon, ConVault AST, rectangular in shape.  The primary steel tank is steel wrapped in styrofoam insulation and an impervious barrier of 30-mil high-density polyethylene (HDPE) membrane.  This composite is then encased in a 6-inch thick concrete vault.  The tank has a primary and an emergency vent.

A supply line from the storage tank is encased in a polyvinyl chloride pipe that exits the ConVaultfrom its top and runs overhead into the generator building.  The fuel is transported to the west day tank by a pump in the generator building.

The two, 250-gallon single-walled day tanks are rectangular in shape and located inside the generator building.  They are connected to each other in two places via a 2-inch rubber line.  Each tank has a vent pipe out the top that merges together into one pipe that is vented out the side of the generator building.  The west tank is connected to the pump that brings fuel from the storage tank and has a fuel supply and return lines connect to the generator.  The west tank also has a low-level sensor that is remotely monitored at the Portland Weather Forecast Office and River Forecast Center (WFO/WFC) located approximately 25 miles away.

Table 1 summarizes the pertinent information on the tanks at the facility.

    - Drainage Pathway and Distance to Navigable Waters

Any spilled fuel oil from the facility, regardless of initial direction, would travel south down the relatively steep gravel access road toward Dixie Mountain Road.  There are no storm drain inlets along the access road or Dixie Road, only open ditches.  The site is located in the headwaters of McKay Creek, a tributary to Dairy Creek that flows into the Tualatin River, a tributary of the Willamette River.

    - Spill History

Reportable Spill events from March 1995 to present (date on cover of this plan):

None.

    - Spill Potential, Volumes, and Rates

The most probable causes for spills from the storage tank are from overfilling or a ruptured hose during fueling.  For this tank, spills caused by failure of the fuel supply line, loss of structural integrity, vehicle collisions, or earthquakes are low probability events.  For the day tanks, the probable causes of spills are from a failure of the pump to shut down or failure of the line from the pump to the day tank.

Table 2 summarizes the potential type of failure, potential spill volume, estimated rate, and direction of spill flow from the tanks.

PART II - DESIGN COMPONENTS AND OPERATIONAL PROCEDURES
FOR SPILL PREVENTION AND CONTROL

This section discusses spill prevention and control measures that shall be implemented at the facility.

- SPILL PREVENTION

This section describes design components and operating procedures that shall be implemented at the facility to prevent oil spills.

- Bulk Storage Tanks and Facility Transfer Operations

Storage Tank:  The tank construction shall be compatible with the number 2 diesel fuel held by the tank.  The tank shall have secondary containment around the primary tank shell.  A float-type level gauge shall indicate the fuel level (from empty to full).

An automatic shut-off valve on the fill spout shall be set to close at 90 percent of the tanks capacity (900-gallons).  The tank also shall have an audible high-level alarm set at 85 percent of capacity (850-gallons) and interstitial monitoring device between the primary and secondary tanks that is connected to the audible alarm system.  A 10-gallon-capacity round spill container shall surround the fill spout.

Day Tanks:  The tank construction shall be compatible with the number 2 diesel fuel held by the tank. The generator building is 9 ½ feet wide and 15 ½ feet long and has a 9-inch-high lip on the door.  Excluding displacement from the equipment, there is approximately 825 gallons of capacity within the sealed concrete floor of the building for secondary containment.

Piping:  An antisiphoning valve shall be located between the main storage tank and the pump to prevent unwanted fuel from being siphoned from the storage tank.  The overhead piping shall be contained within another pipe and protected from damage.

    - Tank Truck Unloading Operations

All delivery drivers shall have U.S. Department of Transportation hazardous material transportation training as required by Federal law.

The remainder of this section discusses the procedures that shall be used during unloading of fuel from the tank truck into the storage tank to prevent spills.  This procedure shall be documented every time refueling occurs using the form found in Appendix A.  Copies of this form shall be kept for 3 years.

The following procedure shall be used prior to fuel unloading:

- Ensure that the audible high-level alarm system and the automatic shutoff valve are function properly.

- A NWS representative should determine the available capacity (ullage) of the tank by converting the reading on the fuel gauge to gallons (See Appendix A). This ullage is communicated to the fuel supply contractor and marked in the fueling log.

- Move spill containment equipment such as booms or spill barriers into the unloading area.

- Block the tank truck wheels.

- Place drip pans under all pump hose fittings (if applicable) prior to unloading.

- The NWS representative and the delivery driver ensure the fill nozzle is place in the appropriate tank appurtenance.  In this case, the fill nozzle is placed in the fill pipe connected to the 10-gallon-capacity round spill container.

Both the NWS representative and the delivery driver shall remain with the vehicle at all times during unloading.  Gauges on the tank and the truck shall be continuously monitored to ensure the ullage is not exceeded.  If the audible high-level alarm sounds, the unloading of fuel shall be stopped as soon as possible.

After fuel unloading is completed:

- Record the amount of fuel transferred to the tank in the log (Appendix A).

- Drain the fill hose and then ensure that all drain valves are closed (if applicable) prior to removal of the hose from the tank

- Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the tank (if it has the capacity) or disposed of appropriately.

- Inspect the tank truck prior to removing the blocks to ensure the lines have been disconnected from the tank.

- Remove the blocks from truck wheels

- Place a copy of the fuel unloading checklist in the SPCC plan.

    - Inspections And Records

Inspection and Maintenance of Tanks:  The storage tank and generator day tank shall be inspected weekly for any oil outside the tank, especially at seams (including the underside).  The outside of exposed piping shall also be inspected weekly, especially at the joints such as gasketed fittings.  Monthly and annual inspections shall follow the checklists shown in Appendix B.

Record Keeping:  The Environmental/Safety Focal Point shall be responsible for completing the ullage logs and documentation of fuel unloading procedures.  These records, as well as records of all inspections, shall be maintained for at least 3 years from the time of inspection.

    - Site Security

The tank shall have adequate lighting to detect spills at night and a security fence with a locked gate to prevent tank damage or spills caused by vandalism.  The generator building shall be kept locked and be the status of the door lock shall be remotely monitored from the Portland WFO/RFC.  Signage around the tank shall warn of the presence of a combustible liquid, that the combustible liquid is diesel fuel number 2, and that smoking is not permitted near the tank.  A fire extinguisher shall be located in the adjacent generator building.  The tank is not located in the direct line of parking lot traffic; therefore no guard posts are required.

    - Training

The Environmental/Safety Focal Point (person responsible for spill prevention at the facility) and an alternate shall be trained in the intent of applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in paragraph 3, above.  Spill control and countermeasure shall also be included in the training.  An outline for the training is found in Appendix C.

Training shall be repeated once per year.  All new personnel responsible for implementing this SPCC plan shall be properly trained before beginning the new position.  A record of who was trained, when, and by whom, shall be filed with this SPCC plan and kept for a period of 3 years.

- SPILL CONTROL

This section describes control measures that shall be implemented to prevent any spilled oil from entering navigable waters or adjoining shorelines.

- Secondary Containment Designs, Construction Material, and Volume

The secondary containment tank on the storage tank and the sealed floor in the generator building beneath the day tanks shall be sized to contain 110 percent of the tank volumes.  Both of these secondary containment features shall be enclosed to prevent precipitation from entering.  An interstitial monitoring system that can detect fuel of 1 inch or more in the secondary shell of the storage tank shall be included.

    - Spill Kits Type And Location

The facility shall have spill kits designed absorb diesel fuel and to divert a spill from navigable waters. These items shall be stored in the generator building or nearby.  The kit shall include oil absorbent socks and mats in a polyethylene container that doubles as a disposal container.  In addition, urethane spill barriers that can divert or contain a relatively small spill and prevent it from reaching navigable waters should be included with the spill kit.

PART III - SPILL COUNTERMEASURES AND REPORTING

The primary emphasis of this SPCC plan is on prevention.  The spill countermeasures presented do not constitute a contingency plan detailed in Title 40 CFR Part 109, nor is one required.  Such a plan is only required under Title 40 CFR 112.7(d) if it is impracticable to provide containment, diversionary structures, or equipment to prevent the discharge of oil to navigable waters.  In addition, this facility is not required to have a facility response plan under Title 40 CFR Part 112.20 since it does not:

- Transfer oil over water from vessels and have a total oil storage capacity of greater than or equal to 42,000 gallons, or

- Have a total storage capacity over 1 million gallons.

Should a spill occur the following measures would be implemented:

- SPILL COUNTERMEASURES

This section presents countermeasures to contain, cleanup, and mitigate the effects of an oil spill that impacts navigable waters or adjacent shorelines.

A spill containment and cleanup activity will never take precedence over the safety of personnel.  No countermeasure activities will be undertaken until conditions are safe for workers.  The following general procedures should be implemented as countermeasures:

- Account for all personnel and ensure their safety.

- Eliminate all ignition sources in the immediate area.

- Attempt to divert flow away from drainage ditches with a spill barrier or the contents of spill kit.

- Attempt to seal or somehow stop leak, if it can be done safely.

- Notify contacts and emergency response contractor as described in the next section for assistance in control and cleanup.

- SPILL REPORTING

This section discusses the reporting procedures for spills of diesel fuel at the facility.  The people and organizations that are notified vary based on the quantity of the spill, whether it reaches navigable waters or adjoining shorelines, and the frequency of spills.

A spill report form that requests the information to be reported to all agencies in written form (to the extent known) is included in Appendix D.  Copies of the completed form should be sent to the NWS Environmental Compliance Officer and the NOAA Western Regional Compliance Officer (see next section).

- General Notification Procedures For All Spills

The responsible person or designee is directly charged with reporting all oil spills that result from facility operations as follows:

- First, call 9-1-1 (or the local emergency agency) if there is an immediate emergency

- Next, notify the appropriate persons within the NWS:

- Mike Jacob, (301) 713-1838 Ext. 165, NWS Environmental Compliance Officer.

- Olga Kebis, (301) 713-1838 Ext. 173, NWS Safety Officer

- Bob Kinsinger, (801) 524-5138 Ext. 223, NWS Western Regional Environmental/Safety Coordinator

- Thanh Minh Trinh, (206) 526-6647, NOAA Western Regional Compliance Officer

  - Federal Notifications

The Federal Clean Water Act as described in Title 40 CFR Part 110.6, requires notifying the U.S. Environmental Protection Agency’s (EPA) National Response Center (or the U.S. Coast Guard [USCG]) as soon as anyone has knowledge of any discharges of oil in quantities that “may be harmful.”  Title 40 CFR Part 110.3 defines “may be harmful” as a discharge that:

  - Violates applicable water quality standards; or

  - Causes a film or sheen upon or discoloration of the surface of the water or adjoining shorelines or cause a sludge or emulsion to be deposited beneath the surface of the water or upon adjoining shorelines

If either of these criteria are met contact:

- The National Response Center (EPA and USCG):
(800) 424-8802.

Under the SPCC regulations, spill information listed in Title 40 CFR Part 112.4(a) must be reported to the regional EPA office within 60 days if either of the following occurs:

- A discharge of more than 1,000 gallons of oil into or upon navigable waters or adjoining shore lines in a single event

- Two spill events that cause visible sheens upon navigable waters or adjoining shore lines within any 12-month period

Diesel fuel is not listed as a hazardous substance under the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA).  Therefore no other notification to the EPA is required for discharges of diesel fuel other than those listed above.

- State Notification

To satisfy the state reporting requirements, the location and quantity of the spill must be determined.  Under the Oregon Administrative Rules Chapter 340, Division 108, Section 0110, a reportable quantity (RQ) is defined as follows:

- If spilled on the surface of the land, any quantity of oil over one barrel (42 gallons).

- If spilled into the waters of the state, any quantity that would produce a visible oil slick, oil solids, or coat aquatic life, habitat, or property with oil.

If one or both of these criteria are met, contact the Oregon Emergency Management Division:

- (800) 452-0311 (from within Oregon)

- (503) 378-4124 (outside of Oregon)

- Cleanup Contractor Notification

An emergency response contractor should also be notified to assist with the clean up, if necessary.  NWS has identified the following three contractors that are available for an emergency response:

- Stayton Environmental		(503) 236-5845

- First Strike Environmental		(503) 620-7773 or (800) 447-3558

- Foss Environmental			(800) 337 -7455

PART IV – RECOMMENDED IMPROVEMENTS

In accordance with Title 40 CFR Section 112.7, this section presents physical upgrades or procedural changes that are not yet fully operational but are called for in the plan.

- PHYSICAL UPGRADES

- Tanks

An automatic overfill shutoff valve shall be installed in the fill spout.  This valve shall be set to stop the flow of fuel into the tank when it reaches 90 percent of capacity.  The fuel supply contractor should be notified to ensure the valve is compatible with the nozzle used to fill the tank.  A high level audible alarm shall also be installed on the storage tank to sound at 85 percent capacity.  EPA Region 10 requires both an audible high level alarm set at 85 percent capacity and an automatic shutoff device set at 90 percent capacity for all double-walled tanks that are not in a diked or bermed enclosure to comply with the requirements of Title 40 CFR Section 112.7(c).

The interstitial monitoring device shall be connected such that an alarm is noticeable at the facility.  In addition, an antisiphoning valve shall be installed in the line between the storage tank and the pump.  This valve is designed to prevent unwanted fuel from being siphoned from the storage tank when the pump is turned off.

- Security

The lighting around the tank shall be upgraded.  A light shall be installed that can be turned on when NWS personnel are at the facility.  The purpose of this lighting is to illuminate the tank area such that any spills can be noticed in the dark.  This requirement is found in Title 40 CFR Section 112.7(e)(9).

Worker security and safety needs improvement around the storage tank.  The tank shall have a “NO SMOKING” sign and a “CAUTION – COMBUSTIBLE LIQUID” sign clearly posted.  The tank should have a sign that reads “DIESEL FUEL.”  These signs are required by the state Fire Marshall.

- Spill Kits

NWS shall purchase adequately sized spill kits and store them near the tanks.  The current kit in the generator building is for spills up to 4 gallons.  NWS shall purchase a kit capable of handling at least 40-gallons.  The kit should include oil absorbent socks and mats in a polyethylene container that doubles as a disposal container.  In addition, it is highly recommend that the facility have urethane spill barriers available.  These barriers can direct or contain a relatively small spill and prevent it from reaching navigable waters.  This requirement is found in Title 40 CFR Section 112.7(c)(1)(iv) and (vii).

- PROCEDURAL CHANGES

- Tank Truck Unloading Procedure

The current tank truck unloading area does not drain into a catchment basin or a treatment facility designed to handle spills.  However, since unloading of fuel occurs only approximately once per year on average, the following procedural improvement should be implemented.  Containment booms and spill barriers from the spill kit described in Part IV, Section A.3. of this plan shall be made easily accessible during tank truck unloading.   The containment booms and spill barriers combined with constant monitoring of the fuel unloading process by NWS personnel will meet the substantive requirements of Title 40 CFR Section 112.7(e)(4).

- Inspections and Preventative Maintenance

The inspection checklists found in Appendix B should be followed.  This requirement is found in Title 40 CFR Section 112.7(e)(8).  The interstitial monitoring device in the storage tank is designed to monitor the integrity of the primary tank.  Visual inspections of the outside of the secondary wall of the storage tank and the primary wall of the day tanks should serve to signal a potential problem with their integrity.  However, if a problem is suspected with any tank, tightness testing should be initiated soon after discovery.

- Training

The Environmental/Safety Focal Point (person responsible for spill prevention at the facility) and an alternate should be trained in the intent of the applicable oil spill regulations and how to implement the inspection and maintenance procedures outlined in the previous section.  Spill control and countermeasure should also be included in the training.  The alternate should be designated in case the primary person is off-site at the time of a spill.  A recommended outline for the training is found in Appendix C.

Training should be repeated once per year.  All new personnel responsible for implementing the SPCC plan should be properly trained before beginning the new position.  A record of who was trained, when, and by whom, should be filed with this SPCC plan and kept for a period of 3 years.  This requirement is found in Title 40 CFR 112.7(e)(10).

Figure 1 Site location

Figure 2 Site Layout

TABLE 1

DESCRIPTIVE INVENTORY OF FACILITY STORAGE

| Tank | Nominal Capacity (Gallons) | Product Stored | Type | Double Walled? |
| --- | --- | --- | --- | --- |
| Storage Tank | 1,000 | Diesel fuel number 2 | AST | Yes |
| Generator Day Tanks | 2 X 250 | Diesel fuel number 2 | AST | No1 |
| Total Capacity | 1,500 |  |  |  |

Notes:	AST	Aboveground storage tank

1	Located in generator building with sealed concrete floor that has a capacity of greater than 500 gallons

TABLE 2

POTENTIAL SPILL SOURCES AND VOLUMES

14

| Source | Event | Potential Spill Volume (gallons) | Estimated Rate (gallons per minute) | Direction of Spill Flow | Remarks |
| --- | --- | --- | --- | --- | --- |
| Storage tank | Overfilling or a ruptured hose during fueling. | >0 to 40a | 80b | South | None |
|  | Failure of fuel supply line to pump | >0 to 1,000 | Variable depending on size of hole | South | Can be minimized through routine inspections; Primary line also has secondary containment from the storage tank to generator building |
|  | Structural failure | >0 to 1,000 | Variable depending on size of hole | South | Low probability event that both primary and secondary tank shells would fail. |
|  | Vehicle collision | >0 to 1,000 | Variable depending on size of puncture | South | Low probability event. Vehicle traffic is limited and traffic flow is not directly towards tanks. |
|  | Overturn or puncture in an earthquake | >0 to 1,000 | Variable depending on size of hole | South | Low probability event. Double walled tank gives extra protection from rupture, but a large earthquake could cause a spill. |
| Two Day Tanks | Failure of pump to shut down after filling day tanks or failure of line from pump to day tank | >0 to 1,000 | Variable depending on size of hole | South | Can be minimized through routine inspections. |
|  | Failure of fuel return line | >0 | 10c | South | Can be minimized through routine inspections. |
|  | Overturn or puncture in an earthquake | >0 to 500 | Variable depending on size of hole | South | Low probability event. |
|  | Structural failure | >0 to 500 | Variable depending on size of hole | South | Low probability event. |

Notes:

a	Based on a maximum pumping rate of 80 gallons per minute from the fill truck and a maximum of 30 seconds to turn off the pump

March 31, 2000

Washington County, Oregon

b	Approximate maximum pumping rate of fill truck

March 31, 2000

c	Estimated return line flow rate

APPENDIX A

Tank Ullage/Fueling Log ANd

Fuel UNLOADING PROCEDURE CHECKLIST

(2 Pages)

APPENDIX A-1

Tank Ullage anD Fueling Log

A-1

Tank Capacity 	 gallons

Washington County, Oregon

| Date | Initials | Gauge Reading | Initial Volume of Fuel in Tank (Gallons) | Available Capacity or Ullage b (Gallons) | Quantity Added (Gallons) | Comments |
| --- | --- | --- | --- | --- | --- | --- |

Note:

a	From gauge reading

March 31, 2000

b	Available capacity (ullage)= tank capacity – initial volume of fuel in tank

APPENDIX A-2

FUEL UNLOADING PrOCEDURE CHECKLIST

Washington County, Oregon

Date:										Tank:

A-2

NWS Representative:								Supplier

March 31, 2000

|  | ITEM |  | DESCRIPTION | COMMENT |
| --- | --- | --- | --- | --- |
| The following six items must be completed before fuel unloading: |  |  |  |  |
|  | 1 |  | Ensure the audible high-level alarm system and automatic shutoff valve are functioning properly. |  |
|  | 2 |  | Determine the available capacity (ullage) of tank by converting the reading on the fuel gauge to gallons (See Appendix A, Page A-1). This ullage should then be marked in the fueling log and communicated to the tank truck unloading contractor. |  |
|  | 3 |  | Move spill containment equipment such as booms or spill barriers into the unloading area. |  |
|  | 4 |  | Block the wheels of the tank truck. |  |
|  | 5 |  | Place drip pans under all pump hose fittings (if applicable) after the hose is hooked up to the tank and before unloading. |  |
|  | 6 |  | Ensure the fill nozzle is placed in the appropriate tank appurtenance. In this case, the fill nozzle is placed in the fill pipe connected to the round spill container. |  |
| During unloading: |  |  |  |  |
|  |  | 7 | Ensure that the NWS representative and the tank truck operator remain with the vehicle at all times during unloading. |  |
|  |  | 8 | Monitor the gauges on the AST and the truck continuously to ensure the ullage is not exceeded. If the audible high-level alarm sounds, stop the unloading of fuel as soon as possible. |  |
| The following six items must be completed after the fuel unloading has been completed: |  |  |  |  |
|  |  | 9 | Record the amount of fuel unloaded in the log (Appendix A, page A-1). |  |
|  |  | 10 | Before removing the fill hose from the AST, ensure that it is drained and that all drain valves are closed (if applicable). |  |
|  |  | 11 | Pour any fuel in the drip pans, tank truck containment pool, or spill container on the fill pipe into the AST (if it has the capacity) or dispose of appropriately (describe how it was disposed of, if applicable). |  |
|  |  | 12 | Inspect the tank truck before removing the blocks to ensure the lines have been disconnected from the AST. |  |
|  |  | 13 | Remove the blocks from tank truck wheels. |  |
|  |  | 14 | Place a copy of this fuel-unloading checklist in the SPCC plan. |  |

APPENDIX B

INSPECTION CHECKLISTS

(3 Pages)

APPENDIX B

INSPECTIONS FORMS

March 31, 2000

B-1

March 31, 2000

Washington County, Oregon

| MONTHLY INSPECTION CHECKLIST (Page 1 of 2) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date of Inspection: | Tank Name or No.: |  |  |  |
| Date of Last Inspection: | Inspected by: |  |  |  |
|  | Signature: |  |  |  |
| A. TANKS |  | YES | NO | NOTES |
| 1. Are there any oil stains on the outside of the tank, including the underside? |  |  |  |  |
| 2. Is there any oil on the ground, concrete, or asphalt around the tank? |  |  |  |  |
| 3. Are there any visible cracks or indications of corrosion on the tank, at fittings, joints, or seals? (such as paint peeling or rust spots) |  |  |  |  |
| 4. Are there any raised spots, dents, or cracks on the tank? |  |  |  |  |
| 5. Does it appear that the foundation has shifted or settled? |  |  |  |  |
| 6. Is the fuel gauge working properly? |  |  |  |  |
| 7. Are all vents clear so they may properly operate? |  |  |  |  |
| 8. If rainwater is present in secondary containment area, does sufficient volume remain for spill control? (if applicable) |  |  |  |  |
| MONTHLY INSPECTION CHECKLIST (Page 2 of 2) |  |  |  |  |
| Date of Inspection: | Tank Name or No.: |  |  |  |
| Date of Last Inspection: | Inspected by: |  |  |  |
|  | Signature: |  |  |  |
| B. PIPING |  | YES | NO | NOTES |
| 1. Is there any oil on the outside of or under any aboveground piping, hoses, fittings, or valves? |  |  |  |  |
| 2. Are aboveground piping, hoses, fittings, or valves in good working condition? |  |  |  |  |
| C. SECURITY/SAFETY/SPILL COUNTERMEASURES |  |  |  |  |
| 1. Are lights working properly to detect a spill at night? |  |  |  |  |
| 2. Are all locks in the “lock” position? |  |  |  |  |
| 3. Are all warning signs properly posted and readable? |  |  |  |  |
| 4. Are vehicle guard posts in place and properly secured? (If applicable) |  |  |  |  |
| 5. Are spill kits easily accessible, protected from the weather, and complete? |  |  |  |  |
| Corrective Actions Required: |  |  |  |  |

Washington County, Oregon

B-2

March 31, 2000

| ANNUAL INSPECTION CHECKLIST (Page 1 of 1) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Date of Inspection: | Tank Name or No.: |  |  |  |
| Date of Last Inspection: | Inspected by: |  |  |  |
|  | Signature: |  |  |  |
| A. MONTHLY CHECKLIST |  | YES | NO | NOTES |
| 1. Has monthly inspection checklist been completed? |  |  |  |  |
| B. TANKS |  |  |  |  |
| 1. Are all alarms and automatic shutoff devices working properly? |  |  |  |  |
| 2. Is interstitial monitor functioning properly (if applicable) |  |  |  |  |
| C. OTHER |  |  |  |  |
| 1. |  |  |  |  |
| Corrective Actions Required: |  |  |  |  |

APPENDIX C

B-3

March 31, 2000

Washington County, Oregon

TRAINING OUTLINE AND COPY OF TITLE 40 OF THE CODE OF FEDERAL REGULATIONS Section 112.1-112.20-Oil Pollution Prevention

(11 Pages)

APPENDIX C

OUTLINE FOR SPILL PREVENTION, CONTROL,

AND COUNTERMEASURE TRAINING

Training will be provided for facility personnel at the following times:

- System startup or whenever new equipment is installed

- Within the first week of employment for new personnel

- Annually

The training will include complete instruction in the elements of the facility’s Spill Prevention, Control, and Countermeasure plan and will include the following:

- Pollution control laws, rules, and regulations including a summary of Title 40 of the Code of Federal Regulations Part 112 "Oil Pollution Prevention" (see Attachment).

B.	Fuel Storage System

1.	Purpose and application of the following system elements:

a.	Tanks

b.	Piping

c.	Pumps

d.	Accessory equipment

- Electronic monitors

- Operation, maintenance, and inspection of system elements

C.	Spill Prevention

- Potential spill sources

- Spill flow direction and impact on navigable waters

- Procedures to prevent spills, especially during fuel unloading

D.	Spill Control

- Secondary containment

- Safety valves

- Pump and equipment shutoff switches

- Use of catch basin inlet covers or other diversionary devices

E.	Spill Countermeasures

- Location and use of emergency phone numbers

- Location and use of fire extinguishers

- Location and use of spill cleanup kit

- Stopping the leak

APPENDIX D

SPILL REPORTING FORM

(1 Page)

APPENDIX D

SPILL REPORTING FORM

| 1. GENERAL |  |  |
| --- | --- | --- |
| Name of Facility: Remote Data Acquisition Site | Address: Washington County, Oregon |  |
| Completed By: | Organization: National Weather Service |  |
| Position: | Phone: |  |
| 2. SPILL INFORMATION |  |  |
| Date: | Time: |  |
| Location at Facility: | Quantity: |  |
| Substance Spilled: Diesel Fuel | Other: |  |
| 3. OUTSIDE NOTIFICATIONS: |  |  |
| Agencies | Recorder at Outside Agency | Date and Time |
| Call 9-1-1 (or the local emergency agency), if there is an immediate emergency |  |  |
| NWS/NOAA: Mike Jacob, (301) 713-1838 Ext. 165 Olga Kebis, (301) 713-1838 Ext. 173 Bob Kinsinger, (801) 524-5138 Ext. 223 Thanh Minh Trinh, (206) 526-6647 |  |  |
| EPA National Response Center or U.S. Coast Guard : (800) 424-8802 |  |  |
| Oregon Emergency Management Division (800) 452-0311 (from within Oregon) or (503) 378-4124 (outside of Oregon) |  |  |
| 5. INFORMATION ON SOURCE AND CAUSE |  |  |
| 6. DESCRIPTION OF ENVIRONMENTAL DAMAGE |  |  |
| 7. CLEANUP ACTION(S) TAKEN |  |  |
| 8. CORRECTIVE ACTION(S) TO PREVENT FUTURE SPILLS |  |  |

Note:	All information must be filled in.  If something is unknown, write “unknown.”

Copies must be sent to the NWS/NOAA personnel listed previously.

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS of TITLE 40 OF THE CODE OF FEDERAL REGULATIONS, Section 112.7, WITH THIS DOCUMENT

(1 Page)

APPENDIX E

CROSS REFERENCE OF THE REQUIREMENTS OF 40 CFR 112.7 AND THIS PLAN

| CFR Citation | Item | Plan Location |
| --- | --- | --- |
| 112.7 (a) | Spill History | Part I.B.4 |
| 112.7 (b) | Potential Spill Prediction, Volumes, and Rates | Part I.B.5 and Table 2 |
| 112.7 (c) | Containment and Diversionary Structures | Part I.B.2 and Part II.B.2 |
| 112.7 (d) | Secondary Containment Impractability | Not Applicable |
| 112.7 (e)(1) | Drainage Control | Part I.B.3 |
| 112.7 (e)(2) | Bulk Storage Tanks and Secondary Containment. |  |
| 112.7 (e)(2)(i) | Tank compatibility with its contents | Part II.A.1 |
| 112.7 (e)(2)(ii) | Diked area construction and containment for storage tanks | Not Applicable |
| 112.7 (e)(2)(iii) | Diked area inspection and drainage of rainwater | Not Applicable |
| 112.7 (e)(2)(iv) | Corrosion protection of buried metallic storage tanks | Not Applicable |
| 112.7 (e)(2)(v) | Corrosion protection of partially buried metallic tanks | Not Applicable |
| 112.7 (e)(2)(vi) | Aboveground tank periodic integrity testing | Part II.A.3 |
| 112.7 (e)(2)(vii) | Control of leakage through internal heating coils | Not Applicable |
| 112.7 (e)(2)(viii) | Tank installation fail-safe engineered | Part II.A.1, B.1 |
| 112.7 (e)(2)(ix) | Observation of disposal facilities for effluent discharge | Not Applicable |
| 112.7 (e)(2)(x) | Visible oil leak corrections from tank seams and gaskets | Part II.A.3 and Appendix A Inspections |
| 112.7 (e)(2)(xi) | Appropriate position of mobile or portable tanks | Not Applicable |
| 112.7 (e)(3) | Facility Transfer Operations |  |
| 112.7 (e)(3)(i) | Buried piping installation protection and examination | Part II.A.1 & Appendix A |
| 112.7 (e)(3)(ii) | Not in-service and standby terminal connections | Not Applicable |
| 112.7 (e)(3)(iii) | Pipe support designs | Not Applicable |
| 112.7 (e)(3)(iv) | Aboveground valve and pipeline examination | Not Applicable |
| 112.7 (e)(3)(v) | Aboveground piping protection from vehicular traffic | Not Applicable |
| 112.7 (e)(4) | Facility Truck Unloading Operations | Part II.A.2 |
| 112.7 (e)(5)-(7) | Oil Production Facilities (onshore) and Oil Drilling, Production, or Workover Facilities (on shore and offshore) | Not Applicable |
| 112.7 (e)(8) | Inspections And Record Keeping | Part II.A.3 |
| 112.7 (e)(9) | Security |  |
| 112.7 (e)(9)(i) | Fencing | Part II.A.4 |
| 112.7 (e)(9)(ii) | Flow valves locked | Not Applicable |
| 112.7 (e)(9)(iii) | Starter controls locked | Not Applicable |
| 112.7 (e)(9)(iv) | Pipeline loading and unloading connections securely capped | Not Applicable |
| 112.7 (e)(9)(v) | Lighting adequate to detect spills | Part II.A.4 |
| 112.7 (e)(10) | Training |  |
| 112.7 (e)(10)(i) | Personnel instructions | Part II.A.5 |
| 112.7 (e)(10)(ii) | Designated person responsible for spill prevention | Page i |
| 112.7 (e)(10)(iii) | Spill prevention briefings | Part II.A.5 |