## TITLE
VJ ASSOCIATES
136 WEST JOHN STREET
HICKSVILLE, NEW YORK - 11801
TEL: (516) 932-1010
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
REVISED
2007-09-20

## QUALIFICATION
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
QUALIFICATIONS
1 | The following estimates were prepared.
A | Ring Building
B | Service Buildings One to Five - two floors each.
C | RF Service Building - two floors
D | Operations Center - two floors
E | Booster Ring and Linac - one floor
F | Lab / Office Buildings One, Four, five - one floor and attic space
G | Site Preparation, Utilities and Improvements
2 | Gross enclosed areas for project as supplied by architect are as follows:
A | Ring Building | 248600 | SF
B | Service Buildings One to Five | 56280 | SF
C | RF Service Building | 9200 | SF
D | Operations Center | 14530 | SF
E | Booster Ring and Linac | 22700 | SF
F | Lab / Office Buildings One to Three | 68400 | SF
-
| Total Gross Enclosed Area | 419710 | SF
3 | Prefabricated Helium Compressor Building | 1900 | SF
4 | Lab / Office Buildings Four and Five are optional and not included in base estimate.
5 | Gross enclosed area for Lab / Office Buildings Four and Five is 45,600 square feet.
6 | Loading dock is included with Ring Building.
7 | Operations Center third floor is not included in base estimate. See alternate cost.
8 | Prefabricated Helium Compressor Building is included with RF Service Building estimate.
9 | The following mark ups are included within each estimate summary.
A | 15% General Contractor's General Conditions, Overhead & Profit
10 | The following mark ups are included on main estimate summary. Not included in individual
building summary sheets.
A | 10% Design Contingency
B | 20% Escalation
11 | The following items are excluded from estimate.
A | A-E fees
B | Overtime
C | Equipment at Ring Building, Booster Ring Building, Linac and Krystron Gallery.
D | Existing buildings on site to demolished to floor slabs under separate contract. See C-102.
12 | Include elevated platform at Ring Building at one location as shown on drawing
A-101A-OPT. Include footings for two future elevated platforms.
13 | Include separate Value Engineering Studies estimates and summary.
14 | VJ Associates 90% Title I estimate is based on the HDR Architecture Inc. 90% Title 1
set dated 09/7/07 and 90% Title I Design Technical Specifications dated Sept 7, 2007.

## WBSSUM)
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
PROJECT COST SUMMARY
TOTAL
WBS |  |  | DESCRIPTION |  | AMOUNT
1.05.03 | .02 |  | IMPROVEMENTS TO LAND |  | 6628518.9815
1.05.03 | .02 | .01 | SITE PREPARATION |  | 3392532.5
1.05.03 | .02 | .02 | SITE RESTORATION AND LANDSCAPING |  | 3235986.4815
1.05.03 | .03 |  | BOOSTER / LINAC, OPERATIONS CENTER, RF SERVICE BUILDING, SERVICE AREA ADJACENT TO SERVICE BUILDING - 1 |  | 14566624.5661
1.05.03 | .04 |  | RING BUILDING |  | 83545079.174 | 83545079.174
1.05.03 | .04 | 01 | PENTANT 1 - INCLUDE SERVICE BUILDING 1 |  | 16709015.8348
1.05.03 | .04 | 02 | PENTANT 2 - INCLUDE SERVICE BUILDING 2 |  | 16709015.8348
1.05.03 | .04 | 03 | PENTANT 3 - INCLUDE SERVICE BUILDING 3 |  | 16709015.8348
1.05.03 | .04 | 04 | PENTANT 4 - INCLUDE SERVICE BUILDING 4 |  | 16709015.8348
1.05.03 | .04 | 05 | PENTANT 5 - INCLUDE SERVICE BUILDING 5 |  | 16709015.8348
1.05.03 | .05 |  | LAB - OFFICE MODULES |  | 22608445.3336
1.05.03 | .05 | 01 | LOB - 1 |  | 7536148.4445
1.05.03 | .05 | 02 | LOB - 4 |  | 7536148.4445
1.05.03 | .05 | 03 | LOB - 5 |  | 7536148.4445
1.05.03 | .06 |  | MECHANICAL UTILITIES - INCLUDE CHILLED WATER |  | 10607030.8081
1.05.03 | .07 |  | ELECTRICAL UTILITIES |  | 11991501.8591
1.05.03 | .08 |  | LN2 & GN2 DISTRIBUTION SYSTEM |  | 1017750
1.05.03 | .09 |  | CHILLED WATER ( NOT FOR THIS PROJECT) |  | N I C
1.05.04 |  |  | INTEGRATED CONTROLS & COMMUNICATIONS |  | N I C
1.05.05 |  |  | STANDARD EQUIPMENT
1.05.05 | 01 |  | RING BUILDING STANDARD EQUIPMENT |  | N I C
1.05.05 | 02 |  | BLOC STANDARD EQUIPMENT |  | N I C
1.05.05 | 03 |  | LOB STANDARD EQUIPMENT |  | N I C
-
|  |  | SUB TOTAL |  | 150964950.7225
|  |  | DESIGN CONTINGENCY * | 10% | 15096495.0722
-
|  |  | SUB TOTAL |  | 166061445.7947
|  |  | ESCALATION* | 20% | 33212289.1589
-
|  |  | TOTAL PROJECT COST |  | 199273734.9537
LAB / OFFICE BUILDINGS THREE AND FOUR
|  |  | BUILDINGS |  | 15072296.8891
|  |  | PARKING LOTS |  | 430000
-
|  |  | SUB TOTAL |  | 15502296.8891
|  |  | DESIGN CONTINGENCY * | 10% | 1550229.6889
-
|  |  | SUB TOTAL |  | 17052526.578
|  |  | ESCALATION* | 20% | 3410505.3156
-
|  |  | LAB / OFFICE BUILDINGS THREE AND FOUR TOTAL COST |  | 20463031.8936
* NOTE: DESIGN CONTINGENCY AND ESCALATION SHOW ON MAIN SUMMARY ONLY

## SUMMARY
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
PROJECT COST SUMMARY
TOTAL
| DESCRIPTION |  | AMOUNT
1.6.3.4 | RING BUILDING |  | 60726462.8814
| SERVICE BUILDINGS ONE THROUGH FIVE |  | 22818616.2926
| RF SERVICE BUILDING |  | 2485277.8546
| OPERATIONS CENTER |  | 5183844.5553
| BOOSTER RING AND LINAC - SERVICE BLDG FOR SB-1 |  | 6897502.1561
1.6.3.5 | LAB / OFFICE BUILDINGS ONE, TWO & THREE |  | 22608445.3336
1.6.3.2 | SITE PREPARATION AND IMPROVEMENT |  | 6628518.9815
1.6.3.6 | MECHANICAL UTILITIES INCLUDING CHILLED WATER |  | 10607030.8081
1.6.3.7 | CHILLED WATER UTILITIES |  | With Above
1.6.3.8 | CRYOGENIC UTILITIES |  | Exclude
1.6.3.9 | ELECTRICAL UTILITIES |  | 11991501.8591
| LN2 & GN2 DISTRIBUTION SYSTEM |  | 1017750
-
| SUB TOTAL |  | 150964950.7225
| DESIGN CONTINGENCY * | 10% | 15096495.0722
-
| SUB TOTAL |  | 166061445.7947
| ESCALATION* | 20% | 33212289.1589
-
| TOTAL PROJECT COST |  | 199273734.9537
* NOTE: DESIGN CONTINGENCY AND ESCALATION SHOW ON MAIN SUMMARY ONLY
ALTERNATE COSTS
| LAB / OFFICE BUILDINGS FOUR AND FIVE |  | 15072296.8891
| PARKING LOTS |  | 430000
-
| SUB TOTAL |  | 15502296.8891
| DESIGN CONTINGENCY * | 10% | 1507229.6889
-
| SUB TOTAL |  | 17009526.578
| ESCALATION* | 20% | 3401905.3156
-
| TOTAL PROJECT COST |  | 20411431.8936

## TRADE - RING BUILDING
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
RING BUILDING
TOTAL
| DESCRIPTION |  | AMOUNT
2 | BUILDING EARTHWORK |  | 1368500
3 | CONCRETE |  | 17138898.7014
4 | MASONRY |  | 28560
5 | METALS |  | 7740587.5
6 | WOOD AND PLASTICS |  | 248600
7 | THERMAL AND MOISTURE PROTECTION |  | 4402535
8 | DOORS AND WINDOWS / CURTAINWALL |  | 2805800
| FINISHES |  | 745609.92
10 | SPECIALTIES |  | 1020000
11 | EQUIPMENT |  | 10000
12 | FURNISHINGS |  | Exclude
13 | SPECIAL CONSTRUCTION |  | Exclude
14 | CONVEYING SYSTEMS |  | 60000
15.1 | HVAC |  | 4858779
15.2 | PLUMBING |  | 1136900
15.3 | FIRE PROTECTION |  | 1243000
16 | ELECTRICAL |  | 9997849.7754
-
| SUB TOTAL |  | 52805619.8968
| GC 'GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 7920842.9845
-
| SUB TOTAL |  | 60726462.8814
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 60726462.8814
| ESCALATION* | 0% | 0
-
| TOTAL COST |  | 60726462.8814 | 60726462.8814
| GROSS ENCLOSED AREA - SF |  | 248600
| COST PER GSF |  | 244.2738
* SEE MAIN SUMMARY SHEET

## EST - RING BUILDING
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
RING BUILDING - CSI TRADE ESTIMATE
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
2 | SITEWORK
| DEMOLITION | [6 empty] | See separate site estimate
| EROSION AND SEDIMENT CONTROL | [6 empty] | See separate site estimate
| TREE PROTECTION | [6 empty] | See separate site estimate
| SITE UTILITIES | [6 empty] | See separate site estimate
| SITE IMPROVEMENTS | [6 empty] | See separate site estimate
| LANDSCAPING | [6 empty] | See separate site estimate
BUILDING EARTHWORK
| Building mass cut excavation and disposal on site | 26500 | CY | 5.4 | 143100 | 3.6 | 95400 | 9 | 238500
| Building isolated cut excavation and disposal on site | 20500 | CY | 5.4 | 110700 | 3.6 | 73800 | 9 | 184500
| Backfill from excavated material | 16000 | CY | 6 | 96000 | 4 | 64000 | 10 | 160000
| Use excess mass and isolated cut material to create earth berm around Ring Building and dispose unused fill off site. | 31000 | CY | 5.4 | 167400 | 3.6 | 111600 | 9 | 279000
| Crushed stone base at concrete slab on grade | 7200 | CY | 21 | 151200 | 14 | 100800 | 35 | 252000
| Vapor barrier at concrete slab on grade | 208000 | SF | 0.15 | 31200 | 0.1 | 20800 | 0.25 | 52000
| Pumping / dewatering during construction | [7 empty] | Not included
| Temporary shoring - place and remove | 1 | LS | 30000 | 30000 | 20000 | 20000 | 50000 | 50000
| Provide continuous porous drain and wrapped around aggregate with filter fabric at perimeter of utility tunnel | 2100 | LF | 15 | 31500 | 10 | 21000 | 25 | 52500
| Misc earthwork, mechanical trenching, earth ramps, hand trim etc. | 1 | LS | 60000 | 60000 | 40000 | 40000 | 100000 | 100000
[5 empty] | - |  | - |  | -
[5 empty] | 821100 |  | 547400 |  | 1368500
3 | CONCRETE
FOUNDATION CONCRETE
Concrete slab on grade. Include all reinforcing and formwork
| 8" Thick - 3,450 SF under elevated platform | 85.6111 | CY | 315 | 26967.5 | 210 | 17978.3333 | 525 | 44945.8333
| 1'-0" Thick - 23,750 SF | 879.6296 | CY | 315 | 277083.3333 | 210 | 184722.2222 | 525 | 461805.5556
| 1'-6" Thick - 131,000 SF | 7277.7778 | CY | 315 | 2292500 | 210 | 1528333.3333 | 525 | 3820833.3333
| 3'-3" Thick - 49,800 SF | 5994.4444 | CY | 315 | 1888250 | 210 | 1258833.3333 | 525 | 3147083.3333
Concrete slab on grade at labyrinths connecting five service buildings. Include all reinforcing and formwork
| 2'-6" Thick - 2,400 SF | 222.2222 | CY | 315 | 70000 | 210 | 46666.6667 | 525 | 116666.6667
| Concrete column footings. Include all reinforcing and formwork. Based on Type F7 and F11 footings shown on drawing S-101. | 2003 | CY | 315 | 630945 | 210 | 420630 | 525 | 1051575
| Concrete piers. Include all reinforcing and formwork. Type P1 See drawing S-101. | 78 | CY | 315 | 24570 | 210 | 16380 | 525 | 40950
| Concrete grade beams at outer ring wall. Include all reinforcing and formwork. See sect 1 - A-304. 300LF x 5 location x 2' x 4.4" deep | 488.8889 | CY | 315 | 154000 | 210 | 102666.6667 | 525 | 256666.6667
| Concrete piers from top of column footings to top of berm. Include all reinforcing and formwork. See drawing A-301 | 252.5995 | CY | 315 | 79568.8542 | 210 | 53045.9028 | 525 | 132614.7569
| Continuous concrete grade beams sitting on above concrete piers at inner ring wall. Include all reinforcing and formwork. See A-301 3' x 2' x 2,500 LF. | 555.5556 | CY | 315 | 175000 | 210 | 116666.6667 | 525 | 291666.6667
Concrete walls at ring tunnel. Include all reinforcing and formwork
| 1'-8" Thick - 2,093 LF x 9' HT | 1165.1033 | CY | 330 | 384484.1 | 220 | 256322.7333 | 550 | 640806.8333
| 2'-8" Thick - 2,953 LF x 9' HT | 2628.17 | CY | 330 | 867296.1 | 220 | 578197.4 | 550 | 1445493.5
| 3'-3" Thick - 470 LF x 9' HT | 509.1667 | CY | 330 | 168025 | 220 | 112016.6667 | 550 | 280041.6667
| 5'-0" Thick - 360 LF x 9' HT | 600 | CY | 330 | 198000 | 220 | 132000 | 550 | 330000
Concrete walls at labyrinths connecting five service buildings. Include all reinforcing and formwork
| 2'-8" Thick - 4,500 SF | 445 | CY | 330 | 146850 | 220 | 97900 | 550 | 244750
| Concrete roof arch over ring tunnel. Include all reinforcing, shoring, bottom and side forms. 44,200 SF | 5994.4444 | CY | 360 | 2158000 | 240 | 1438666.6667 | 600 | 3596666.6667
Concrete roof arch at labyrinths connecting five service buildings. Include all reinforcing and formwork
| 3'-3" Thick - 3,600 SF | 433.3333 | CY | 330 | 143000 | 220 | 95333.3333 | 550 | 238333.3333
| Extra cost to form out openings in concrete tunnel roof for ductwork | 122 | OPG | 300 | 36600 | 200 | 24400 | 500 | 61000
| Extra cost for 2" thick isolation joint between tunnel arch and grade beam | 2500 | LF | 30 | 75000 | 20 | 50000 | 50 | 125000
| Vehicular access tunnel below Ring Building to inner court areas. Include all earthwork, concrete slabs, walls and roof slabs, waterproofing and backfill. 72' x 16.5' wide | 1188 | SF | 105 | 124740 | 70 | 83160 | 175 | 207900
| Approach ramps to above vehicular tunnel below Ring Building to inner court areas. Include all earthwork, concrete slabs, walls, waterproofing and backfill. See drawing C-109. | [7 empty] | With Sitework
| Steam access tunnel / mechanical space below Ring Building to inner court areas. Include all earthwork, concrete slabs, walls, stairs, areaways with gratings, roof slabs, waterproofing and backfill. 88' x 22' | 1936 | SF | 111 | 214896 | 74 | 143264 | 185 | 358160
| Concrete footings at elevated platform at Ring Building as shown on drawing A101-A OPT. One location | 178 | CY | 330 | 58740 | 220 | 39160 | 550 | 97900
| Concrete footings at two future elevated platform locations at Ring Building as shown on drawing A101-A OPT. | 88.8889 | CY | 330 | 29333.3333 | 220 | 19555.5556 | 550 | 48888.8889
|  |  |  | 0 | 0 | 0 | 0 |  | 0
| Misc foundation concrete | 1 | LS | 45000 | 45000 | 30000 | 30000 | 75000 | 75000
| SUPERSTRUCTURE CONCRETE | [7 empty] | None
| Concrete fill on metal deck with wwm reinforcing at elevated steel platform at Ring Building between LOB 1 and LOB 2 as per drawing A101A-OPT. | 3450 | SF | 4.2 | 14490 | 2.8 | 9660 | 7 | 24150
[5 empty] | - |  | - |  | -
[5 empty] | 10283339.2208 |  | 6855559.4806 |  | 17138898.7014
4 | MASONRY
| EXTERIOR | [7 empty] | None
INTERIOR
| Assume interior cmu walls at main loading docks, stock room and hazard waste storage. Not indicated. See drawing A-101G 170' x 14' x 1 loc | 2380 | SF | 7.2 | 17136 | 4.8 | 11424 | 12 | 28560
[5 empty] | - |  | - |  | -
[5 empty] | 17136 |  | 11424 |  | 28560
5 | METALS
STRUCTURAL STEEL
Structural steel framing including steel beams, columns, baseplates and roof trusses. See drawing S-102
| Steel beams at inside arc supporting roof trusses | 75 | TON | 2280 | 171000 | 1520 | 114000 | 3800 | 285000
| Steel beams at outside arc supporting roof trusses | 97.02 | TON | 2280 | 221205.6 | 1520 | 147470.4 | 3800 | 368676
| Type RJ-1 special open web steel joists with curved top chord and straight bottom chord. | 220.08 | TON | 2400 | 528192 | 1600 | 352128 | 4000 | 880320
| Steel tube columns | 260.559 | TON | 2100 | 547173.9 | 1400 | 364782.6 | 3500 | 911956.5
| Electric / Mechanical steel beam and hanger support frame 2,600 sf x 29' wide x 3 lb/sf | 126.15 | TON | 1980 | 249777 | 1320 | 166518 | 3300 | 416295
| Structural steel framing at raised platform in Ring Building at one location as shown on drawing A-101A-OPT - 3,450 SF | 20.7 | TON | 1980 | 40986 | 1320 | 27324 | 3300 | 68310
| Steel base plates 262 ea x 200 lb | 26.2 | TON | 1980 | 51876 | 1320 | 34584 | 3300 | 86460
| Anchor bolts at column base plates | 1048 | EA | 60 | 62880 | 40 | 41920 | 100 | 104800
| Grout at steel baseplates | 262 | EA | 90 | 23580 | 60 | 15720 | 150 | 39300
| Addition cost for moment connections | 1 | LS | 30000 | 30000 | 20000 | 20000 | 50000 | 50000
METAL DECK
| 1 1/2" Deep 20 Gauge acoustic steel roof deck - no concrete fill - at main roof truss | 225200 | SF | 1.65 | 371580 | 1.1 | 247720 | 2.75 | 619300
| Metal deck at elevated steel platform at Ring Building between LOB 1 and LOB 2 as per drawing A101A-OPT. | 3450 | SF | 1.8 | 6210 | 1.2 | 4140 | 3 | 10350
MISC IRONWORK
| General misc ironwork - loose steel lintels, railings, bollards, embedded steel in concrete etc. | 1 | LS | 60000 | 60000 | 40000 | 40000 | 100000 | 100000
| Painted metal stairs at elevated platform at Ring Building | 3 | EA | 1500 | 4500 | 1000 | 3000 | 2500 | 7500
| Assume free standing painted metal railing at elevated platform at Ring Building | 272 | LF | 90 | 24480 | 60 | 16320 | 150 | 40800
EXTERIOR METAL PANEL WALLS
| Exterior metal panel sandwich wall system with liner including all supports | 106795 | SF | 19.2 | 2050464 | 12.8 | 1366976 | 32 | 3417440
| Exterior metal panel sandwich wall system with liner including all supports at interface between Ring Building and LOB 3 & 4 Alternates. ( Wall must be built if LOB 3 & 4 are not. (180' x 29' high x 2 locations. ) | 10440 | SF | 19.2 | 200448 | 12.8 | 133632 | 32 | 334080
[5 empty] | - |  | - |  | -
[5 empty] | 4644352.5 |  | 3096235 |  | 7740587.5
6 | WOOD AND PLASTICS
CARPENTRY
| Misc wood blocking, protection and scaffolding at Ring Building | 248600 | SF | 0.6 | 149160 | 0.4 | 99440 | 1 | 248600
MILLWORK
| Interior millwork | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 149160 |  | 99440 |  | 248600
7 | THERMAL & MOISTURE PROTECTION
ROOFING AND FLASHING
| Sloping standing seam roofing system including rigid insulation and exterior grade gypsum board sheathing ( on metal roof deck). | 233479 | SF | 9 | 2101311 | 6 | 1400874 | 15 | 3502185
| Metal soffit and fascia at sloping standing seam roof at outer ring wall | 11880 | SF | 12 | 142560 | 8 | 95040 | 20 | 237600
| Metal soffit and fascia at sloping standing seam roof at inner ring wall | 10862.5 | SF | 12 | 130350 | 8 | 86900 | 20 | 217250
| Metal gutter assembly at sloping standing seam roof at outer ring wall only | 1980 | LF | 45 | 89100 | 30 | 59400 | 75 | 148500
| Roof expansion joint assemblies at double column lines. 10 locations | 840 | LF | 30 | 25200 | 20 | 16800 | 50 | 42000
| Misc flashing and sheetmetal as required | 1 | LS | 15000 | 15000 | 10000 | 10000 | 25000 | 25000
FIRE PROOFING
| Spray on fireproofing @ beams and columns at Link Building - contact area | [7 empty] | Not required
| Fire stops at all openings in fire rated walls and slabs | 1 | LS | 15000 | 15000 | 10000 | 10000 | 25000 | 25000
INSULATION
| Misc insulation | [7 empty] | With Exterior wall systems
CAULKING
| Include all caulking and sealants with exterior wall systems | [7 empty] | With Exterior wall systems
WATERPROOFING
| Membrane waterproofing at concrete link tunnel outer walls | 41000 | SF | 3 | 123000 | 2 | 82000 | 5 | 205000
[5 empty] | - |  | - |  | -
[5 empty] | 2641521 |  | 1761014 |  | 4402535
8 | DOORS AND WINDOWS / CURTAINWALL
DOORS, FRAMES AND FINISH HARDWARE
| Furnish HM Exterior doors and frames - allowance | 10 | EA | 1200 | 12000 | 0 | 0 | 1200 | 12000
Furnish HM interior doors and frames at loading dock and storage rooms
| HM doors, frames and finish hardware | 15 | EA | 1000 | 15000 | 0 | 0 | 1000 | 15000
| Furnish and install 12" x 12" Lead lined doors and frames at concrete walls between ring tunnel and experiment hall. | 60 | EA | 1500 | 90000 | 1000 | 60000 | 2500 | 150000
| Furnish and install 10' x 6' shielded doors and frames at concrete walls between ring tunnel and experiment hall for people access | 60 | EA | 24000 | 1440000 | 16000 | 960000 | 40000 | 2400000
| Furnish and install two super sliding Lead lined doors and frames | 2 | EA | 60000 | 120000 | 40000 | 80000 | 100000 | 200000
| Furnish and install exterior motorized overhead doors and frames at loading dock 10' x 12' x 2 each See drawing A-101G | 240 | SF | 36 | 8640 | 24 | 5760 | 60 | 14400
| Furnish and install interior motorized overhead doors and frames at stock room 10' x 12' x 1 each See drawing A-101G | 120 | SF | 36 | 4320 | 24 | 2880 | 60 | 7200
| -` | 120 | SF | 36 | 4320 | 24 | 2880 | 60 | 7200
| CURTAIN WALL CONSTRUCTION | [7 empty] | None
| Exterior insulated clerestory glass walls 5'-0" high. | [7 empty] | Exclude
[5 empty] | - |  | - |  | -
[5 empty] | 1694280 |  | 1111520 |  | 2805800
9 | FINISHES
| INTERIOR WALLS | [7 empty] | With masonry
| Interior painted fire rated gypsum board walls - allowance | 2000 | SF | 7.2 | 14400 | 4.8 | 9600 | 12 | 24000
| Interior painted cmu walls at loading dock | 4760 | SF | 0.75 | 3570 | 0.5 | 2380 | 1.25 | 5950
FLOOR FINISHES
| Concrete sealer at experimental hall | 127215 | SF | 0.9 | 114493.5 | 0.6 | 76329 | 1.5 | 190822.5
WALL FINISHES
| Seal and paint cmu walls at loading docks | 10920 | SF | 0.9 | 9828 | 0.6 | 6552 | 1.5 | 16380
CEILINGS
| Unfinished exposed ceilings | 229500 | SF | [5 empty] | No work
MISC
| Paint exposed building structural steel | 805 | TON | 90 | 72450 | 60 | 48300 | 150 | 120750
| Paint exterior of concrete tunnel ring walls | 44924.28 | SF | 0.9 | 40431.852 | 0.6 | 26954.568 | 1.5 | 67386.42
| Spray paint exposed roof structure | 202464 | SF | 0.9 | 182217.6 | 0.6 | 121478.4 | 1.5 | 303696
| Paint HM doors and frames | 25 | LEAF | 39 | 975 | 26 | 650 | 65 | 1625
| Misc interior painting | 1 | LS | 9000 | 9000 | 6000 | 6000 | 15000 | 15000
[5 empty] | - |  | - |  | -
[5 empty] | 447365.952 |  | 298243.968 |  | 745609.92
10 | SPECIALTIES
| Misc specialties - fire extinguishers, corner guards, signage etc. | 1 | LS | 12000 | 12000 | 8000 | 8000 | 20000 | 20000
| Acoustic treatment allowance as per Engineer | 1 | LS | 600000 | 600000 | 400000 | 400000 | 1000000 | 1000000
[5 empty] | - |  | - |  | -
[5 empty] | 612000 |  | 408000 |  | 1020000
11 | EQUIPMENT
| Loading dock equipment | 1 | LS | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
| Equipment at ring tunnel and experiment hall | [7 empty] | Exclude
[5 empty] | - |  | - |  | -
[5 empty] | 6000 |  | 4000 |  | 10000
12 | FURNISHINGS | [7 empty] | Exclude
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | Exclude
13 | SPECIAL CONSTRUCTION | [7 empty] | Exclude
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | Exclude
14 | CONVEYING SYSTEMS
| Allow for metal pan stairs from steam mech room / tunnel below Ring Bldg to grade 1ncluding all riser / tread and platform assemblies, and stringers. One flight per building. | 4 | FLT | 9000 | 36000 | 6000 | 24000 | 15000 | 60000
[5 empty] | - |  | - |  | -
[5 empty] | 36000 |  | 24000 |  | 60000
15.1 | HVAC
Ductwork
| Galvanized, supply - high pressure, return - low pressure, exhaust - high pressure | 200399 | LBS | 2.4 | 480957.6 | 5.6 | 1122234.4 | 8 | 1603192
| Stainless steel exhaust ( hood connection to the horizontal main). | 6597 | LBS | 4.5 | 29686.5 | 10.5 | 69268.5 | 15 | 98955
| Insulation of galvanized ductwork | 91183 | SF | 1.2 | 109419.6 | 2.8 | 255312.4 | 4 | 364732
Duct accessories
| VAV boxes - install only FBO | 210 | EA | 180 | 37800 | 120 | 25200 | 300 | 63000
| Registers | 210 | EA | 120 | 25200 | 80 | 16800 | 200 | 42000
Piping
| Process cooling piping | [7 empty] | NIC
| Steam condensate | 750 | LF | 30 | 22500 | 20 | 15000 | 50 | 37500
| Low pressure supply steam | 750 | LF | 48 | 36000 | 32 | 24000 | 80 | 60000
| Condensate water supply and return | 1250 | LF | 36 | 45000 | 24 | 30000 | 60 | 75000
| Hot water supply and return | 6500 | LF | 36 | 234000 | 24 | 156000 | 60 | 390000
| Hot water VAV box coil | 110 | EA | 900 | 99000 | 600 | 66000 | 1500 | 165000
| Compressed air | 750 | LF | 12 | 9000 | 8 | 6000 | 20 | 15000
| Fittings and valves | 1 | LS | 180000 | 180000 | 120000 | 120000 | 300000 | 300000
| Insulation | 1 | LS | 135000 | 135000 | 90000 | 90000 | 225000 | 225000
| Wall and slab penetrations | 70 | EA | 1500 | 105000 | 1000 | 70000 | 2500 | 175000
| Testing and balancing | 1 | LS | 90000 | 90000 | 60000 | 60000 | 150000 | 150000
| Automatic temperature control (DDC ), incl. equipment in Service Buildings | 248600 | SF | 2.4 | 596640 | 1.6 | 397760 | 4 | 994400
| Misc and seismic restraints | 1 | LS | 60000 | 60000 | 40000 | 40000 | 100000 | 100000
[5 empty] | - |  | - |  | -
[5 empty] | 2295203.7 |  | 2563575.3 |  | 4858779
15.2 | PLUMBING
| Process system piping (nitrogen, liquid nitrogen, compressed air, deionized water, deoinized water make-up, process Cooling water (techn. Facilities) | 248600 | SF | 2.4 | 596640 | 1.6 | 397760 | 4 | 994400
| Floor drains | 50000 | SF | 1.5 | 75000 | 1 | 50000 | 2.5 | 125000
| Drinking fountains and roughing | 5 | EA | 2100 | 10500 | 1400 | 7000 | 3500 | 17500
[5 empty] | - |  | - |  | -
[5 empty] | 682140 |  | 454760 |  | 1136900
15.3 | FIRE PROTECTION
| Sprinkler heads (wet system, incl. brunches/sub branches & main from Service Bdg | 248600 | SF | 3 | 745800 | 2 | 497200 | 5 | 1243000
[5 empty] | - |  | - |  | -
[5 empty] | 745800 |  | 497200 |  | 1243000
16 | ELECTRICAL
| Furnish & install devices w/ conduit & wire | 248600 | SF | 3.3162 | 824412.9881 | 2.2108 | 549608.6587 | 5.527 | 1374021.6468
| Furnish & install telecommunication system | 248600 | SF | 3.3162 | 824412.9881 | 2.2108 | 549608.6587 | 5.527 | 1374021.6468
| Provide power, conduit and cabling for card access system | 248600 | SF | 0.58109 | 144459.0734 | 0.38739 | 96306.049 | 0.96848 | 240765.1224
| LIGHTING & BRANCH WIRING | [6 empty] | 0
| Type K (4LF Industrial) w/ 4LF MC 12/2 Flex | 480 | EA | 176.932 | 84927.3638 | 117.9547 | 56618.2426 | 294.8867 | 141545.6064
| Type P 400 Watt MH Pendant Mt)d. w/ 4LF MC 12/2 Flex | 345 | EA | 292.7338 | 100993.1776 | 195.1559 | 67328.785 | 487.8897 | 168321.9626
| Type Q (4LF Vapor Tight Surface Mtd.) w/ 2LF Seal tigh Flex 3#12 | 80 | EA | 298.4767 | 23878.14 | 198.9845 | 15918.76 | 497.4612 | 39796.9
| Type Q / EM(4LF Vapor Tight Surface Mtd.) w/ 2LF Seal tigh Flex 3#12 | 20 | EA | 298.4767 | 5969.535 | 198.9845 | 3979.69 | 497.4612 | 9949.225
| Branch Circuits: 3/4" EMT 5#12 | 11600 | LF | 18.5181 | 214809.7512 | 12.3454 | 143206.5008 | 30.8635 | 358016.252
| Branch Circuits: 3/4" EMT 4#12 for lighting on first floor plan | 750 | LF | 17.6748 | 13256.1247 | 11.7832 | 8837.4165 | 29.4581 | 22093.5412
| Light Fixture Quote( LAW Lighting: Contact: Lisa W. Tel #845-225-1366) | 1 | LS | 141570 | 141570 | 94380 | 94380 | 235950 | 235950 | Quote
FIRE ALARM
| Install Pull Stations w/ 3/4" EMT & FA Cable (15LF) | 20 | EA | 305.2812 | 6105.6237 | 203.5208 | 4070.4158 | 508.802 | 10176.0395
| Install Fire Signal Strobe w/ 3/4" EMT & FA Cable (10LF) | 90 | EA | 269.3851 | 24244.6611 | 179.5901 | 16163.1074 | 448.9752 | 40407.7685
| Install Fire Signal Horn w/ Strobe w/ 3/4" EMT & FA Cable (10LF) | 150 | EA | 269.3833 | 40407.4902 | 179.5888 | 26938.3268 | 448.9721 | 67345.817
| Install Fire Alarm Information Management System | 1 | EA | 3590.07 | 3590.07 | 2393.38 | 2393.38 | 5983.45 | 5983.45
| 3/4" EMT w/ FA Cable | 11660 | LF | 12.7572 | 148749.4576 | 8.5048 | 99166.305 | 21.2621 | 247915.7626
| Misc Items & Materials | 1 | LS | 4573.8 | 4573.8 | 3049.2 | 3049.2 | 7623 | 7623
| Fire Alarm Quote as per Simplex Grinnell (Kevin Q.) | 1 | LSQ | 77790.9 | 77790.9 | 51860.6 | 51860.6 | 129651.5 | 129651.5
ELECTRICAL POWER & FEEDERS
| 45 Kva Transformer K - Rated w/ (1) 2 1/2" Flex 3LF 5#1/0, 1#6 grd & (1) 1 1/4" Flex 3#4, 1#8 grd | 150 | EA | 5114.6336 | 767195.0368 | 3409.7557 | 511463.3579 | 8524.3893 | 1278658.3947
| 100 Amp, 120/208V, 3PH, 4W | 60 | EA | 2483.8275 | 149029.65 | 1655.885 | 99353.1 | 4139.7125 | 248382.75
| 150 Amps, 120/208V, 3PH, 4W | 30 | EA | 3949.077 | 118472.31 | 2632.718 | 78981.54 | 6581.795 | 197453.85
| 150 Amps, 120/208V, 3PH, 4W, 2 Section panel | 120 | EA | 7898.154 | 947778.48 | 5265.436 | 631852.32 | 13163.59 | 1579630.8
| 400 Amps, 480/277V, 3PH, 4W | 30 | EA | 6324.3675 | 189731.025 | 4216.245 | 126487.35 | 10540.6125 | 316218.375
| 3 1/2" EMT 4#500, 1#3 grd | 4450 | LF | 86.9382 | 386875.1271 | 57.9588 | 257916.7514 | 144.8971 | 644791.8785
| 2 1/2" EMT 5# 1/0, 1#6 grD | 1500 | LF | 40.2867 | 60430.062 | 26.8578 | 40286.708 | 67.1445 | 100716.77
| 2" EMT 3#1, 1#3/0, 2#8 grd | 4200 | LF | 30.5991 | 128516.157 | 20.3994 | 85677.438 | 50.9985 | 214193.595
| 1 1/4" EMT 3#4, 1#8 grd | 8600 | LF | 16.3432 | 140551.2405 | 10.8954 | 93700.827 | 27.2386 | 234252.0675
| Conduit & Disturbition Supports | 1 | LS | 49050 | 49050 | 32700 | 32700 | 81750 | 81750
| 1/2" RGD 1#6 grd for Transformer | 1500 | LF | 10.7312 | 16096.872 | 7.1542 | 10731.248 | 17.8854 | 26828.12
| Ground Rods and clamps | 150 | EA | 137.97 | 20695.5012 | 91.98 | 13797.0008 | 229.95 | 34492.502
| HVAC EQUIPMENT CONNECTIONS & FEEDERS | [6 empty] | 0
| Power to Motorized dampers for Exhaust Valves 3/4" EMT 3#12 | 2900 | LF | 16.8316 | 48811.5936 | 11.2211 | 32541.0624 | 28.0526 | 81352.656
| Connections to Motorized dampers for exhaust fans: 1/2" Flex 3#12 | 110 | EA | 83.5651 | 9192.1655 | 55.7101 | 6128.1103 | 139.2752 | 15320.2758
MISCELLANEOUS
| FIRE ALARM PROGRAMMING & TESTING | 1 | LS | 5263.5 | 5263.5 | 3509 | 3509 | 8772.5 | 8772.5
| Furnish & install data fire detection system | 1 | LS | 72600 | 72600 | 48400 | 48400 | 121000 | 121000
| TEMPORARY LIGHT & POWER | 248600 | SF | 0.45 | 111870 | 0.3 | 74580 | 0.75 | 186450
| PENETRATION & FIRE STOPPING | 248600 | SF | 0.3 | 74580 | 0.2 | 49720 | 0.5 | 124300
UNDERGROUND VEHICULAR TUNNEL
| Furnish & install Lighting & Branch circuits | 1188 | SF | 9 | 10692 | 6 | 7128 | 15 | 17820
| Misc. Material | 1188 | SF | 6 | 7128 | 4 | 4752 | 10 | 11880
[5 empty] | - |  | - |  | -
[5 empty] | 5998709.8653 |  | 3999139.9102 |  | 9997849.7754
[5 empty] | 31074108.2381 |  | 21731511.6587 |  | 52805619.8968
[7 empty] | 0 |  | 52805619.8968

## TRADE - SERVICE BLDGS
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
SERVICE BUILDINGS - ONE TO FIVE
TOTAL
| DESCRIPTION |  |  | AMOUNT
2 | BUILDING EARTHWORK |  |  | 280375
3 | CONCRETE |  |  | 1858881.6667
4 | MASONRY |  |  | 349560
5 | METALS |  |  | 2703777.5
6 | WOOD AND PLASTICS |  |  | 95655
7 | THERMAL AND MOISTURE PROTECTION |  |  | 656765
8 | DOORS AND WINDOWS / CURTAINWALL |  |  | 164000
9 | FINISHES |  |  | 225370
10 | SPECIALTIES |  |  | 82500
11 | EQUIPMENT |  |  | None
12 | FURNISHINGS |  |  | None
13 | SPECIAL CONSTRUCTION |  |  | None
14 | CONVEYING SYSTEMS |  |  | 700000
15.1 | HVAC |  |  | 10193790
15.2 | PLUMBING |  |  | 394875
15.3 | FIRE PROTECTION |  |  | 365820
16 | ELECTRICAL |  |  | 1770905.8704
-
| SUB TOTAL |  |  | 19842275.0371
| GC 'GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | 2976341.2556
-
| SUB TOTAL |  |  | 22818616.2926
| DESIGN CONTINGENCY * |  | 0% | 0
-
| SUB TOTAL |  |  | 22818616.2926
| ESCALATION * |  | 0% | 0
-
| TOTAL COST |  |  | 22818616.2926 | 22818616.2926
| GROSS ENCLOSED AREA - SF |  |  | 56280
| COST PER GSF |  |  | 405.4481
* SEE MAIN SUMMARY SHEET
| Service elevator - Holeless hydraulic - 2 stop, 5000 lb capacity, 100 FPM, Interior cab size 5'-11" x 8'-6". One per building | 3 | EA |  | 125000

## EST - SERVICE BLDGS
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
SERVICE BUILDINGS ONE TO FIVE - CSI TRADE ESTIMATE
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
2 | SITEWORK
| DEMOLITION | [6 empty] | See separate site estimate
| EROSION AND SEDIMENT CONTROL | [6 empty] | See separate site estimate
| TREE PROTECTION | [6 empty] | See separate site estimate
| SITE UTILITIES | [6 empty] | See separate site estimate
| SITE IMPROVEMENTS | [6 empty] | See separate site estimate
| LANDSCAPING | [6 empty] | See separate site estimate
BUILDING EARTHWORK
| Building mass cut excavation and disposal on site | 2500 | CY | 5.4 | 13500 | 3.6 | 9000 | 9 | 22500 | 0
| Building isolated cut excavation and disposal on site | 6500 | CY | 5.4 | 35100 | 3.6 | 23400 | 9 | 58500 | 0
| Backfill from excavated material | 4000 | CY | 6 | 24000 | 4 | 16000 | 10 | 40000 | 0
| Disposal on site | 5000 | CY | 5.4 | 27000 | 3.6 | 18000 | 9 | 45000 | 0
| Crushed stone base at concrete slab on grade | 1125 | CY | 21 | 23625 | 14 | 15750 | 35 | 39375 | 0
| Pumping / dewatering during construction | [7 empty] | Not required | 0
| Misc earthwork, mechanical trenching, earth ramps, hand trim etc. | 5 | BLDG | 9000 | 45000 | 6000 | 30000 | 15000 | 75000 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 168225 |  | 112150 |  | 280375 | -280375
0
3 | CONCRETE | [8 empty] | 0
| FOUNDATION CONCRETE | [8 empty] | 0
| Concrete column footings and piers - include all formwork and reinforcing. See S-106 | 195 | CY | 315 | 61425 | 210 | 40950 | 525 | 102375 | 0
| Concrete slab on grade. Include wwm and vapor barrier. 6" thick | 30455 | SF | 4.8 | 146184 | 3.2 | 97456 | 8 | 243640 | 0
| Concrete wall footings and grade beams at building perimeter. See S-302 Note: Exclude footings at column line shared with Ring Building. | 781.1111 | CY | 315 | 246050 | 210 | 164033.3333 | 525 | 410083.3333 | 0
| 2'-8" Thick concrete mat under labyrinth walls on service building side at first floor. Include reinforcing and formwork. See A-302 | 440 | CY | 315 | 138600 | 210 | 92400 | 525 | 231000 | 0
| Allow for concrete mat at base of elevator shaft. | 5 | BLDG | 3000 | 15000 | 2000 | 10000 | 5000 | 25000 | 0
| Misc foundation concrete - equipment pads, curbs etc. | 5 | BLDG | 15000 | 75000 | 10000 | 50000 | 25000 | 125000 | 0
0
| SUPERSTRUCTURE CONCRETE | [8 empty] | 0
| Concrete fill on metal deck at second floor | 25825 | SF | 3.6 | 92970 | 2.4 | 61980 | 6 | 154950 | 0
| 2'-8" Thick concrete labyrinth walls on service building side at first floor. Include reinforcing and formwork. See A-101D and A-302 | 350 | CY | 315 | 110250 | 210 | 73500 | 525 | 183750 | 0
| 3'-3" Thick concrete arch over labyrinth walls on service building side at first floor. Include reinforcing and formwork. See A-302 | 390 | CY | 315 | 122850 | 210 | 81900 | 525 | 204750 | 0
| 1'-0" Thick concrete walls at first floor. Include reinforcing and formwork. See A-101D | 84.4444 | CY | 315 | 26600 | 210 | 17733.3333 | 525 | 44333.3333 | 0
| Misc concrete equipment pads | 5 | BLDG | 6000 | 30000 | 4000 | 20000 | 10000 | 50000 | 0
0
| PRECAST CONCRETE | [8 empty] | 0
| Architectural exterior precast concrete panels at Service Buildings at grade. See drawing A-202 | 2400 | SF | 21 | 50400 | 14 | 33600 | 35 | 84000 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 1115329 |  | 743552.6667 |  | 1858881.6667 | -1858881.6667
0
4 | MASONRY | [8 empty] | 0
| EXTERIOR | [7 empty] | None | 0
0
| INTERIOR | [8 empty] | 0
| Interior cmu walls at stairs, elevators, toilets and electric switchgear room . Include second floor wall separating service buildings from ring building. | 29130 | SF | 7.2 | 209736 | 4.8 | 139824 | 12 | 349560 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 209736 |  | 139824 |  | 349560 | -349560
0
5 | METALS | [8 empty] | 0
| STRUCTURAL STEEL | [8 empty] | 0
| Structural steel framing including steel beams, columns, baseplates. See drawing S-106. | 365 | TON | 1980 | 722700 | 1320 | 481800 | 3300 | 1204500 | 0
| Shear studs at second floor only | 3010 | EA | 2.1 | 6321 | 1.4 | 4214 | 3.5 | 10535 | 0
| Anchor bolts at column base plates | 400 | EA | 60 | 24000 | 40 | 16000 | 100 | 40000 | 0
| Grout at steel baseplates | 80 | EA | 90 | 7200 | 60 | 4800 | 150 | 12000 | 0
0
| METAL DECK | [8 empty] | 0
| 1 1/2" Deep 20 Gauge acoustic steel roof deck - no concrete fill - at main roof truss | 30450 | SF | 1.5 | 45675 | 1 | 30450 | 2.5 | 76125 | 0
| 2" Deep 18 Gauge - Lok - metal deck at floors | 25825 | SF | 2.1 | 54232.5 | 1.4 | 36155 | 3.5 | 90387.5 | 0
| MISC IRONWORK | [8 empty] | 0
| Steel lintels at door and elevator openings in interior cmu walls. | 60 | OPG | 90 | 5400 | 60 | 3600 | 150 | 9000 | 0
| Steel gratings and frames at pits 9' x 6' x 5 ea | 270 | SF | 21 | 5670 | 14 | 3780 | 35 | 9450 | 0
| Painted pipe handrails at fire stairs | 250 | LF | 36 | 9000 | 24 | 6000 | 60 | 15000 | 0
| Smoke hatch and frame at elevator shaft | 5 | EA | 1500 | 7500 | 1000 | 5000 | 2500 | 12500 | 0
| General misc ironwork | 56280 | SF | 0.6 | 33768 | 0.4 | 22512 | 1 | 56280 | 0
0
| EXTERIOR METAL PANEL WALLS | [8 empty] | 0
| Exterior metal panel sandwich wall system with liner including all supports | 36500 | SF | 19.2 | 700800 | 12.8 | 467200 | 32 | 1168000 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 1622266.5 |  | 1081511 |  | 2703777.5 | -2703777.5
0
6 | WOOD AND PLASTICS | [8 empty] | 0
| CARPENTRY | [8 empty] | 0
| Install HM doors, frames and finish hardware LABOR COST ONLY | 80 | LEAF | 150 | 12000 | 0 | 0 | 150 | 12000 | 0
| Wood blocking at roof parapet walls | 1095 | LF | 15 | 16425 | 10 | 10950 | 25 | 27375 | 0
| Misc wood blocking, protection and scaffolding at Service Buildings | 56280 | SF | 0.6 | 33768 | 0.4 | 22512 | 1 | 56280 | 0
| MILLWORK | [8 empty] | 0
| Interior millwork allowance | [7 empty] | None | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 62193 |  | 33462 |  | 95655 | -95655
0
7 | THERMAL & MOISTURE PROTECTION | [8 empty] | 0
| ROOFING AND FLASHING | [8 empty] | 0
| Sloping standing seam roofing system including rigid insulation and exterior grade gypsum board sheathing ( on metal roof deck). See A-101D | 31000 | SF | 9 | 279000 | 6 | 186000 | 15 | 465000 | 0
| Metal soffit and fascia at edge of sloping standing seam roof | 1095 | SF | 12 | 13140 | 8 | 8760 | 20 | 21900 | 0
| Metal base flashing assembly where sloping metal roof meets Ring Building. | 485 | LF | 30 | 14550 | 20 | 9700 | 50 | 24250 | 0
| Metal gutter as required | 1095 | LF | 15 | 16425 | 10 | 10950 | 25 | 27375 | 0
| Misc flashing at rooftop equipment curbs, thru roof vents and roof drains | 5 | BLDG | 6000 | 30000 | 4000 | 20000 | 10000 | 50000 | 0
| FIRE PROOFING | [8 empty] | 0
| Spray on fireproofing @ beams and columns at stair / elevator enclosure only | [7 empty] | Not required | 0
| Fire stops at all openings in fire rated walls and slabs | 5 | BLDG | 6000 | 30000 | 4000 | 20000 | 10000 | 50000 | 0
| INSULATION | [8 empty] | 0
| Misc insulation ( all wall insulation with GB ) | [7 empty] | With Exterior wall systems | 0
| CAULKING | [8 empty] | 0
| Include all caulking and sealants with exterior wall systems | [7 empty] | With Exterior wall systems | 0
| Membrane waterproofing at foundation retaining walls adjacent to earth berm | 2280 | SF | 4.8 | 10944 | 3.2 | 7296 | 8 | 18240 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 394059 |  | 262706 |  | 656765 | -656765
0
8 | DOORS AND WINDOWS / CURTAINWALL | [8 empty] | 0
| DOORS, FRAMES AND FINISH HARDWARE | [8 empty] | 0
| Furnish HM Exterior doors and frames | [8 empty] | 0
| HM doors, frames and finish hardware | 10 | EA | 1000 | 10000 | 0 | 0 | 1000 | 10000 | 0
0
| Furnish HM interior doors and frames | [8 empty] | 0
| HM doors, frames and finish hardware | 50 | EA | 900 | 45000 | 0 | 0 | 900 | 45000 | 0
| HM doors, frames and finish hardware | 10 | PR | 1800 | 18000 | 0 | 0 | 1800 | 18000 | 0
| Extra cost for vision lites and frames at HM doors | 5 | BLDG | 6000 | 30000 | 0 | 0 | 6000 | 30000 | 0
| Furnish and install painted metal access doors and frames for MEP trades | 5 | BLDG | 3000 | 15000 | 2000 | 10000 | 5000 | 25000 | 0
| Furnish and install exterior motorized overhead doors and frames 12' x 10' x 5 ea | 600 | SF | 36 | 21600 | 24 | 14400 | 60 | 36000 | 0
0
| INTERIOR GLAZING | [7 empty] | None | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 139600 |  | 24400 |  | 164000 | -164000
0
9 | FINISHES | [8 empty] | 0
| INTERIOR WALLS | [7 empty] | With masonry | 0
0
| FLOOR FINISHES | [8 empty] | 0
| Concrete sealer | 56280 | SF | 0.6 | 33768 | 0.4 | 22512 | 1 | 56280 | 0
0
| WALL FINISHES | [8 empty] | 0
| Seal and paint cmu walls | 23000 | SF | 0.9 | 20700 | 0.6 | 13800 | 1.5 | 34500 | 0
0
| CEILINGS | [8 empty] | 0
| Unfinished exposed ceilings | 56280 | SF | [5 empty] | No work | 0
0
| MISC | [8 empty] | 0
| Paint exposed building structural steel | 365 | TON | 90 | 32850 | 60 | 21900 | 150 | 54750 | 0
| Spray paint exposed roof structure | 31000 | SF | 0.9 | 27900 | 0.6 | 18600 | 1.5 | 46500 | 0
| Paint HM doors and frames | 80 | LEAF | 39 | 3120 | 26 | 2080 | 65 | 5200 | 0
| Misc interior painting | 56280 | SF | 0.3 | 16884 | 0.2 | 11256 | 0.5 | 28140 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 135222 |  | 90148 |  | 225370 | -225370
0
10 | SPECIALTIES | [8 empty] | 0
| Misc specialties - fire extinguishers, corner guards, signage, toilet accessories | 5 | BLDG | 3000 | 15000 | 2000 | 10000 | 5000 | 25000 | 0
| Metal lockers 5 per building | 25 | EA | 180 | 4500 | 120 | 3000 | 300 | 7500 | 0
| Exterior metal ventilation louvers and frames | 5 | BLDG | 6000 | 30000 | 4000 | 20000 | 10000 | 50000 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 49500 |  | 33000 |  | 82500 | -82500
0
11 | EQUIPMENT | [7 empty] | None | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 0 |  | 0 |  | None | 0
0
0
12 | FURNISHINGS | [7 empty] | None | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 0 |  | 0 |  | None | 0
0
13 | SPECIAL CONSTRUCTION | [7 empty] | None | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 0 |  | 0 |  | None | 0
0
14 | CONVEYING SYSTEMS | [8 empty] | 0
| Service elevator - Holeless hydraulic - 2 stop, 5000 lb capacity, 100 FPM, Interior cab size 5'-11" x 8'-6". One per building | 5 | EA | 75000 | 375000 | 50000 | 250000 | 125000 | 625000 | 0
| Metal pan fire stairs including all riser / tread and platform assemblies, and stringers. One flight per building. | 5 | FLT | 9000 | 45000 | 6000 | 30000 | 15000 | 75000 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 420000 |  | 280000 |  | 700000 | -700000
0
15.1 | HVAC | [8 empty] | 0
| Equipment | [8 empty] | 0
| Packaged RTU custom made 2" double wall construction gavanized steel interior liner, S & R fans, cooling and steam preheating coils, filters, humidifier, etc. | [8 empty] | 0
| For Experim. Hall service (sound attenuator)- 2ea total, say 125Tn/each | 1250 | TN | 800 | 1000000 | 3000 | 4000000 | 4000 | 5000000 | 0
| For Ring Bdg service- 1 ea | 250 | TN | 800 | 200000 | 3000 | 800000 | 4000 | 1000000 | 0
| Exhaust fan for Lab. fume hood, Strobic type, total three fans | 5 | SET | 4000 | 20000 | 16000 | 80000 | 20000 | 100000 | 0
| Exhaust fans, general (misc. rooms & toilet) | 30000 | CFM | 0.6 | 18000 | 1.4 | 42000 | 2 | 60000 | 0
| Water pumps at first floor | 20 | EA | 1500 | 30000 | 3500 | 70000 | 5000 | 100000 | 0
| Condensate pumps, double with receiver at first floor | 5 | SET | 1500 | 7500 | 3500 | 17500 | 5000 | 25000 | 0
| Water pumps at second floor | 10 | EA | 1500 | 15000 | 3500 | 35000 | 5000 | 50000 | 0
| Heat exchangers at first floor | 5 | EA | 3000 | 15000 | 7000 | 35000 | 10000 | 50000 | 0
| Heat exchangers at second floor | 10 | EA | 3000 | 30000 | 7000 | 70000 | 10000 | 100000 | 0
| Process cooling water filter, tank and air separator | 5 | EA | 1500 | 7500 | 3500 | 17500 | 5000 | 25000 | 0
0
| Ductwork beyond mechanical room | [8 empty] | 0
| Galvanized | 145895 | LBS | 2.4 | 350148 | 5.6 | 817012 | 8 | 1167160 | 0
| Duct accessories and louvers | 350 | LBS | 45 | 15750 | 105 | 36750 | 150 | 52500 | 0
| Insulation of galvanized ducts | 62250 | SF | 1.2 | 74700 | 2.8 | 174300 | 4 | 249000 | 0
0
| Piping | [8 empty] | 0
| Incoming services - Include connection to new main pipe 5' length, underground beyond service building, sleeves, link seal, welding, earthwork etc. | [8 empty] | 0
| 5" LPS | 5 | CONN | 30000 | 150000 | 20000 | 100000 | 50000 | 250000 | 0
| 2" CPD | [7 empty] | Included above | 0
| 8" CWS & R | 10 | CONN | 1762.8 | 17628 | 1175.2 | 11752 | 2938 | 29380 | 0
| 6" CTS & R | 10 | CONN | 1320 | 13200 | 880 | 8800 | 2200 | 22000 | 0
| 6" Fire protection, 3" domestic water and 1" compressed air | [7 empty] | With Plumbing | 0
0
| Process Cooling Tower Water system (Condenser water system) | [8 empty] | 0
| Condenser water pipe beyond of Mech. room., black steel, sch 40, w/ fittings, valves, hangers, anchors incl. piping of heat pump (evaporator) & exchanger | 5 | SET | 75000 | 375000 | 50000 | 250000 | 125000 | 625000 | 0
| Insulation | 1 | LS | 100000 | 100000 | 50000 | 50000 | 150000 | 150000 | 0
0
| Steam & condensate system | [8 empty] | 0
| Steam & condensate pipe beyond of Mech. room, black steel, sch 40 & 80, welded w/ fittings, valves, hangers, anchors | 1250 | LF | 50 | 62500 | 50 | 62500 | 100 | 125000 | 0
| Hook - up of equipment | [8 empty] | 0
| AHU steam coil w/ 2-way control valve | 20 | Set | 4038 | 80760 | 3500 | 70000 | 7538 | 150760 | 0
| HX (steam side) | 5 | Set | 3230 | 16150 | 3000 | 15000 | 6230 | 31150 | 0
| Condensate pump, duplex w/ receiver incl. condens. pipes return @ rigs | 5 | Set | 4480 | 22400 | 3520 | 17600 | 8000 | 40000 | 0
0
0
| Cooled water system | [8 empty] | 0
| Cooled water pipe include fittings, valves hangers and anchors | 800 | LF | 110 | 88000 | 0 | 0 | 110 | 88000 | 0
| Hook up of AHU, coiling coil | 15 | EA | 15000 | 225000 | 0 | 0 | 15000 | 225000 | 0
| HX (steam side) | 1 | LS | 10000 | 10000 | 0 | 0 | 10000 | 10000 | 0
| Insulation | 1 | LS | 50000 | 50000 | 0 | 0 | 50000 | 50000 | 0
0
| Heating Water system | [8 empty] | 0
| Hot water S&R pipe beyond of Mech. room, black steel, sch 40 & 80, welded w/ fittings, valves, hangers, anchors | 500 | LF | 50 | 25000 | 50 | 25000 | 100 | 50000 | 0
| Hook - up of | [8 empty] | 0
| AHU reheat coil w/ 2-way control valve | 5 | Set | 4038 | 20190 | 3500 | 17500 | 7538 | 37690 | 0
| HX (water side) | 5 | Set | 3230 | 16150 | 3000 | 15000 | 6230 | 31150 | 0
| Insulation | 1 | LS | 30000 | 30000 | 20000 | 20000 | 50000 | 50000 | 0
0
| Testing & balancing | [7 empty] | Refer to Ring Bldg | 0
| Automatic temperature control (DDC) | [7 empty] | Refer to Ring Bldg | 0
| Misc. | 5 | BLDG | 30000 | 150000 | 20000 | 100000 | 50000 | 250000 | 0
| Rigging (AHU, EF, pumps) | [7 empty] | incl. above | 0
| HVAC of Mech. Room | [7 empty] | incl. above | 0
| Support for duct & pipes | [7 empty] | incl. above | 0
| Patching (cutting by GC ) | [7 empty] | incl. above | 0
| Seismic restraints | [7 empty] | incl. above | 0
| Commissioning, submittal, shop dwg, "as built" dwg | [7 empty] | incl. above | 0
| Conc. pads, steel - by GC | [7 empty] | incl. above | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 3235576 |  | 6958214 |  | 10193790 | -10193790
0
15.2 | PLUMBING | [8 empty] | 0
| Domestic water incoming service w/meter & DDCHV assembly | [8 empty] | 0
| 3" for Domestic water system | 5 | Set | 6750 | 33750 | 8250 | 41250 | 15000 | 75000 | 0
| 6" for Fire protection system | 5 | Set | 11250 | 56250 | 13750 | 68750 | 25000 | 125000 | 0
| Roof drain | 30455 | SF | 0.3 | 9136.5 | 0.7 | 21318.5 | 1 | 30455 | 0
| Floor drain | 56280 | SF | 0.45 | 25326 | 1.05 | 59094 | 1.5 | 84420 | 0
| Piping beyond of MEP room incl. domestic water heater (electr.), mix. valve assembly | 1 | LS | 22500 | 22500 | 27500 | 27500 | 50000 | 50000 | 0
| Unisex toilet plumbing fixtures | 10 | EA | 1350 | 13500 | 1650 | 16500 | 3000 | 30000 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 160462.5 |  | 234412.5 |  | 394875 | -394875
0
15.3 | FIRE PROTECTION | [8 empty] | 0
| Fire protection for Service Buildings no 1 to no 5 based on gross enclosed area | 56280 | SF | 3.9 | 219492 | 2.6 | 146328 | 6.5 | 365820 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 219492 |  | 146328 |  | 365820 | -365820
0
16 | ELECTRICAL | [8 empty] | 0
| Furnish & Install 1x4 industrial Light fixtures (Allow) | 210 | EA | 339.7375 | 71344.8767 | 226.4917 | 47563.2511 | 566.2292 | 118908.1278 | 0 | 1.15
| Furnish & Install Exit Signs w/ 4LF MC 12/2 Flex (Allow) | 20 | EA | 291.3133 | 5826.2662 | 194.2089 | 3884.1774 | 485.5222 | 9710.4436 | 0
| 3/4" EMT 3#12 For Pendant Mtd Fixtures @ Exposed Ceiling) | 2280 | LF | 15.5794 | 35520.9875 | 10.3863 | 23680.6583 | 25.9656 | 59201.6458 | 0
| Furnish & Install (2X4) w/ 4LF MC 12/2 Flex in Toliet | 10 | EA | 308.0113 | 3080.1131 | 205.3409 | 2053.4087 | 513.3522 | 5133.5218 | 0
| WIRING DEVICES & BRANCH WIRING |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GFI w/ J.B. & 25LF 12/2MC (Indoor) | 80 | EA | 192.4966 | 15399.7305 | 128.3311 | 10266.487 | 320.8277 | 25666.2175 | 0
| Duplex w/ J.B. & 25 LF 3/4" EMT 3#12 | 40 | EA | 229.752 | 9190.0783 | 153.168 | 6126.7188 | 382.9199 | 15316.7971 | 0
| Switch w/ J.B. & 20 LF 3/4" EMT 3#12 | 70 | EA | 174.6754 | 12227.2775 | 116.4503 | 8151.5183 | 291.1257 | 20378.7958 | 0
| Tele / Data jack w/ 1" EMT & (4) CAT5e Cable (10LF) | 10 | EA | 240.0337 | 2400.3375 | 160.0225 | 1600.225 | 400.0562 | 4000.5625 | 0
| 3/4" EMT 5#12 Devices | 1250 | LF | 18.5181 | 23147.6025 | 12.3454 | 15431.735 | 30.8635 | 38579.3375 | 0
| CARD ACCESS SYSTEM |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Card readers w/ 3/4" EMT & Cabling (15LF) | 5 | EA | 150.449 | 752.2449 | 100.2993 | 501.4966 | 250.7483 | 1253.7415 | 0
| Power to Card Access Control panel: 3/4" EMT 4#12 | 100 | LF | 15.5802 | 1558.02 | 10.3868 | 1038.68 | 25.967 | 2596.7 | 0
| 3/4" EMT w/ Cabling from each Card Acces Point to Control panel | 600 | LF | 9.6598 | 5795.8758 | 6.4399 | 3863.9172 | 16.0997 | 9659.793 | 0
| FIRE ALARM SYSTEM |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Install Fire alarm control Panel (4100U Series) w/ misc. material | 5 | EA | 4424.97 | 22124.85 | 2949.98 | 14749.9 | 7374.95 | 36874.75 | 0
| Install Pull Stations w/ 3/4" EMT & FA Cable (15LF) | 10 | EA | 305.2812 | 3052.8118 | 203.5208 | 2035.2079 | 508.802 | 5088.0197 | 0
| Install Fire Signal Strobe w/ 3/4" EMT & FA Cable (10LF) | 10 | EA | 269.4222 | 2694.2223 | 179.6148 | 1796.1482 | 449.037 | 4490.3705 | 0
| Install Fire Signal Horn w/ Strobe w/ 3/4" EMT & FA Cable (10LF) | 25 | EA | 269.3721 | 6734.3034 | 179.5814 | 4489.5356 | 448.9536 | 11223.839 | 0
| Install Smoke Detectors w/ 3/4" EMT & FA Cable (10LF) | 20 | EA | 269.3805 | 5387.6097 | 179.587 | 3591.7398 | 448.9675 | 8979.3495 | 0
| Install Heat Detectors w/ 3/4" EMT & FA Cable (10LF) | 15 | EA | 269.3944 | 4040.916 | 179.5963 | 2693.944 | 448.9907 | 6734.86 | 0
| Install Duct Detectors w/ 3/4" EMT & FA Cable (10LF) Assume | 40 | EA | 269.3805 | 10775.2194 | 179.587 | 7183.4796 | 448.9675 | 17958.699 | 0
| Interfacing w/ Info. Management System @ Security FronT Entrance in Booster Ring: 3/4" RGS w FA Cable | 1500 | LF | 11.6969 | 17545.4235 | 7.798 | 11696.949 | 19.4949 | 29242.3725 | 0
| 3/4" EMT w/ FA Cable | 2300 | LF | 9.6598 | 22217.5239 | 6.4399 | 14811.6826 | 16.0997 | 37029.2065 | 0
| 3/4" EMT w/ FA Cable to Duct Detectors | 6000 | LF | 7.439 | 44633.754 | 4.9593 | 29755.836 | 12.3983 | 74389.59 | 0
| 3/4" RGS 4 #10 | 550 | LF | 22.2939 | 12261.645 | 14.8626 | 8174.43 | 37.1565 | 20436.075 | 0
| Grounding to Building 3/4" RGS 1 #10 | 500 | LF | 11.1543 | 5577.132 | 7.4362 | 3718.088 | 18.5904 | 9295.22 | 0
| Fire Alarm Quote as per Simplex Grinnell (Kevin Q.) | 1 | LSQ | 109626 | 109626 | 73084 | 73084 | 182710 | 182710 | 0
| DISTRIBUTION EQUIPMENT & FEEDERS | [8 empty] | 0
| 15 KVA Transformers T- Rated w/ 1 1/4" Flex 3#6, 1#8grd (3LF) & 3/4" Flex 4#10(3LF) | 10 | EA | 2767.4681 | 27674.6808 | 1844.9787 | 18449.7872 | 4612.4468 | 46124.4679 | 0
| 100 Amp, 120/208V, 3PH, 4W | 10 | EA | 2483.8275 | 24838.275 | 1655.885 | 16558.85 | 4139.7125 | 41397.125 | 0
| 600 Amp, 480/277V, 3PH, 4W, 2 section panel | 10 | EA | 16430.832 | 164308.32 | 10953.888 | 109538.88 | 27384.72 | 273847.2 | 0
| (2) Sets of 3" EMT 4#350, 1 #1 grd | 1000 | LF | 68.061 | 68061.048 | 45.374 | 45374.032 | 113.4351 | 113435.08 | 0
| 1 1/4" EMT 3#6, 1#8 grd | 100 | LF | 14.6274 | 1462.7448 | 9.7516 | 975.1632 | 24.3791 | 2437.908 | 0
| 3/4" EMT 4#10 | 100 | LF | 17.7399 | 1773.99 | 11.8266 | 1182.66 | 29.5665 | 2956.65 | 0
| HVAC EQUIPMENT CONNECTIONS & FEEDERS | [6 empty] | 0 |  | 0
| AHU 201A & 201B (100 Amps): 1 1/4" EMT 4#2 | 600 | LF | 29.0628 | 17437.68 | 19.3752 | 11625.12 | 48.438 | 29062.8 | 0
| AHU 101A & 101B (30 Amps): 3/4" EMT 4#10 | 400 | LF | 17.7399 | 7095.96 | 11.8266 | 4730.64 | 29.5665 | 11826.6 | 0
| GFI w/ J.B. & 25 LF 3/4" EMT 3#12 for Pumps #1 &3 | 10 | EA | 453.8516 | 4538.5164 | 302.5678 | 3025.6776 | 756.4194 | 7564.194 | 0
| 3/4" EMT 3#12 | 1000 | LF | 16.8316 | 16831.584 | 11.2211 | 11221.056 | 28.0526 | 28052.64 | 0
| Power to heat exchangers: 3/4" EMT 3#10 | 3750 | LF | 16.8843 | 63316.125 | 11.2562 | 42210.75 | 28.1405 | 105526.875 | 0
| Power to Cooling towers #2 Assuming to be 175 Amps: 2" RGS 4# 2/0 | 500 | LF | 40.5511 | 20275.5465 | 27.0341 | 13517.031 | 67.5852 | 33792.5775 | 0
| Power to Cooling towers #1: Assuming to be 100 Amps: 1 1/4" RGS 4# 2 | 500 | LF | 26.9172 | 13458.588 | 17.9448 | 8972.392 | 44.862 | 22430.98 | 0
| Power to Pumps: 3/4" EMT 4#10 | 4000 | LF | 17.7399 | 70959.6 | 11.8266 | 47306.4 | 29.5665 | 118266 | 0
| Power to exhaust fans: 3/4" EMT 3#12 | 500 | LF | 16.8291 | 8414.55 | 11.2194 | 5609.7 | 28.0485 | 14024.25 | 0
| ELEVATOR EQUIPMENT | [6 empty] | 0 |  | 0
| Power to Elevator Control Panel: 1 1/4" EMT 4#2 ( Assume 100 Amps) | 550 | LF | 20.5082 | 11279.499 | 13.6721 | 7519.666 | 34.1803 | 18799.165 | 0
| Furnish & Install Elevator Pit Light fixture | 5 | EA | 209.994 | 1049.9702 | 139.996 | 699.9802 | 349.9901 | 1749.9504 | 0
| Switch w/ J.B. & 20 LF 3/4" RGS 3#12 | 5 | EA | 193.8304 | 969.1519 | 129.2203 | 646.1013 | 323.0506 | 1615.2532 | 0
| GFI Duplex w/ J.B. & 25 LF 3/4" RGS 3#12 | 5 | EA | 348.0364 | 1740.1821 | 232.0243 | 1160.1214 | 580.0607 | 2900.3034 | 0
| 100 Amp Disc. Switch | 5 | EA | 798.6653 | 3993.3267 | 532.4436 | 2662.2178 | 1331.1089 | 6655.5445 | 0
| 30 Amp Disc. Sw. for Cab Light & Misc Power | 10 | EA | 450.846 | 4508.46 | 300.564 | 3005.64 | 751.41 | 7514.1 | 0
| 3/4" EMT 4#10 | 750 | LF | 9.1845 | 6888.3424 | 6.123 | 4592.2283 | 15.3074 | 11480.5707 | 0
| Misc Equipment Connections | 5 | LS | 1569.612 | 7848.06 | 1046.408 | 5232.04 | 2616.02 | 13080.1 | 0
| MISCELLANEOUS | [8 empty] | 0
| FIRE ALARM PROGRAMMING & TESTING | 1 | LS | 8167.5 | 8167.5 | 5445 | 5445 | 13612.5 | 13612.5 | 0
| TEMPORARY LIGHT & POWER | 56280 | SF | 0.45 | 25326 | 0.3 | 16884 | 0.75 | 42210 | 0
| PENETRATION & FIRE STOPPING | 56280 | SF | 0.3 | 16884 | 0.2 | 11256 | 0.5 | 28140 | 0
| GROUNDING SYSTEM | 1 | LS | 10527 | 10527 | 7018 | 7018 | 17545 | 17545 | 0
[5 empty] | - |  | - |  | - | 0
[5 empty] | 1062543.5222 |  | 708362.3482 |  | 1770905.8704 | -1770905.8704
[5 empty] | 8994204.5222 |  | 10848070.5148 |  | 19842275.0371
[7 empty] | 0 |  | 19842275.0371

## TRADE - RF SERVICE BLDG
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
RF SERVICE BUILDING
TOTAL
| DESCRIPTION |  | AMOUNT
2 | BUILDING EARTHWORK |  | 44300
3 | CONCRETE |  | 405205.3611
4 | MASONRY |  | 29256
5 | METALS |  | 456463
6 | WOOD AND PLASTICS |  | 24806
7 | THERMAL AND MOISTURE PROTECTION |  | 147322
8 | DOORS AND WINDOWS / CURTAINWALL |  | 17700
9 | FINISHES |  | 47989
10 | SPECIALTIES |  | 7500
11 | EQUIPMENT |  | None
12 | FURNISHINGS |  | None
13 | SPECIAL CONSTRUCTION |  | 161500
14 | CONVEYING SYSTEMS |  | 0
15.1 | HVAC |  | 243900
15.2 | PLUMBING |  | 146340
15.3 | FIRE PROTECTION |  | 58280
16 | ELECTRICAL |  | 370549.8168
-
| SUB TOTAL |  | 2161111.178
| GC 'GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 324166.6767
-
| SUB TOTAL |  | 2485277.8546
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 2485277.8546
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 2485277.8546 | 2485277.8546
| GROSS ENCLOSED AREA - 9200 SF Service Building |  | 9756
| COST PER GSF |  | 254.7435
* SEE MAIN SUMMARY SHEET

## EST - RF SERVICE BLDG
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
RF SERVICE BUILDING - CSI TRADE ESTIMATE
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
2 | SITEWORK
| DEMOLITION | [6 empty] | See separate site estimate
| EROSION AND SEDIMENT CONTROL | [6 empty] | See separate site estimate
| TREE PROTECTION | [6 empty] | See separate site estimate
| SITE UTILITIES | [6 empty] | See separate site estimate
| SITE IMPROVEMENTS | [6 empty] | See separate site estimate
| LANDSCAPING | [6 empty] | See separate site estimate
BUILDING EARTHWORK
| Building mass cut excavation and disposal on site | 550 | CY | 5.4 | 2970 | 3.6 | 1980 | 9 | 4950
| Building isolated cut excavation and disposal on site | 900 | CY | 5.4 | 4860 | 3.6 | 3240 | 9 | 8100
| Backfill from excavated material | 600 | CY | 6 | 3600 | 4 | 2400 | 10 | 6000
| Disposal on site | 850 | CY | 5.4 | 4590 | 3.6 | 3060 | 9 | 7650
| Crushed stone base at concrete slab on grade | 360 | CY | 21 | 7560 | 14 | 5040 | 35 | 12600
| Pumping / dewatering during construction | [7 empty] | Not included
| Misc earthwork, mechanical trenching, earth ramps, hand trim etc. | 1 | LS | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
[5 empty] | - |  | - |  | -
[5 empty] | 26580 |  | 17720 |  | 44300
3 | CONCRETE
FOUNDATION CONCRETE
| Concrete column footings and piers - include all formwork and reinforcing | 72 | CY | 315 | 22680 | 210 | 15120 | 525 | 37800
| Concrete slab on grade. Include wwm and vapor barrier. 6" thick | 9756 | SF | 4.8 | 46828.8 | 3.2 | 31219.2 | 8 | 78048
| Concrete wall footings and grade beams at building perimeter | 171.2963 | CY | 315 | 53958.3333 | 210 | 35972.2222 | 525 | 89930.5556
| '2'-8" Thick concrete mat under labyrinth walls on RF Service Building side at first floor. Include reinforcing and formwork. Similar to drawing A-302 | 80.1 | CY | 315 | 25231.5 | 210 | 16821 | 525 | 42052.5
| Reinforced concrete slab on grade at free standing prefab helium compressor building | 1900 | SF | 7.2 | 13680 | 4.8 | 9120 | 12 | 22800
| Misc foundation concrete | 1 | LS | 1500 | 1500 | 1000 | 1000 | 2500 | 2500
SUPERSTRUCTURE CONCRETE
| Concrete fill on metal deck at roof | [7 empty] | Not required
| 2'-8" Thick concrete labyrinth walls on service building side at first floor. Include reinforcing and formwork. Similar to drawing A-302. | 118.6667 | CY | 315 | 37380 | 210 | 24920 | 525 | 62300
| '3'-3" Thick concrete arch over labyrinth walls on service building side at first floor. Include reinforcing and formwork. Similar to drawing A-302 | 123.3796 | CY | 315 | 38864.5833 | 210 | 25909.7222 | 525 | 64774.3056
| Misc concrete equipment pads | 1 | LS | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
[5 empty] | - |  | - |  | -
[5 empty] | 243123.2167 |  | 162082.1444 |  | 405205.3611
4 | MASONRY
| INTERIOR | [7 empty] | None
| Interior cmu walls | 2438 | SF | 7.2 | 17553.6 | 4.8 | 11702.4 | 12 | 29256
[5 empty] | - |  | - |  | -
[5 empty] | 17553.6 |  | 11702.4 |  | 29256
5 | METALS
STRUCTURAL STEEL
| Structural steel framing including steel beams, columns, baseplates and windbracing. Allow 15# / SF | 73.17 | TON | 1980 | 144876.6 | 1320 | 96584.4 | 3300 | 241461
| Anchor bolts at column base plates | 40 | EA | 60 | 2400 | 40 | 1600 | 100 | 4000
| Grout at steel baseplates | 10 | EA | 90 | 900 | 60 | 600 | 150 | 1500
METAL DECK
| 1 1/2" Deep 18 Gauge Type B roof deck - no concrete fill - at main roof, set back roofs and penthouse roof | 9756 | SF | 1.5 | 14634 | 1 | 9756 | 2.5 | 24390
MISC IRONWORK
| General misc ironwork, rooftop dunnage steel | 9756 | SF | 1.2 | 11707.2 | 0.8 | 7804.8 | 2 | 19512
EXTERIOR METAL PANEL WALLS
| Exterior insulated metal panel wall system including all supports | 5175 | SF | 19.2 | 99360 | 12.8 | 66240 | 32 | 165600
[5 empty] | - |  | - |  | -
[5 empty] | 273877.8 |  | 182585.2 |  | 456463
6 | WOOD AND PLASTICS
CARPENTRY
| Install HM doors, frames and finish hardware LABOR COST ONLY | 7 | LEAF | 150 | 1050 | 0 | 0 | 150 | 1050
| Wood blocking at gravel stop at roof edge | 250 | LF | 12 | 3000 | 8 | 2000 | 20 | 5000
| Wood blocking at base flashing at intersection of roof and exterior walls | 360 | LF | 15 | 5400 | 10 | 3600 | 25 | 9000
| Misc wood blocking, protection and scaffolding at RF Service Building | 9756 | SF | 0.6 | 5853.6 | 0.4 | 3902.4 | 1 | 9756
MILLWORK
| Interior millwork allowance | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 15303.6 |  | 9502.4 |  | 24806
7 | THERMAL & MOISTURE PROTECTION
ROOFING AND FLASHING
| Flat membrane roofing system including rigid insulation | 9756 | SF | 7.2 | 70243.2 | 4.8 | 46828.8 | 12 | 117072
| Metal gravel stop at roof edge | 250 | LF | 15 | 3750 | 10 | 2500 | 25 | 6250
| Base flashing at roof / wall intersections, and equipment curbs | 360 | LF | 15 | 5400 | 10 | 3600 | 25 | 9000
| Misc flashing at rooftop equipment curbs, thru roof vents and roof drains | 1 | LS | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
FIRE PROOFING
| Spray on fireproofing @ beams and columns | [7 empty] | Not Required
| Fire stops at all openings in fire rated walls and slabs | 1 | LS | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
INSULATION
| Misc insulation ( all wall insulation with GB ) | [7 empty] | With Exterior wall systems
CAULKING
| Include all caulking and sealants with exterior wall systems | [7 empty] | With Exterior wall systems
[5 empty] | - |  | - |  | -
[5 empty] | 88393.2 |  | 58928.8 |  | 147322
8 | DOORS AND WINDOWS / CURTAINWALL
DOORS, FRAMES AND FINISH HARDWARE
Furnish HM Exterior doors and frames
| HM doors, frames and finish hardware | 2 | EA | 1000 | 2000 | 0 | 0 | 1000 | 2000
Furnish HM interior doors and frames
| HM doors, frames and finish hardware | 1 | EA | 900 | 900 | 0 | 0 | 900 | 900
| HM doors, frames and finish hardware | 2 | PR | 1800 | 3600 | 0 | 0 | 1800 | 3600
| Extra cost for vision lites and frames at HM doors | 1 | LS | 2000 | 2000 | 0 | 0 | 2000 | 2000
| Furnish and install painted metal access doors and frames for MEP trades | 1 | LS | 1200 | 1200 | 800 | 800 | 2000 | 2000
| Furnish and install exterior motorized overhead doors and frames 12' x 10' x 1ea | 120 | SF | 36 | 4320 | 24 | 2880 | 60 | 7200
| INTERIOR GLAZING | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 14020 |  | 3680 |  | 17700
9 | FINISHES
| INTERIOR WALLS | [7 empty] | With masonry
FLOOR FINISHES
| Concrete sealer | 9756 | SF | 0.9 | 8780.4 | 0.6 | 5853.6 | 1.5 | 14634
WALL FINISHES
| Seal and paint cmu walls - one side | 2438 | SF | 0.6 | 1462.8 | 0.4 | 975.2 | 1 | 2438
CEILINGS
| Unfinished exposed ceilings | 9756 | SF | [5 empty] | No work
MISC
| Paint exposed building structural steel | 73 | TON | 90 | 6570 | 60 | 4380 | 150 | 10950
| Spray paint exposed roof structure | 9756 | SF | 0.9 | 8780.4 | 0.6 | 5853.6 | 1.5 | 14634
| Paint HM doors and frames | 7 | LEAF | 39 | 273 | 26 | 182 | 65 | 455
| Misc interior painting | 9756 | SF | 0.3 | 2926.8 | 0.2 | 1951.2 | 0.5 | 4878
[5 empty] | - |  | - |  | -
[5 empty] | 28793.4 |  | 19195.6 |  | 47989
10 | SPECIALTIES
| Misc specialties - fire extinguishers, corner guards, signage etc. | 1 | BLDG | 1500 | 1500 | 1000 | 1000 | 2500 | 2500
| Exterior metal ventilation louvers and frames | 1 | BLDG | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
[5 empty] | - |  | - |  | -
[5 empty] | 4500 |  | 3000 |  | 7500
11 | EQUIPMENT | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
12 | FURNISHINGS | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
13 | SPECIAL CONSTRUCTION
| Furnish and install Prefabricated Helium Compressor Building. Include structure, roof, exterior façade and exterior doors. | 1900 | SF | 15 | 28500 | 10 | 19000 | 25 | 47500
| Furnish and install MEP SYSTEMS AT Prefabricated Helium Compressor Building. | 1900 | SF | 36 | 68400 | 24 | 45600 | 60 | 114000
[5 empty] | - |  | - |  | -
[5 empty] | 96900 |  | 64600 |  | 161500
14 | CONVEYING SYSTEMS | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | 0
15.1 | HVAC
| RF Service Building - based on gross enclosed area. Roof top units | 9756 | SF | 15 | 146340 | 10 | 97560 | 25 | 243900
[5 empty] | - |  | - |  | -
[5 empty] | 146340 |  | 97560 |  | 243900
15.2 | PLUMBING
| RF Service Building - based on gross enclosed area | 9756 | SF | 9 | 87804 | 6 | 58536 | 15 | 146340
[5 empty] | - |  | - |  | -
[5 empty] | 87804 |  | 58536 |  | 146340
15.3 | FIRE PROTECTION
| RF Service Building - based on gross enclosed area | 9756 | SF | 3 | 29268 | 2 | 19512 | 5 | 48780
| Prefabricated Helium Compressor Building - based on gross enclosed area | 1900 | SF | 3 | 5700 | 2 | 3800 | 5 | 9500
[5 empty] | - |  | - |  | -
[5 empty] | 34968 |  | 23312 |  | 58280
16 | ELECTRICAL
POWER EQUIPMENT
| Furnish & install devices w/ conduit & wire | 9756 | SF | 2.4031 | 23444.2534 | 1.602 | 15629.5022 | 4.0051 | 39073.7556
| Furnish & install telecommunication system | 9756 | SF | 1.579 | 15405.2118 | 1.0527 | 10270.1412 | 2.6317 | 25675.353
| Furnish & install card access system | 9756 | SF | 0.74778 | 7295.3417 | 0.49852 | 4863.5611 | 1.2463 | 12158.9028
| Furnish & install fire alarm devices w/ branch wiring | 9756 | SF | 3.9821 | 38849.4652 | 2.6547 | 25899.6434 | 6.6368 | 64749.1086
| Furnish & install Lighting & Branch circuits | 9756 | SF | 2.973 | 29004.2953 | 1.982 | 19336.1969 | 4.955 | 48340.4922
ELECTRICAL POWER
| Power equipment | 9756 | GSF | 2.0408 | 19909.7542 | 1.3605 | 13273.1695 | 3.4013 | 33182.9237
| Motor connections, switches & controllers | 9756 | GSF | 0.3982 | 3884.7925 | 0.26546 | 2589.8617 | 0.66366 | 6474.6542
| Exper eqpt Conn's, Switches, Controllers | 9756 | GSF | 0.75504 | 7366.1702 | 0.50336 | 4910.7802 | 1.2584 | 12276.9504
| Ground, lighting protection, Elect-Stat | 9756 | GSF | 0.62578 | 6105.1139 | 0.41719 | 4070.0759 | 1.043 | 10175.1899
| Motor feeders | 9756 | GSF | 1.2015 | 11722.1267 | 0.80102 | 7814.7511 | 2.0025 | 19536.8778
| Power feeders | 9756 | GSF | 2.4031 | 23444.2534 | 1.602 | 15629.5022 | 4.0051 | 39073.7556
| Exper eqpt feeders | 9756 | GSF | 1.579 | 15405.2118 | 1.0527 | 10270.1412 | 2.6317 | 25675.353
MISCELLANEOUS
| FIRE ALARM PROGRAMMING & TESTING | 1 | LS | 6098.4 | 6098.4 | 4065.6 | 4065.6 | 10164 | 10164
| TEMPORARY LIGHT & POWER | 9756 | SF | 0.45 | 4390.2 | 0.3 | 2926.8 | 0.75 | 7317
| PENETRATION & FIRE STOPPING | 9756 | SF | 0.3 | 2926.8 | 0.2 | 1951.2 | 0.5 | 4878
| GROUNDING SYSTEM | 1 | LS | 7078.5 | 7078.5 | 4719 | 4719 | 11797.5 | 11797.5
[5 empty] | - |  | - |  | -
[5 empty] | 222329.8901 |  | 148219.9267 |  | 370549.8168
[5 empty] | 1300486.7068 |  | 860624.4712 |  | 2161111.178
[7 empty] | 0 |  | 2161111.178

## TRADE - OPERATIONS CENTER
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
OPERATIONS CENTER
TOTAL
| DESCRIPTION |  | AMOUNT
2 | BUILDING EARTHWORK |  | 44450
3 | CONCRETE |  | 328120.6667
4 | MASONRY |  | None
5 | METALS |  | 808640.5
6 | WOOD AND PLASTICS |  | 106012.5
7 | THERMAL AND MOISTURE PROTECTION |  | 170425
8 | DOORS AND WINDOWS / CURTAINWALL |  | 944500
9 | FINISHES |  | 479753
10 | SPECIALTIES |  | 230955
11 | EQUIPMENT |  | 46900
12 | FURNISHINGS |  | None
13 | SPECIAL CONSTRUCTION |  | None
14 | CONVEYING SYSTEMS |  | 260000
15.1 | HVAC |  | 377780
15.2 | PLUMBING |  | 87180
15.3 | FIRE PROTECTION |  | 72650
16 | ELECTRICAL |  | 550324.251
-
| SUB TOTAL |  | 4507690.9177
| GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 676153.6376
-
| SUB TOTAL |  | 5183844.5553
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 5183844.5553
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 5183844.5553 | 5183844.5553
| GROSS ENCLOSED AREA - SF |  | 14530
| COST PER GSF |  | 356.7684
* SEE MAIN SUMMARY SHEET

## EST - OPERATIONS CENTER
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
OPERATIONS CENTER - CSI TRADE ESTIMATE
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
2 | SITEWORK
| DEMOLITION | [6 empty] | See separate site estimate
| EROSION AND SEDIMENT CONTROL | [6 empty] | See separate site estimate
| TREE PROTECTION | [6 empty] | See separate site estimate
| SITE UTILITIES | [6 empty] | See separate site estimate
| SITE IMPROVEMENTS | [6 empty] | See separate site estimate
| LANDSCAPING | [6 empty] | See separate site estimate
BUILDING EARTHWORK
| Building mass cut excavation and disposal on site | 600 | CY | 5.4 | 3240 | 3.6 | 2160 | 9 | 5400
| Building isolated cut excavation and disposal on site | 750 | CY | 5.4 | 4050 | 3.6 | 2700 | 9 | 6750
| Backfill from excavated material | 700 | CY | 6 | 4200 | 4 | 2800 | 10 | 7000
| Disposal on site | 650 | CY | 5.4 | 3510 | 3.6 | 2340 | 9 | 5850
| Crushed stone base at concrete slab on grade | 270 | CY | 21 | 5670 | 14 | 3780 | 35 | 9450
| Pumping / dewatering during construction | [7 empty] | Not included
| Misc earthwork, mechanical trenching, earth ramps, hand trim etc. | 1 | LS | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
[5 empty] | - |  | - |  | -
[5 empty] | 26670 |  | 17780 |  | 44450
3 | CONCRETE
FOUNDATION CONCRETE
| Concrete column footings and piers - include all formwork and reinforcing | 90 | CY | 315 | 28350 | 210 | 18900 | 525 | 47250
| Concrete slab on grade. Include wwm and vapor barrier. 6" thick | 7308 | SF | 4.8 | 35078.4 | 3.2 | 23385.6 | 8 | 58464
| Concrete wall footings and grade beams at building perimeter | 191.5556 | CY | 315 | 60340 | 210 | 40226.6667 | 525 | 100566.6667
| Concrete elevator pit slabs and walls | 2 | EA | 12000 | 24000 | 8000 | 16000 | 20000 | 40000
| Misc foundation concrete | 1 | LS | 9000 | 9000 | 6000 | 6000 | 15000 | 15000
SUPERSTRUCTURE CONCRETE
| Concrete fill on metal deck at second floor | 8640 | SF | 3.6 | 31104 | 2.4 | 20736 | 6 | 51840
| Misc concrete equipment pads and curbs | 1 | LS | 9000 | 9000 | 6000 | 6000 | 15000 | 15000
[5 empty] | - |  | - |  | -
[5 empty] | 196872.4 |  | 131248.2667 |  | 328120.6667
4 | MASONRY | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
5 | METALS
STRUCTURAL STEEL
| Structural steel framing including steel beams, columns, baseplates and windbracing. Allow 15# / SF. No structural drawings available | 118.05 | TON | 1980 | 233739 | 1320 | 155826 | 3300 | 389565
| Extra cost for steel truss at second floor over Link Bldg space | 32.25 | TON | 2280 | 73530 | 1520 | 49020 | 3800 | 122550
| Shear studs - allow 1 per 10 SF | 1575 | EA | 2.1 | 3307.5 | 1.4 | 2205 | 3.5 | 5512.5
| Anchor bolts at column base plates | 100 | EA | 60 | 6000 | 40 | 4000 | 100 | 10000
| Grout at steel baseplates | 25 | EA | 90 | 2250 | 60 | 1500 | 150 | 3750
METAL DECK
| 1 1/2" Deep 18 Gauge Type B roof deck - no concrete fill - at main roof, set back roofs and penthouse roof | 8700 | SF | 1.5 | 13050 | 1 | 8700 | 2.5 | 21750
| 3" Deep 18 Gauge - Lok - metal deck at second floor | 8640 | SF | 2.1 | 18144 | 1.4 | 12096 | 3.5 | 30240
MISC IRONWORK
| Railing at second floor terrace | 46 | LF | 90 | 4140 | 60 | 2760 | 150 | 6900
| Railing at second floor lobby overlook | 24 | LF | 90 | 2160 | 60 | 1440 | 150 | 3600
| Painted pipe handrails at fire stairs | 380 | LF | 36 | 13680 | 24 | 9120 | 60 | 22800
| General misc ironwork | 14530 | SF | 1.5 | 21795 | 1 | 14530 | 2.5 | 36325
EXTERIOR METAL PANEL WALLS
| Exterior metal panel sandwich wall system with liner including all supports | 4864 | SF | 19.2 | 93388.8 | 12.8 | 62259.2 | 32 | 155648
[5 empty] | - |  | - |  | -
[5 empty] | 485184.3 |  | 323456.2 |  | 808640.5
6 | WOOD AND PLASTICS
CARPENTRY
| Install SC Wood &HM doors, frames and finish hardware LABOR COST ONLY | 33 | LEAF | 150 | 4950 | 0 | 0 | 150 | 4950
| Wood blocking at roof parapet walls | 410 | LF | 15 | 6150 | 10 | 4100 | 25 | 10250
| Misc wood blocking, protection and scaffolding at Operations Building | 14530 | SF | 0.75 | 10897.5 | 0.5 | 7265 | 1.25 | 18162.5
MILLWORK
| Interior millwork allowance | 14530 | SF | 3 | 43590 | 2 | 29060 | 5 | 72650
[5 empty] | - |  | - |  | -
[5 empty] | 65587.5 |  | 40425 |  | 106012.5
7 | THERMAL & MOISTURE PROTECTION
ROOFING AND FLASHING
| Flat membrane roofing system including rigid insulation | 8700 | SF | 7.2 | 62640 | 4.8 | 41760 | 12 | 104400
| Metal cap and base flashing at main roof parapet walls | 410 | LF | 21 | 8610 | 14 | 5740 | 35 | 14350
| Metal coping at main roof parapet walls | 410 | LF | 24 | 9840 | 16 | 6560 | 40 | 16400
| Base flashing at roof / wall intersections, and equipment curbs | 131 | LF | 15 | 1965 | 10 | 1310 | 25 | 3275
| Misc flashing at rooftop equipment curbs, thru roof vents and roof drains | 1 | LS | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
FIRE PROOFING
| Spray on fireproofing as required between the Ring Building and the interior ring side of the Ops Center | 1 | LS | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
| Fire stops at all openings in fire rated walls and slabs | 1 | LS | 7200 | 7200 | 4800 | 4800 | 12000 | 12000
INSULATION
| Misc insulation ( all wall insulation with GB ) | [7 empty] | With Exterior wall systems
CAULKING
| Include all caulking and sealants with exterior wall systems | [7 empty] | With Exterior wall systems
[5 empty] | - |  | - |  | -
[5 empty] | 102255 |  | 68170 |  | 170425
8 | DOORS AND WINDOWS / CURTAINWALL
DOORS, FRAMES AND FINISH HARDWARE
Furnish HM Exterior doors and frames
| HM doors, frames and finish hardware | 2 | EA | 1000 | 2000 | 0 | 0 | 1000 | 2000
| HM doors, frames and finish hardware | 1 | PR | 2000 | 2000 | 0 | 0 | 2000 | 2000
Furnish Solid core wood & HM interior doors and frames
| SC Wood &HM doors, frames and finish hardware | 15 | EA | 900 | 13500 | 0 | 0 | 900 | 13500
| SC Wood &HM doors, frames and finish hardware | 7 | PR | 1800 | 12600 | 0 | 0 | 1800 | 12600
| Extra cost for vision lites and frames at HM doors | 1 | LS | 10000 | 10000 | 0 | 0 | 10000 | 10000
| Exterior glass doors and finish hardware at second floor terrace | 2 | PR | 2520 | 5040 | 1680 | 3360 | 4200 | 8400
| Glass Vestibule entry doors, frames and finish hardware | 4 | PR | 6000 | 24000 | 4000 | 16000 | 10000 | 40000
| Furnish and install painted metal access doors and frames for MEP trades | 1 | LS | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
INTERIOR GLAZING
| Assume interior glass wall at second floor viewing gallery bridge | 1440 | SF | 30 | 43200 | 20 | 28800 | 50 | 72000
| Interior glass wall at first floor vestibule | 240 | SF | 30 | 7200 | 20 | 4800 | 50 | 12000
| Misc interior glazing and mirrors | 1 | LS | 9000 | 9000 | 6000 | 6000 | 15000 | 15000
WINDOWS
| Exterior windows and frames | [7 empty] | None
CURTAIN WALL
| Exterior storefront glass wall system at first floor lobby entry | 1350 | SF | 66 | 89100 | 44 | 59400 | 110 | 148500
| Exterior insulated curtain wall system including all supports | 7100 | SF | 51 | 362100 | 34 | 241400 | 85 | 603500
[5 empty] | - |  | - |  | -
[5 empty] | 582740 |  | 361760 |  | 944500
9 | FINISHES
INTERIOR WALLS
| Fire rated gypsum board walls | 7300 | SF | 4.8 | 35040 | 3.2 | 23360 | 8 | 58400
| Gypsum board shaft walls | 4320 | SF | 6 | 25920 | 4 | 17280 | 10 | 43200
| Open office walls at third floor | [7 empty] | None
| Gypsum board chase walls - one side | 1080 | SF | 3.6 | 3888 | 2.4 | 2592 | 6 | 6480
| GB furr at inside face of exterior wall | 6200 | SF | 2.4 | 14880 | 1.6 | 9920 | 4 | 24800
| GB furr at steel columns | 2600 | SF | 2.4 | 6240 | 1.6 | 4160 | 4 | 10400
FLOOR FINISHES
| Main entrance lobby floor | 2284 | SF | 9 | 20556 | 6 | 13704 | 15 | 34260
| Concrete sealer | 2100 | SF | 0.6 | 1260 | 0.4 | 840 | 1 | 2100
| Ceramic tile floors | 1100 | SF | 6 | 6600 | 6 | 6600 | 12 | 13200
| Seamless Sheet Linoleum Flooring | 4300 | SF | 6 | 25800 | 4 | 17200 | 10 | 43000
| Carpeting | 2944 | SF | 2.7 | 7948.8 | 1.8 | 5299.2 | 4.5 | 13248
| Rubber Stair Treads | [7 empty] | With stairs
| Entry mat with aluminum frame at vestibule | 175 | SF | 21 | 3675 | 14 | 2450 | 35 | 6125
BASE
| Ceramic tile base | 180 | LF | 6 | 1080 | 4 | 720 | 10 | 1800
| Rubber 4" wall base | 1600 | LF | 1.2 | 1920 | 1.8 | 2880 | 3 | 4800
| Marble saddles at tile floors | 6 | EA | 30 | 180 | 20 | 120 | 50 | 300
WALL FINISHES
| Ceramic tile walls | 1440 | SF | 6 | 8640 | 4 | 5760 | 10 | 14400
| Vinyl wall covering at conference rooms | 1200 | SF | 1.8 | 2160 | 1.2 | 1440 | 3 | 3600
| Prime and paint gypsum board walls | 19000 | SF | 0.6 | 11400 | 0.4 | 7600 | 1 | 19000
| Wall finishes at main entrance lobby | 3240 | SF | 7.2 | 23328 | 4.8 | 15552 | 12 | 38880
CEILINGS
| Main entrance lobby ceiling | 2284 | SF | 12 | 27408 | 8 | 18272 | 20 | 45680
| Acoustical Panel Ceilings | 10500 | SF | 3.6 | 37800 | 2.4 | 25200 | 6 | 63000
| Paint exposed ceilings | 1500 | SF | 0.75 | 1125 | 0.5 | 750 | 1.25 | 1875
MISC
| Paint SC Wood & HM doors and frames | 33 | LEAF | 39 | 1287 | 26 | 858 | 65 | 2145
| Misc interior painting | 14530 | SF | 1.2 | 17436 | 0.8 | 11624 | 2 | 29060
[5 empty] | - |  | - |  | -
[5 empty] | 285571.8 |  | 194181.2 |  | 479753
10 | SPECIALTIES
| Raised access flooring at computer room at first floor and control room at second floor. | 2523 | SF | 9 | 22707 | 6 | 15138 | 15 | 37845
| Provide roof screens surrounding approx 1/3 of roof at rooftop units | 2250 | SF | 24 | 54000 | 16 | 36000 | 40 | 90000
| Door signs | 39 | EA | 90 | 3510 | 60 | 2340 | 150 | 5850
| Misc signage | 1 | LS | 9000 | 9000 | 6000 | 6000 | 15000 | 15000
| Building logo | 1 | LS | 15000 | 15000 | 10000 | 10000 | 25000 | 25000
Toilet partitions and urinal screens
| Regular | [7 empty] | None
| Handicap | [7 empty] | None
| Urinal screens | [7 empty] | None
Toilet accessories
| At Unisex Toilet | 2 | RM | 900 | 1800 | 600 | 1200 | 1500 | 3000
| At Men's Public Toilets | 1 | RM | 900 | 900 | 600 | 600 | 1500 | 1500
| At Womens Toilets | 1 | RM | 1200 | 1200 | 800 | 800 | 2000 | 2000
| At Janitors Closets | 1 | RM | 300 | 300 | 200 | 200 | 500 | 500
| Fire extinguishers and cabinets - not shown | 10 | EA | 70 | 700 | 200 | 2000 | 270 | 2700
| Metal Lockers - not shown | 30 | EA | 150 | 4500 | 100 | 3000 | 250 | 7500
| Wood benches - not shown | 4 | EA | 300 | 1200 | 200 | 800 | 500 | 2000
| Window blinds | 2000 | SF | 2.7 | 5400 | 1.8 | 3600 | 4.5 | 9000
| Misc specialties | 14530 | SF | 1.2 | 17436 | 0.8 | 11624 | 2 | 29060
[5 empty] | - |  | - |  | -
[5 empty] | 137653 |  | 93302 |  | 230955
11 | EQUIPMENT
| Refrigerator at lunch break rooms | 1 | EA | 900 | 900 | 600 | 600 | 1500 | 1500
| Microwave at lunch break rooms | 1 | EA | 240 | 240 | 160 | 160 | 400 | 400
| Grille kitchen at first floor lobby | 300 | SF | 90 | 27000 | 60 | 18000 | 150 | 45000
[5 empty] | - |  | - |  | -
[5 empty] | 28140 |  | 18760 |  | 46900
12 | FURNISHINGS | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
13 | SPECIAL CONSTRUCTION | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
14 | CONVEYING SYSTEMS
| Metal pan fire stairs including all riser / tread and platform assemblies, and stringers. First to second floor | 2 | FLT | 9000 | 18000 | 6000 | 12000 | 15000 | 30000
| Passenger elevator - 2 stop | 1 | EA | 57000 | 57000 | 38000 | 38000 | 95000 | 95000
| Freight elevator - 2 stop | 1 | EA | 81000 | 81000 | 54000 | 54000 | 135000 | 135000
[5 empty] | - |  | - |  | -
[5 empty] | 156000 |  | 104000 |  | 260000
15.1 | HVAC
| HVAC based on gross enclosed area | 14530 | SF | 15.6 | 226668 | 10.4 | 151112 | 26 | 377780
[5 empty] | - |  | - |  | -
[5 empty] | 226668 |  | 151112 |  | 377780
15.2 | PLUMBING
| Plumbing based on gross enclosed area | 14530 | SF | 3.6 | 52308 | 2.4 | 34872 | 6 | 87180
[5 empty] | - |  | - |  | -
[5 empty] | 52308 |  | 34872 |  | 87180
15.3 | FIRE PROTECTION
| Sprinkler heads (wet system, say 150sf per spr. head) incl. branch piping from main from Service Bdg | 14530 | SF | 3 | 43590 | 2 | 29060 | 5 | 72650
[5 empty] | - |  | - |  | -
[5 empty] | 43590 |  | 29060 |  | 72650
16 | ELECTRICAL
POWER EQUIPMENT
| Furnish & install devices w/ conduit & wire | 14530 | SF | 2.4031 | 34916.5344 | 1.602 | 23277.6896 | 4.0051 | 58194.224
| Furnish & install telecommunication system | 14530 | SF | 1.579 | 22943.4876 | 1.0527 | 15295.6584 | 2.6317 | 38239.146
| Furnish & install card access system | 14530 | SF | 0.74776 | 10864.953 | 0.49851 | 7243.302 | 1.2463 | 18108.255
| Furnish & install fire alarm devices w/ branch wiring | 14530 | SF | 3.9821 | 57860.022 | 2.6547 | 38573.348 | 6.6368 | 96433.37
| Furnish & install Lighting & Branch circuits | 14530 | SF | 2.973 | 43197.2904 | 1.982 | 28798.1936 | 4.955 | 71995.484
ELECTRICAL POWER
| Power equipment | 14530 | GSF | 2.0408 | 29652.8892 | 1.3605 | 19768.5928 | 3.4013 | 49421.482
| Motor connections, switches & controllers | 14530 | GSF | 0.39822 | 5786.1474 | 0.26548 | 3857.4316 | 0.6637 | 9643.579
| Exper eqpt Conn's, Switches, Controllers | 14530 | GSF | 0.75502 | 10970.4408 | 0.50335 | 7313.6272 | 1.2584 | 18284.068
| Ground, lighting protection, Elect-Stat | 14530 | GSF | 0.6258 | 9092.8596 | 0.4172 | 6061.9064 | 1.043 | 15154.766
| Motor feeders | 14530 | GSF | 1.2015 | 17457.9042 | 0.80101 | 11638.6028 | 2.0025 | 29096.507
| Power feeders | 14530 | GSF | 2.4031 | 34916.5344 | 1.602 | 23277.6896 | 4.0051 | 58194.224
| Exper eqpt feeders | 14530 | GSF | 1.579 | 22943.4876 | 1.0527 | 15295.6584 | 2.6317 | 38239.146
MISCELLANEOUS
| FIRE ALARM PROGRAMMING & TESTING | 1 | LS | 8167.5 | 8167.5 | 5445 | 5445 | 13612.5 | 13612.5
| TEMPORARY LIGHT & POWER | 14530 | SF | 0.45 | 6538.5 | 0.3 | 4359 | 0.75 | 10897.5
| PENETRATION & FIRE STOPPING | 14530 | SF | 0.3 | 4359 | 0.2 | 2906 | 0.5 | 7265
| GROUNDING SYSTEM | 1 | LS | 10527 | 10527 | 7018 | 7018 | 17545 | 17545
[5 empty] | - |  | - |  | -
[5 empty] | 330000 |  | 220324 |  | 550324.251
[5 empty] | 2719337.2753 |  | 1788353.5169 |  | 4507690.9177
[7 empty] | 0.1255 |  | 4507690.9177

## TRADE - BOOSTER RING & LINAC
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
BOOSTER RING AND LINAC
TOTAL
| DESCRIPTION |  | AMOUNT
2 | BUILDING EARTHWORK |  | 183398.1481
3 | CONCRETE |  | 2331300.3704
4 | MASONRY |  | 0
5 | METALS |  | 636533
6 | WOOD AND PLASTICS |  | 43150
7 | THERMAL AND MOISTURE PROTECTION |  | 329850
8 | DOORS AND WINDOWS / CURTAINWALL |  | 50900
9 | FINISHES |  | 75295
10 | SPECIALTIES |  | 375000
11 | EQUIPMENT |  | None
12 | FURNISHINGS |  | None
13 | SPECIAL CONSTRUCTION |  | None
14 | CONVEYING SYSTEMS |  | 8000
15.1 | HVAC |  | 650800
15.2 | PLUMBING |  | 227000
15.3 | FIRE PROTECTION |  | 204300
16 | ELECTRICAL |  | 882301.4433
-
| SUB TOTAL |  | 5997827.9619
| GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 899674.1943
-
| SUB TOTAL |  | 6897502.1561
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 6897502.1561
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 6897502.1561 | 6897502.1561
| GROSS ENCLOSED AREA - SF |  | 22700
| COST PER GSF |  | 303.8547
* SEE MAIN SUMMARY SHEET

## EST - BOOSTER RING & LINAC
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
BOOSTER RING AND LINAC - CSI TRADE ESTIMATE
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
2 | SITEWORK
| DEMOLITION | [6 empty] | See separate site estimate
| EROSION AND SEDIMENT CONTROL | [6 empty] | See separate site estimate
| TREE PROTECTION | [6 empty] | See separate site estimate
| SITE UTILITIES | [6 empty] | See separate site estimate
| SITE IMPROVEMENTS | [6 empty] | See separate site estimate
| LANDSCAPING | [6 empty] | See separate site estimate
BUILDING EARTHWORK
| Building mass cut excavation and disposal off site | 2200 | CY | 5.4 | 11880 | 3.6 | 7920 | 9 | 19800
| Building isolated cut excavation and disposal off site | 3800 | CY | 5.4 | 20520 | 3.6 | 13680 | 9 | 34200
| Backfill from excavated material | 2000 | CY | 6 | 12000 | 4 | 8000 | 10 | 20000
| Use excess mass and isolated cut material to create earth berm around Booster Ring Tunnel and dispose unused fill off site. | 4000 | CY | 5.4 | 21600 | 3.6 | 14400 | 9 | 36000
| Crushed stone base at 8" thick concrete slab on grade | 418.5185 | CY | 21 | 8788.8889 | 14 | 5859.2593 | 35 | 14648.1481
| Pumping / dewatering during construction | [7 empty] | Not included
| Provide continuous porous drain and wrapped around aggregate with filter fabric at perimeter of booster tunnel | 1350 | LF | 15 | 20250 | 10 | 13500 | 25 | 33750
| Misc earthwork, mechanical trenching, earth ramps, hand trim etc. | 1 | LS | 15000 | 15000 | 10000 | 10000 | 25000 | 25000
[5 empty] | - |  | - |  | -
[5 empty] | 110038.8889 |  | 73359.2593 |  | 183398.1481
3 | CONCRETE
FOUNDATION CONCRETE
| Concrete column footings and piers - include all formwork and reinforcing. | 90 | CY | 315 | 28350 | 210 | 18900 | 525 | 47250
| Concrete slab on grade at Booster Service Building and Klystom Gallery. Include wwm, formwork and vapor barrier. 8" thick - 11,300 SF | 281 | CY | 270 | 75870 | 180 | 50580 | 450 | 126450
| 1'-8" Thick reinforced concrete slab on grade at booster ring tunnel, labyrinths and Linac. Include all formwork. 14,570 SF | 901.1815 | CY | 330 | 297389.8889 | 220 | 198259.9259 | 550 | 495649.8148
| Form out for continuous trench drain frame and cover set in concrete slab on grade | 680 | LF | 30 | 20400 | 20 | 13600 | 50 | 34000
| Concrete wall footings and grade beams at Booster Service Building and Klystrom Gallery | 411.1111 | CY | 315 | 129500 | 210 | 86333.3333 | 525 | 215833.3333
Concrete walls. Include reinforcing and formwork at booster ring tunnel, labyrinths and Linac.
| 1'-8" Thick - 800 LF x 9'-0" HT | 445.3333 | CY | 330 | 146960 | 220 | 97973.3333 | 550 | 244933.3333
| 2'-8" Thick - 1050 LF x 9'-0" HT | 934.5 | CY | 330 | 308385 | 220 | 205590 | 550 | 513975
| Allow additional cost for two 10' x 10' knock out panels for entrance into booster tunnel | 200 | SF | 60 | 12000 | 40 | 8000 | 100 | 20000
| 1'-8" Thick concrete roof arch over booster ring tunnel, labyrinths and Linac Include all reinforcing, shoring, bottom and side forms. 14,570 SF | 901.1815 | CY | 360 | 324425.3333 | 240 | 216283.5556 | 600 | 540708.8889
| Extra cost for 2" thick isolation joint between booster ring tunnel arch and service bldg | 350 | LF | 30 | 10500 | 20 | 7000 | 50 | 17500
| Misc foundation concrete | 1 | LS | 15000 | 15000 | 10000 | 10000 | 25000 | 25000
SUPERSTRUCTURE CONCRETE
| Concrete fill on metal deck at Booster Service Building roof deck and Klyston Gallery roof deck | [7 empty] | None
| Additional work to connect booster ring tunnel to Linac | 1 | LS | 30000 | 30000 | 20000 | 20000 | 50000 | 50000
[5 empty] | - |  | - |  | -
[5 empty] | 1398780.2222 |  | 932520.1481 |  | 2331300.3704
4 | MASONRY
| EXTERIOR | [7 empty] | None
INTERIOR
| Interior cmu walls | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | 0
5 | METALS
STRUCTURAL STEEL
| Structural steel framing including steel beams, columns, baseplates at Booster Service Building and Klystron Gallery. Allow 15# / SF - 11,300 SF | 84.75 | TON | 1980 | 167805 | 1320 | 111870 | 3300 | 279675
| Anchor bolts at column base plates | 120 | EA | 60 | 7200 | 40 | 4800 | 100 | 12000
| Grout at steel baseplates | 30 | EA | 90 | 2700 | 60 | 1800 | 150 | 4500
METAL DECK
| 1 1/2" Deep 20 Gauge Type B roof deck - no concrete fill - at Booster Service Building roof and Klystron Gallery roof | 11300 | SF | 1.5 | 16950 | 1 | 11300 | 2.5 | 28250
MISC IRONWORK
| General misc ironwork | 22700 | SF | 0.6 | 13620 | 0.4 | 9080 | 1 | 22700
EXTERIOR METAL PANEL WALLS
| Exterior insulated metal panel wall system including all supports at Booster Service Building and Klyston Gallery. | 9044 | SF | 19.2 | 173644.8 | 12.8 | 115763.2 | 32 | 289408
[5 empty] | - |  | - |  | -
[5 empty] | 381919.8 |  | 254613.2 |  | 636533
6 | WOOD AND PLASTICS
CARPENTRY
| Install HM doors, frames and finish hardware LABOR COST ONLY | 28 | LEAF | 150 | 4200 | 0 | 0 | 150 | 4200
| Wood blocking at gravel stop at roof edge | 600 | LF | 12 | 7200 | 8 | 4800 | 20 | 12000
| Wood blocking at base flashing at intersection of roof and exterior walls | 170 | LF | 15 | 2550 | 10 | 1700 | 25 | 4250
| Misc wood blocking, protection and scaffolding | 22700 | SF | 0.6 | 13620 | 0.4 | 9080 | 1 | 22700
MILLWORK
| Interior millwork allowance | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 27570 |  | 15580 |  | 43150
7 | THERMAL & MOISTURE PROTECTION
ROOFING AND FLASHING
| Flat membrane roofing system including rigid insulation | 11300 | SF | 7.2 | 81360 | 4.8 | 54240 | 12 | 135600
| Metal gravel stop at roof edge | 600 | LF | 15 | 9000 | 10 | 6000 | 25 | 15000
| Base flashing at roof / wall intersections, and equipment curbs | 170 | LF | 15 | 2550 | 10 | 1700 | 25 | 4250
| Misc flashing at rooftop equipment curbs, thru roof vents and roof drains | 1 | LS | 4500 | 4500 | 3000 | 3000 | 7500 | 7500
FIRE PROOFING
| Spray on fireproofing @ beams and columns | [7 empty] | Not Required
| Fire stops at all openings in fire rated walls and slabs | 1 | LS | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
INSULATION
| Misc insulation ( all wall insulation with GB ) | [7 empty] | With Exterior wall systems
CAULKING
| Include all caulking and sealants with exterior wall systems | [7 empty] | With Exterior wall systems
WATERPROOFING
| Membrane waterproofing at concrete walls and concrete tunnel roof behind earth berm. | 31500 | SF | 3 | 94500 | 2 | 63000 | 5 | 157500
[5 empty] | - |  | - |  | -
[5 empty] | 197910 |  | 131940 |  | 329850
8 | DOORS AND WINDOWS / CURTAINWALL
DOORS, FRAMES AND FINISH HARDWARE
Furnish HM Exterior doors and frames
| HM doors, frames and finish hardware | 6 | EA | 1000 | 6000 | 0 | 0 | 1000 | 6000
Furnish HM interior doors and frames
| HM doors, frames and finish hardware | 16 | EA | 900 | 14400 | 0 | 0 | 900 | 14400
| HM doors, frames and finish hardware | 6 | PR | 1800 | 10800 | 0 | 0 | 1800 | 10800
| Extra cost for vision lites and frames at HM doors | 1 | LS | 7500 | 7500 | 0 | 0 | 7500 | 7500
| Furnish and install painted metal access doors and frames for MEP trades | 1 | LS | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
| Furnish and install exterior motorized overhead doors and frames 12' x 10' x 1 ea | 120 | SF | 36 | 4320 | 24 | 2880 | 60 | 7200
| INTERIOR GLAZING | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 46020 |  | 4880 |  | 50900
9 | FINISHES
INTERIOR WALLS
| Interior fire rated gypsum board walls - say 12' high | 3936 | SF | 4.8 | 18892.8 | 3.2 | 12595.2 | 8 | 31488
FLOOR FINISHES
| Concrete sealer | 22700 | SF | 0.6 | 13620 | 0.4 | 9080 | 1 | 22700
WALL FINISHES
| Prime and paint gypsum board walls | 7872 | SF | 0.6 | 4723.2 | 0.4 | 3148.8 | 1 | 7872
CEILINGS
| Unfinished exposed ceilings | 22700 | SF | [5 empty] | No work
MISC
| Paint HM doors and frames | 29 | LEAF | 39 | 1131 | 26 | 754 | 65 | 1885
| Misc interior painting | 22700 | SF | 0.3 | 6810 | 0.2 | 4540 | 0.5 | 11350
[5 empty] | - |  | - |  | -
[5 empty] | 45177 |  | 30118 |  | 75295
10 | SPECIALTIES
| Misc specialties - fire extinguishers, corner guards, signage etc. | 1 | LS | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
| Exterior metal ventilation louvers and frames | 1 | LS | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
| Additional cost for Booster Ring Service Building adjacent to SB - 1 | 1500 | SF | 144 | 216000 | 96 | 144000 | 240 | 360000
[5 empty] | - |  | - |  | -
[5 empty] | 225000 |  | 150000 |  | 375000
11 | EQUIPMENT | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
12 | FURNISHINGS | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
13 | SPECIAL CONSTRUCTION | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
14 | CONVEYING SYSTEMS
| Metal pan fire stairs including all riser / tread and platform assemblies, and stringers. Provide stair to mezzanine from booster area. | 1 | EA | 4800 | 4800 | 3200 | 3200 | 8000 | 8000
[5 empty] | - |  | - |  | -
[5 empty] | 4800 |  | 3200 |  | 8000
15.1 | HVAC
Booster Service Building and Klystrom Gallery - based on gross enclosed area
| Packaged RTU custom made 2" double wall construction galvanized steel interior liner, S & R fans, cooling and steam preheating coils, filters, humidifier, etc. | 40 | TON | 1000 | 40000 | 3000 | 120000 | 4000 | 160000
|  | 15000 | LB | 4.8 | 72000 | 3.2 | 48000 | 8 | 120000
| Piping | 11268 | SF | 2.4 | 27043.2 | 1.6 | 18028.8 | 4 | 45072
Booster ring tunnel and Linac - based on gross enclosed area
| Packaged RTU custom made 2" double wall construction gabanized steel interior liner, S & R fans, cooling and steam preheating coils, filters, humidifier, etc. | 40 | TON | 1000 | 40000 | 3000 | 120000 | 4000 | 160000
| Galvanized steel ductwork supply and return | 15000 | LB | 4.8 | 72000 | 3.2 | 48000 | 8 | 120000
| Piping | 11432 | SF | 2.4 | 27436.8 | 1.6 | 18291.2 | 4 | 45728
[5 empty] | - |  | - |  | -
[5 empty] | 278480 |  | 372320 |  | 650800
15.2 | PLUMBING
| Booster Servixce Building and Klystrom Gallery - based on gross enclosed area | 22700 | SF | 3 | 68100 | 2 | 45400 | 5 | 113500
| Booster ring tunnel and Linac - based on gross enclosed area | 22700 | SF | 3 | 68100 | 2 | 45400 | 5 | 113500
[5 empty] | - |  | - |  | -
[5 empty] | 136200 |  | 90800 |  | 227000
15.3 | FIRE PROTECTION
| Booster Service Building and Klystrom Gallery - based on gross enclosed area | 22700 | SF | 3 | 68100 | 2 | 45400 | 5 | 113500
| Booster ring tunnel and Linac - based on gross enclosed area | 22700 | SF | 2.4 | 54480 | 1.6 | 36320 | 4 | 90800
[5 empty] | - |  | - |  | -
[5 empty] | 122580 |  | 81720 |  | 204300
16 | ELECTRICAL
POWER EQUIPMENT
| Furnish & install devices w/ conduit & wire | 22700 | SF | 2.4031 | 54549.462 | 1.602 | 36366.308 | 4.0051 | 90915.77
| Furnish & install telecommunication system | 22700 | SF | 1.5791 | 35844.8853 | 1.0527 | 23896.5902 | 2.6318 | 59741.4755
| Furnish & install card access system | 22700 | SF | 0.74778 | 16974.606 | 0.49852 | 11316.404 | 1.2463 | 28291.01
| Furnish & install fire alarm devices w/ branch wiring | 22700 | SF | 3.9821 | 90394.3473 | 2.6548 | 60262.8982 | 6.6369 | 150657.2455
| Furnish & install Lighting & Branch circuits | 22700 | SF | 2.973 | 67486.8693 | 1.982 | 44991.2462 | 4.955 | 112478.1155
ELECTRICAL POWER
| Power equipment | 22700 | GSF | 2.0408 | 46325.572 | 1.3605 | 30883.7147 | 3.4013 | 77209.2867
| Motor connections, switches & controllers | 22700 | GSF | 0.39823 | 9039.795 | 0.26549 | 6026.53 | 0.66371 | 15066.3249
| Exper eqpt Conn's, Switches, Controllers | 22700 | GSF | 0.75504 | 17139.408 | 0.50336 | 11426.272 | 1.2584 | 28565.68
| Ground, lighting protection, Elect-Stat | 22700 | GSF | 0.62583 | 14206.2926 | 0.41722 | 9470.8617 | 1.043 | 23677.1544
| Motor feeders | 22700 | GSF | 1.2015 | 27275.1813 | 0.80103 | 18183.4542 | 2.0026 | 45458.6355
| Power feeders | 22700 | GSF | 2.4031 | 54549.462 | 1.602 | 36366.308 | 4.0051 | 90915.77
| Exper eqpt feeders | 22700 | GSF | 1.5791 | 35844.8853 | 1.0527 | 23896.5902 | 2.6318 | 59741.4755
MISCELLANEOUS
| FIRE ALARM PROGRAMMING & TESTING | 1 | LS | 8167.5 | 8167.5 | 5445 | 5445 | 13612.5 | 13612.5
| TEMPORARY LIGHT & POWER | 22700 | SF | 0.45 | 10215 | 0.3 | 6810 | 0.75 | 17025
| PENETRATION & FIRE STOPPING | 22700 | SF | 0.3 | 6810 | 0.2 | 4540 | 0.5 | 11350
| GROUNDING SYSTEM | 1 | LS | 10527 | 10527 | 7018 | 7018 | 17545 | 17545
| Allowance for utility modifications | 1 | LS | 24030.6 | 24030.6 | 16020.4 | 16020.4 | 40051 | 40051
[5 empty] | - |  | - |  | -
[5 empty] | 529380.866 |  | 352920.5773 |  | 882301.4433
[5 empty] | 3503856.7771 |  | 2493971.1847 |  | 5997827.9619
[7 empty] | 0 |  | 5997827.9619

## TRADE - LAB-OFFICE BLDGS 1 TO 3
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
LAB / OFFICE BUILDINGS - ONE TO THREE
TOTAL
| DESCRIPTION |  | AMOUNT
2 | BUILDING EARTHWORK |  | 233850
3 | CONCRETE |  | 1435420.8333
4 | MASONRY |  | 131328
5 | METALS |  | 2630978.5
6 | WOOD AND PLASTICS |  | 470400
7 | THERMAL AND MOISTURE PROTECTION |  | 1775826
8 | DOORS AND WINDOWS / CURTAINWALL |  | 2331330
9 | FINISHES |  | 2170347.5
10 | SPECIALTIES |  | 564930
11 | EQUIPMENT |  | 64200
12 | FURNISHINGS |  | 615000
13 | SPECIAL CONSTRUCTION |  | None
14 | CONVEYING SYSTEMS |  | 90000
15.1 | HVAC |  | 3798150
15.2 | PLUMBING |  | 927000
15.3 | FIRE PROTECTION |  | 273600
16 | ELECTRICAL |  | 2147156.8481
-
| SUB TOTAL |  | 19659517.6814
| GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 2948927.6522
-
| SUB TOTAL |  | 22608445.3336
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 22608445.3336
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 22608445.3336 | 22608445.3336
| GROSS ENCLOSED AREA - SF |  | 68400
| COST PER GSF |  | 330.5328
* SEE MAIN SUMMARY SHEET

## EST - LAB-OFFICE BLDGS 1 TO 3
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
LAB / OFFICE BUILDINGS - ONE TO THREE - CSI TRADE ESTIMATE
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
2 | SITEWORK
| DEMOLITION | [6 empty] | See separate site estimate
| EROSION AND SEDIMENT CONTROL | [6 empty] | See separate site estimate
| TREE PROTECTION | [6 empty] | See separate site estimate
| SITE UTILITIES | [6 empty] | See separate site estimate
| SITE IMPROVEMENTS | [6 empty] | See separate site estimate
| LANDSCAPING | [6 empty] | See separate site estimate
BUILDING EARTHWORK
| Building mass cut excavation and disposal on site | 2850 | CY | 5.4 | 15390 | 3.6 | 10260 | 9 | 25650
| Building isolated cut excavation and disposal on site | 4200 | CY | 5.4 | 22680 | 3.6 | 15120 | 9 | 37800
| Backfill from excavated material | 2700 | CY | 6 | 16200 | 4 | 10800 | 10 | 27000
| Disposal on site | 4350 | CY | 5.4 | 23490 | 3.6 | 15660 | 9 | 39150
| Crushed stone base at concrete slab on grade | 2550 | CY | 21 | 53550 | 14 | 35700 | 35 | 89250
| Pumping / dewatering during construction | [7 empty] | Not included
| Provide drainage below concrete slab on grade | [7 empty] | Not included
| Misc earthwork, mechanical trenching, earth ramps, hand trim etc. | 3 | BLDG | 3000 | 9000 | 2000 | 6000 | 5000 | 15000
[5 empty] | - |  | - |  | -
[5 empty] | 140310 |  | 93540 |  | 233850
3 | CONCRETE
FOUNDATION CONCRETE
| Concrete column footings and piers - include all formwork and reinforcing. See drawing S-103 | 276 | CY | 315 | 86940 | 210 | 57960 | 525 | 144900
| Concrete slab on grade. Include wwm and vapor barrier. 6" thick | 68400 | SF | 4.8 | 328320 | 3.2 | 218880 | 8 | 547200
| Concrete wall footings and grade beams at building perimeter | 1083.2778 | CY | 315 | 341232.5 | 210 | 227488.3333 | 525 | 568720.8333
| Concrete pad at dumpster | 3 | BLDG | 1200 | 3600 | 800 | 2400 | 2000 | 6000
| Concrete pad at cylinder rack | 3 | BLDG | 3000 | 9000 | 2000 | 6000 | 5000 | 15000
| Misc foundation concrete | 3 | BLDG | 6000 | 18000 | 4000 | 12000 | 10000 | 30000
SUPERSTRUCTURE CONCRETE
| Concrete fill on metal deck at attic space | [7 empty] | None required
| Misc concrete equipment pads and curbs | 3 | BLDG | 6000 | 18000 | 4000 | 12000 | 10000 | 30000
PRECAST CONCRETE
| Architectural exterior precast concrete panel at Lab office Buildings at grade. 8" x 1'-0" high. See wall section 1 - drawing A-309 | 1560 | SF | 36 | 56160 | 24 | 37440 | 60 | 93600
[5 empty] | - |  | - |  | -
[5 empty] | 861252.5 |  | 574168.3333 |  | 1435420.8333
4 | MASONRY | [7 empty] | None
| Cmu walls between ring building and LOB Buildings if required | 10944 | SF | 7.2 | 78796.8 | 4.8 | 52531.2 | 12 | 131328
[5 empty] | - |  | - |  | -
[5 empty] | 78796.8 |  | 52531.2 |  | 131328
5 | METALS
STRUCTURAL STEEL
| Structural steel roof framing including steel beams, columns, baseplates and windbracing. See drawings S-104 and S-105. | 522 | TON | 1980 | 1033560 | 1320 | 689040 | 3300 | 1722600
| Shear studs at mezzanine | 1566 | EA | 2.1 | 3288.6 | 1.4 | 2192.4 | 3.5 | 5481
| Moment connections | [7 empty] | None required
| Anchor bolts at column base plates | 540 | EA | 60 | 32400 | 40 | 21600 | 100 | 54000
| Grout at steel baseplates | 135 | EA | 90 | 12150 | 60 | 8100 | 150 | 20250
METAL DECK
| 1 1/2" Deep 18 Gauge Type B roof deck - no concrete fill - at main roof sloping roof | 74730 | SF | 1.65 | 123304.5 | 1.1 | 82203 | 2.75 | 205507.5
| 1 1/2" Deep 18 Gauge Type B roof deck - no concrete fill - at flat low roof | 9198 | SF | 1.5 | 13797 | 1 | 9198 | 2.5 | 22995
| 3" Deep 18 Gauge - Lok - metal deck at attic space | 14850 | SF | 2.1 | 31185 | 1.4 | 20790 | 3.5 | 51975
MISC IRONWORK
| General misc ironwork | 68400 | SF | 1.2 | 82080 | 0.8 | 54720 | 2 | 136800
EXTERIOR METAL PANEL WALLS
| Exterior flat metal panel sandwich wall system with liner including all supports. See wall section 1 drawing A-309. | 10200 | SF | 19.2 | 195840 | 12.8 | 130560 | 32 | 326400
| Exterior preformed metal panel sandwich wall system with liner including all supports | 1660 | SF | 19.2 | 31872 | 12.8 | 21248 | 32 | 53120
| Exterior metal panel fascia including all supports | 910 | SF | 21 | 19110 | 14 | 12740 | 35 | 31850
[5 empty] | - |  | - |  | -
[5 empty] | 1578587.1 |  | 1052391.4 |  | 2630978.5
6 | WOOD AND PLASTICS
CARPENTRY
| Install SC Wood &HM doors, frames and finish hardware LABOR COST ONLY | 264 | LEAF | 150 | 39600 | 0 | 0 | 150 | 39600
| Wood blocking at gravel stop at edge of low roof | 1020 | LF | 12 | 12240 | 8 | 8160 | 20 | 20400
| Misc wood blocking, protection and scaffolding at Lab Building | 68400 | SF | 0.6 | 41040 | 0.4 | 27360 | 1 | 68400
MILLWORK
| Interior millwork allowance | 68400 | SF | 3 | 205200 | 2 | 136800 | 5 | 342000
[5 empty] | - |  | - |  | -
[5 empty] | 298080 |  | 172320 |  | 470400
7 | THERMAL & MOISTURE PROTECTION
ROOFING AND FLASHING
| Sloping standing seam roofing system including rigid insulation and exterior grade gypsum board sheathing ( on metal roof deck). See drawing A-303 | 74730 | SF | 9 | 672570 | 6 | 448380 | 15 | 1120950
| Flat membrane roofing system including rigid insulation at low flat roof. See drawing A-309 | 9198 | SF | 7.2 | 66225.6 | 4.8 | 44150.4 | 12 | 110376
| Metal soffit and fascia at sloping standing seam roof | 9600 | SF | 12 | 115200 | 8 | 76800 | 20 | 192000
| Metal gutter assembly at sloping standing seam roof | 960 | LF | 45 | 43200 | 30 | 28800 | 75 | 72000
| Assume gravel stop at edge of flat roofs | 1020 | LF | 15 | 15300 | 10 | 10200 | 25 | 25500
| Base flashing at roof / clearstory glass intersection | 960 | LF | 15 | 14400 | 10 | 9600 | 25 | 24000
| Misc flashing at rooftop equipment curbs, thru roof vents and roof drains | 3 | BLDG | 6000 | 18000 | 4000 | 12000 | 10000 | 30000
FIRE PROOFING
| Spray on fireproofing @ beams and columns | 68400 | SF | 1.5 | 102600 | 1 | 68400 | 2.5 | 171000
| Fire stops at all openings in fire rated walls and slabs | 3 | BLDG | 6000 | 18000 | 4000 | 12000 | 10000 | 30000
INSULATION
| Misc insulation ( all wall insulation with GB ) | [7 empty] | With Exterior wall systems
CAULKING
| Include all caulking and sealants with exterior wall systems | [7 empty] | With Exterior wall systems
[5 empty] | - |  | - |  | -
[5 empty] | 1065495.6 |  | 710330.4 |  | 1775826
8 | DOORS AND WINDOWS / CURTAINWALL
DOORS, FRAMES AND FINISH HARDWARE
Furnish HM Exterior doors and frames
| HM doors, frames and finish hardware | 3 | EA | 1000 | 3000 | 0 | 0 | 1000 | 3000
Furnish Solid core wood & HM interior doors and frames
| SC Wood &HM doors, frames and finish hardware | 201 | EA | 900 | 180900 | 0 | 0 | 900 | 180900
| SC Wood &HM doors, frames and finish hardware | 30 | PR | 1800 | 54000 | 0 | 0 | 1800 | 54000
| Extra cost for vision lites and frames at HM doors | 3 | BLDG | 10000 | 30000 | 0 | 0 | 10000 | 30000
| Interior glass doors and finish hardware at Conference rooms. 2 pair per building | 6 | PR | 2520 | 15120 | 1680 | 10080 | 4200 | 25200
| Glass Vestibule entry doors, frames and finish hardware | 12 | PR | 6000 | 72000 | 4000 | 48000 | 10000 | 120000
| Furnish and install painted metal access doors and frames for MEP trades | 3 | BLDG | 3000 | 9000 | 2000 | 6000 | 5000 | 15000
INTERIOR GLAZING
| Assume interior glass walls at Conference rooms | 864 | SF | 30 | 25920 | 20 | 17280 | 50 | 43200
| Misc interior glazing and mirrors | 3 | BLDG | 9000 | 27000 | 6000 | 18000 | 15000 | 45000
WINDOWS
| Exterior windows and frames | [7 empty] | None
CURTAIN WALL
| Exterior storefront glass wall system at first floor lobby entry | 1500 | SF | 66 | 99000 | 44 | 66000 | 110 | 165000
| Exterior insulated curtain wall system including all supports | 13260 | SF | 51 | 676260 | 34 | 450840 | 85 | 1127100
| Exterior insulated clearstory glass wall system including all supports. 384' x 4' ht x 3 bldg | 4608 | SF | 51 | 235008 | 34 | 156672 | 85 | 391680
| Extra cost for horizontal window louvers at first floor curtain walls | 1470 | LF | 30 | 44100 | 20 | 29400 | 50 | 73500
| Extra cost for horizontal window louvers at second floor clear story | 1155 | LF | 30 | 34650 | 20 | 23100 | 50 | 57750
[5 empty] | - |  | - |  | -
[5 empty] | 1505958 |  | 825372 |  | 2331330
9 | FINISHES
INTERIOR WALLS
| Fire rated gypsum board walls | 91125 | SF | 4.5 | 410062.5 | 3 | 273375 | 7.5 | 683437.5
| Gypsum board shaft walls | 4200 | SF | 6 | 25200 | 4 | 16800 | 10 | 42000
| Gypsum board chase walls - one side | 3360 | SF | 3.6 | 12096 | 2.4 | 8064 | 6 | 20160
| Gypsum board at attic perimeter | 2460 | SF | 3.6 | 8856 | 2.4 | 5904 | 6 | 14760
| Open office walls | 1572 | LF | 90 | 141480 | 60 | 94320 | 150 | 235800
| GB furr at inside face of exterior wall | 19500 | SF | 2.4 | 46800 | 1.6 | 31200 | 4 | 78000
| GB furr at steel columns | 12000 | SF | 2.4 | 28800 | 1.6 | 19200 | 4 | 48000
FLOOR FINISHES
| Concrete sealer | 16980 | SF | 0.9 | 15282 | 0.6 | 10188 | 1.5 | 25470
| Ceramic tile floors | 2850 | SF | 6 | 17100 | 6 | 17100 | 12 | 34200
| Seamless Sheet Linoleum Flooring | 20300 | SF | 6 | 121800 | 4 | 81200 | 10 | 203000
| Carpeting | 28000 | SF | 2.7 | 75600 | 1.8 | 50400 | 4.5 | 126000
| Entry mat with aluminum frame at vestibule | 270 | SF | 21 | 5670 | 14 | 3780 | 35 | 9450
BASE
| Ceramic tile base | 780 | LF | 7.2 | 5616 | 4.8 | 3744 | 12 | 9360
| Rubber 4" wall base | 14400 | LF | 1.2 | 17280 | 1.8 | 25920 | 3 | 43200
| Marble saddles at tile floors | 15 | EA | 30 | 450 | 20 | 300 | 50 | 750
WALL FINISHES
| Ceramic tile walls | 6630 | SF | 6 | 39780 | 4 | 26520 | 10 | 66300
| Vinyl wall covering at conference rooms | 5700 | SF | 1.8 | 10260 | 1.2 | 6840 | 3 | 17100
| Prime and paint gypsum board walls | 123000 | SF | 0.6 | 73800 | 0.4 | 49200 | 1 | 123000
CEILINGS
| Acoustical Panel Ceilings | 51600 | SF | 3.3 | 170280 | 2.2 | 113520 | 5.5 | 283800
| Paint exposed ceilings | 16800 | SF | 0.75 | 12600 | 0.5 | 8400 | 1.25 | 21000
MISC
| Paint SC Wood & HM doors and frames | 264 | LEAF | 39 | 10296 | 26 | 6864 | 65 | 17160
| Misc interior painting | 68400 | SF | 0.6 | 41040 | 0.4 | 27360 | 1 | 68400
[5 empty] | - |  | - |  | -
[5 empty] | 1290148.5 |  | 880199 |  | 2170347.5
10 | SPECIALTIES
| Canopy construction at main lobby entrances for Buildings 1, 2 and 3. Include structural steel, decking, finished soffit, finished fascia, roofing, drainage and lighting. 310 SF x 3 bldgs | 930 | SF | 96 | 89280 | 64 | 59520 | 160 | 148800
| Door signs | 252 | EA | 90 | 22680 | 60 | 15120 | 150 | 37800
| Misc signage | 3 | BLDG | 6000 | 18000 | 4000 | 12000 | 10000 | 30000
| Building logo | 3 | BLDG | 15000 | 45000 | 10000 | 30000 | 25000 | 75000
Toilet partitions and urinal screens
| Regular | 12 | EA | 100 | 1200 | 1400 | 16800 | 1500 | 18000
| Handicap | 6 | EA | 200 | 1200 | 2000 | 12000 | 2200 | 13200
| Urinal screens | 3 | EA | 50 | 150 | 550 | 1650 | 600 | 1800
Toilet accessories
| At Shower rooms | 6 | RM | 900 | 5400 | 600 | 3600 | 1500 | 9000
| At Men's Public Toilets | 3 | RM | 900 | 2700 | 600 | 1800 | 1500 | 4500
| At Womens Toilets | 3 | RM | 1200 | 3600 | 800 | 2400 | 2000 | 6000
| At Janitors Closets | 3 | RM | 300 | 900 | 200 | 600 | 500 | 1500
| Fire extinguishers and cabinets - not shown | 18 | EA | 70 | 1260 | 200 | 3600 | 270 | 4860
| Metal Lockers - not shown | 60 | EA | 150 | 9000 | 100 | 6000 | 250 | 15000
| Wood benches - not shown | 6 | EA | 300 | 1800 | 200 | 1200 | 500 | 3000
| Window blinds at first floor | 13260 | SF | 2.7 | 35802 | 1.8 | 23868 | 4.5 | 59670
| Misc specialties | 68400 | SF | 1.2 | 82080 | 0.8 | 54720 | 2 | 136800
[5 empty] | - |  | - |  | -
[5 empty] | 320052 |  | 244878 |  | 564930
11 | EQUIPMENT
| Kitchen equipment at all kitchens - 2 per building | 6 | RM | 4800 | 28800 | 3200 | 19200 | 8000 | 48000
| Dishwasher at each kitchen | 6 | EA | 900 | 5400 | 600 | 3600 | 1500 | 9000
| Garbage disposal unit at each kitchen | 6 | EA | 720 | 4320 | 480 | 2880 | 1200 | 7200
[5 empty] | - |  | - |  | -
[5 empty] | 38520 |  | 25680 |  | 64200
12 | FURNISHINGS
| Assume laboratory casework, countertops and shelving at all laboratories. Six lab rooms per building | 18 | RM | 15000 | 270000 | 10000 | 180000 | 25000 | 450000
| Furnish and install fume hood - one per building | 3 | EA | 12000 | 36000 | 8000 | 24000 | 20000 | 60000
| Furnish and install fume hood with HEPA filter and exhaust fan - one per building | 3 | EA | 21000 | 63000 | 14000 | 42000 | 35000 | 105000
[5 empty] | - |  | - |  | -
[5 empty] | 369000 |  | 246000 |  | 615000
13 | SPECIAL CONSTRUCTION | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
14 | CONVEYING SYSTEMS
| Allow for metal pan fire stairs to attic including all riser / tread and platform assemblies, and stringers. Two flight per building. | 6 | FLT | 9000 | 54000 | 6000 | 36000 | 15000 | 90000
[5 empty] | - |  | - |  | -
[5 empty] | 54000 |  | 36000 |  | 90000
15.1 | HVAC
Equipment
| Packaged RTU custom made 2" double wall construction gabanized steel interior liner, S & R fans, cooling and steam preheating coils, filters, humidifier, etc.Total - two each. Assume 32.5 cooling capacity each. | 195 | TN | 1000 | 195000 | 3000 | 585000 | 4000 | 780000
| Exhaust system with recovery | 3 | SYS | 72000 | 216000 | 48000 | 144000 | 120000 | 360000
Ductwork
| Galvanized steel duct (supply, return, exh. Air) w/ assocc. details | 75000 | LB | 4.8 | 360000 | 3.2 | 240000 | 8 | 600000
| Stainless steel duct for exhaust @ F.H. | 7500 | IB | 9 | 67500 | 6 | 45000 | 15 | 112500
| Insulation/ Acoust. Lin. | 45000 | SF | 1.8 | 81000 | 1.2 | 54000 | 3 | 135000
| Duct accessories | 1 | LS | 90000 | 90000 | 60000 | 60000 | 150000 | 150000
Piping
Chilled water system
Equipment conn.
| AHU, cooling coil, say 5" | 6 | SET | 12000 | 72000 | 8000 | 48000 | 20000 | 120000
| VAV, say 3/4"/ 1" | 180 | SET | 900 | 162000 | 600 | 108000 | 1500 | 270000
| Chilled water pipe distr., black steel, sch 40, w/ fittings, valves, hangers, anchors, say 21/2" average | 68400 | SF | 1.8 | 123120 | 1.2 | 82080 | 3 | 205200
| Insulation | 1 | LS | 45000 | 45000 | 30000 | 30000 | 75000 | 75000
Steam & condensate system
| LP Steam/condesate pipe distr., black steel, sch 40/sch80, w/ fittings, valves, hangers, anchors, say 21/2" average | 68400 | SF | 0.9 | 61560 | 0.6 | 41040 | 1.5 | 102600
| Hook - up of AHU steam coil w/ 2-way control valve | 6 | EA | 9045 | 54270 | 6030 | 36180 | 15075 | 90450
| Insulation | 1 | LS | 27000 | 27000 | 18000 | 18000 | 45000 | 45000
| Heating water system | 68400 | SF | 2.1 | 143640 | 1.4 | 95760 | 3.5 | 239400
| Testing & balancing | 68400 | SF | 0.6 | 41040 | 0.4 | 27360 | 1 | 68400
| Automatic temperature control (DDC ) | 68400 | SF | 3 | 205200 | 2 | 136800 | 5 | 342000
| Misc. | 68400 | SF | 0.9 | 61560 | 0.6 | 41040 | 1.5 | 102600
Rigging (AHU, EF, pumps)
Support for duct & pipes
HVAC of Mech. Room
Patching (cutting by GC )
Seismic restraints
[5 empty] | - |  | - |  | -
[5 empty] | 2005890 |  | 1792260 |  | 3798150
15.2 | PLUMBING
| Fixtures: water closet, lavatory, urinal, mop sink, drinking fountain, shower) w/ trim & rough piping | 57 | EA | 1080 | 61560 | 720 | 41040 | 1800 | 102600
| Lab fixtures only trim & rough piping of sink w/eye wash, emerg. shower (sinks FBO) | 36 | EA | 1200 | 43200 | 800 | 28800 | 2000 | 72000
| Cold & hot water, recirc., pump, electr. DHWH, sanitary, vent, storm, spec. gases, traps, etc | 68400 | SF | 4.8 | 328320 | 3.2 | 218880 | 8 | 547200
| Process system piping (nitrogen, liquid nitrogen, compressed air, deionized water | 68400 | SF | 1.8 | 123120 | 1.2 | 82080 | 3 | 205200
[5 empty] | - |  | - |  | -
[5 empty] | 556200 |  | 370800 |  | 927000
15.3 | FIRE PROTECTION
| Fire protection for Lab / Office Buildings | 68400 | SF | 2.4 | 164160 | 1.6 | 109440 | 4 | 273600
[5 empty] | - |  | - |  | -
[5 empty] | 164160 |  | 109440 |  | 273600
16 | ELECTRICAL
INSTALLATION OF LIGHT FIXTURES (Scale 1/8" =1'-0")
| Type A (2X4) w/ 4LF MC 12/2 Flex | 294 | EA | 19.2347 | 5655.0115 | 12.8232 | 3770.0076 | 32.0579 | 9425.0191
| Type B (4LF) Pendant w/ 4LF MC 12/2 Flex & JB | 132 | EA | 33.9124 | 4476.4332 | 22.6082 | 2984.2888 | 56.5206 | 7460.7221
| Type B / EM (4LF) Pendant w/ 4LF MC 12/2 Flex & JB | 18 | EA | 33.9229 | 610.6125 | 22.6153 | 407.075 | 56.5382 | 1017.6874
| TypeC / EM (4LF) Pendant w/ 4LF MC 12/2 Flex & JB | 216 | EA | 33.9113 | 7324.8449 | 22.6075 | 4883.2299 | 56.5189 | 12208.0748
| Type C / EM (4LF) Pendant w/ 4LF MC 12/2 Flex & JB | 36 | EA | 33.9229 | 1221.2249 | 22.6153 | 814.15 | 56.5382 | 2035.3749
| Type D (2X4) w/ 4LF MC 12/2 Flex | 18 | EA | 19.2565 | 346.6171 | 12.8377 | 231.0781 | 32.0942 | 577.6951
| Type E (2X2) w/ 4LF MC 12/2 Flex | 87 | EA | 19.2357 | 1673.507 | 12.8238 | 1115.6713 | 32.0595 | 2789.1783
| Type E/EM (2X2) w/ 4LF MC 12/2 Flex | 78 | EA | 19.2387 | 1500.6159 | 12.8258 | 1000.4106 | 32.0644 | 2501.0264
| Type F (2X4) w/ 4LF MC 12/2 Flex | 84 | EA | 19.2333 | 1615.5983 | 12.8222 | 1077.0655 | 32.0555 | 2692.6638
| Type G1 (Compact Down Light) w/ 4LF MC 12/2 Flex | 12 | EA | 17.981 | 215.7716 | 11.9873 | 143.8477 | 29.9683 | 359.6193
| Type G1/ EM (Compact Down Light) w/ 4LF MC 12/2 Flex | 6 | EA | 18.0505 | 108.3032 | 12.0337 | 72.2022 | 30.0842 | 180.5054
| Type G2 (Compact Wall washer) w/ 4LF MC 12/2 Flex | 24 | EA | 17.981 | 431.5431 | 11.9873 | 287.6954 | 29.9683 | 719.2385
| Type H (Compact Downlight) w/ 4LF MC 12/2 Flex Wet Location | 6 | EA | 18.0505 | 108.3032 | 12.0337 | 72.2022 | 30.0842 | 180.5054
| Type G2 (Compact Wall washer) w/ 4LF MC 12/2 Flex | 24 | EA | 17.981 | 431.5431 | 11.9873 | 287.6954 | 29.9683 | 719.2385
| Type J1 (Ceiling recess 4LF) w/ 4LF MC 12/2 Flex | 36 | EA | 20.1146 | 724.1255 | 13.4097 | 482.7503 | 33.5243 | 1206.8758
| Type J1/ EM (Ceiling recess 4LF) w/ 4LF MC 12/2 Flex | 6 | EA | 20.1378 | 120.8267 | 13.4252 | 80.5512 | 33.563 | 201.3779
| Type J2 (Ceiling recess 4LF) w/ 4LF MC 12/2 Flex | 57 | EA | 20.1085 | 1146.1841 | 13.4057 | 764.1227 | 33.5142 | 1910.3069
| Type J2/ EM (Ceiling recess 4LF) w/ 4LF MC 12/2 Flex | 12 | EA | 20.1378 | 241.6535 | 13.4252 | 161.1023 | 33.563 | 402.7558
| Type J3 (Ceiling recess 4LF) w/ 4LF MC 12/2 Flex | 9 | EA | 20.1378 | 181.2401 | 13.4252 | 120.8267 | 33.563 | 302.0668
| Type K (4LF Industrial) w/ 4LF MC 12/2 Flex | 18 | EA | 20.2306 | 364.15 | 13.487 | 242.7667 | 33.7176 | 606.9166
| Type L (2X4) w/ 4LF MC 12/2 Flex | 48 | EA | 19.2333 | 923.199 | 12.8222 | 615.466 | 32.0555 | 1538.665
| Type M (2X4) w/ 4LF MC 12/2 Flex | 24 | EA | 19.2333 | 461.5995 | 12.8222 | 307.733 | 32.0555 | 769.3325
| Exit Signs w/ 4LF MC 12/2 Flex | 54 | EA | 19.241 | 1039.0164 | 12.8274 | 692.6776 | 32.0684 | 1731.6939
| Switch w/ J.B. & 20 LF 12/2 MC | 138 | EA | 41.9555 | 5789.8645 | 27.9704 | 3859.9097 | 69.9259 | 9649.7742
| 3 Way Switch w/ J.B. & 20LF 12/3 MC | 6 | EA | 44.9454 | 269.6727 | 29.9636 | 179.7818 | 74.9091 | 449.4545
| Ceiling Mounted Occupancy Sensors w/ J.B. & 4LF 12/2 MC Flex | 60 | EA | 138.6741 | 8320.4464 | 92.4494 | 5546.9643 | 231.1235 | 13867.4107
| Wall Mounted Occupancy Sensors w/ J.B. & 20LF 12/2 MC Flex | 162 | EA | 150.4919 | 24379.6811 | 100.3279 | 16253.1208 | 250.8198 | 40632.8019
| Branch Circuits: 3/4" EMT 5#12 | 2250 | LF | 6.8428 | 15396.3909 | 4.5619 | 10264.2606 | 11.4047 | 25660.6515
| 3/4" EMT 3#12 For Pendant Mtd Fixtures @ Exposed Ceiling) | 1080 | LF | 5.1332 | 5543.903 | 3.4222 | 3695.9353 | 8.5554 | 9239.8383
| Light Fixture Quote( LAW Lighting: Contact: Lisa W. Tel #845-225-1366) | 1 | LS | 239580 | 239580 | 159720 | 159720 | 399300 | 399300 | Quote
WIRING DEVICES (Scale 1/8" =1'-0")
| Duplex w/ J.B. &25LF 12/2 MC | 666 | EA | 43.9839 | 29293.3014 | 29.3226 | 19528.8676 | 73.3066 | 48822.169
| GFI w/ J.B. & 25LF 12/2MC (Indoor) | 18 | EA | 59.8345 | 1077.021 | 39.8897 | 718.014 | 99.7242 | 1795.035
| Duplex w/ J.B. & 25 LF 3/4" EMT 3#12 | 39 | EA | 57.3606 | 2237.0645 | 38.2404 | 1491.3763 | 95.601 | 3728.4408
| Floor Mtd Duplex w/ 3/4" EMT 3#12 (15LF) | 18 | EA | 197.4307 | 3553.7518 | 131.6204 | 2369.1679 | 329.0511 | 5922.9198
| 3/4" EMT 3#12 For Furniture work stations | 2025 | LF | 5.1329 | 10394.0875 | 3.4219 | 6929.3917 | 8.5548 | 17323.4792
| Connection for Furniture work stations | 18 | EA | 42.5799 | 766.4382 | 28.3866 | 510.9588 | 70.9665 | 1277.397
| Wire mold For Work Lab Benches w/ outlets @ 6" oc.: G4050 w/ 5507 series plates | 972 | LF | 38.0592 | 36993.5841 | 25.3728 | 24662.3894 | 63.4321 | 61655.9735
| 3/4" EMT 5#12 for Wire Mold @ work lab benches | 6090 | LF | 6.8428 | 41672.8646 | 4.5619 | 27781.9098 | 11.4047 | 69454.7744
| Branch Circuits: 3/4" EMT 5#12 | 1695 | LF | 7.3002 | 12373.8859 | 4.8668 | 8249.2573 | 12.167 | 20623.1432
TELECOMMUNICATION (Scale 1/8" =1'-0")
| Tele / Data jack w/ 1" EMT & (4) CAT5e Cable (10LF) | 195 | EA | 48.0089 | 9361.7337 | 32.0059 | 6241.1558 | 80.0148 | 15602.8895
| Floor Mtd Tele/ Data w/ 1" EMT (4) cat 5e (30LF) | 60 | EA | 215.6547 | 12939.2802 | 143.7698 | 8626.1868 | 359.4244 | 21565.467
| Cat 5e Cable | 261600 | LF | 0.52599 | 137598.1992 | 0.35066 | 91732.1328 | 0.87664 | 229330.332
| 12 Strand FO Cable | 6000 | LF | 1.7449 | 10469.646 | 1.1633 | 6979.764 | 2.9082 | 17449.41
| 24 Strand FO Cable | 6000 | LF | 2.6049 | 15629.328 | 1.7366 | 10419.552 | 4.3415 | 26048.88
| 48 Strand FO Cable | 600 | LF | 3.4648 | 2078.901 | 2.3099 | 1385.934 | 5.7747 | 3464.835
| 96 Strand FO Cable | 600 | LF | 6.0447 | 3626.8056 | 4.0298 | 2417.8704 | 10.0745 | 6044.676
| 900 Pair Cat 3 Cable | 600 | LF | 21.4987 | 12899.205 | 14.3324 | 8599.47 | 35.8311 | 21498.675
| Cable Tray 18" Ladder Type | 1200 | LF | 13.8593 | 16631.208 | 9.2396 | 11087.472 | 23.0989 | 27718.68
| 18" Ladder Racks Vertical Mounted | 100 | LF | 13.1413 | 1314.1326 | 8.7609 | 876.0884 | 21.9022 | 2190.221
| Tele / Data jack w/ 1 1/2" EMT & (4) CAT5e Cable (15LF) @ wiremold (as per section 16744Part 2.1 Note B) | 72 | EA | 189.6962 | 13658.1291 | 126.4642 | 9105.4194 | 316.1604 | 22763.5485
| (2) set of 4" EMT from MDF closets to IDF closets | 600 | LF | 18.0338 | 10820.304 | 12.0226 | 7213.536 | 30.0564 | 18033.84
| Terminal backboards | 114 | LF | 5.4049 | 616.1562 | 3.6033 | 410.7708 | 9.0081 | 1026.927
| Terminal Racks 19"x 7FT high (including Patch Panels & Vertical cable manager | 6 | EA | 9100.41 | 54602.46 | 6066.94 | 36401.64 | 15167.35 | 91004.1
| Riser Fiber opitc Termination Enclosures CCS-03U & CCS-01U | 12 | EA | 386.9761 | 4643.7138 | 257.9841 | 3095.8092 | 644.9602 | 7739.523
| Wire management panel CJP-02U | 12 | EA | 108.1195 | 1297.4346 | 72.0797 | 864.9564 | 180.1992 | 2162.391
| Patch Panel Housing CCH-04U | 12 | EA | 297.2244 | 3566.6928 | 198.1496 | 2377.7952 | 495.374 | 5944.488
| CCH-CP12-57&59 (12 Port Panels) | 24 | EA | 66.3745 | 1592.9892 | 44.2497 | 1061.9928 | 110.6242 | 2654.982
| Fiber Opitc Terminations | 3 | LS | 1234.2 | 3702.6 | 822.8 | 2468.4 | 2057 | 6171
| Testing , Labelling of System & Punch downs | 3 | LS | 8712 | 26136 | 5808 | 17424 | 14520 | 43560
| Grounding for Tele/Data rooms & equipment | 3 | LS | 1626.24 | 4878.72 | 1084.16 | 3252.48 | 2710.4 | 8131.2
FIRE ALARM SYSTEM (Scale 1/8" =1'-0")
| Install Fire alarm control Panel (4100U Series) w/ misc. material | 3 | EA | 1452.726 | 4358.178 | 968.484 | 2905.452 | 2421.21 | 7263.63
| Install Pull Stations w/ 3/4" EMT & FA Cable (15LF) | 18 | EA | 51.7963 | 932.3328 | 34.5308 | 621.5552 | 86.3271 | 1553.8881
| Install Fire Signal Strobe w/ 3/4" EMT & FA Cable (10LF) | 69 | EA | 42.7929 | 2952.7073 | 28.5286 | 1968.4716 | 71.3214 | 4921.1789
| Install Fire Signal Horn w/ Strobe w/ 3/4" EMT & FA Cable (10LF) | 48 | EA | 42.7921 | 2054.021 | 28.5281 | 1369.3473 | 71.3202 | 3423.3683
| Install Smoke Detectors w/ 3/4" EMT & FA Cable (10LF) | 18 | EA | 42.7747 | 769.9448 | 28.5165 | 513.2965 | 71.2912 | 1283.2413
| Install Duct Detectors w/ 3/4" EMT & FA Cable (10LF) Assume | 72 | EA | 42.7863 | 3080.614 | 28.5242 | 2053.7427 | 71.3105 | 5134.3567
| Interfacing w/ Info. Management System @ Security FronT Entrance in Booster Ring: 3/4" RGS w FA Cable | 1200 | LF | 2.9402 | 3528.2874 | 1.9602 | 2352.1916 | 4.9004 | 5880.479
| 3/4" EMT w/ FA Cable | 6500 | LF | 1.6715 | 10864.5537 | 1.1143 | 7243.0358 | 2.7858 | 18107.5895
| 3/4" EMT w/ FA Cable to Duct Detectors | 8640 | LF | 1.6013 | 13835.6288 | 1.0676 | 9223.7526 | 2.6689 | 23059.3814
| 3/4" RGS 4 #10 | 950 | LF | 3.5949 | 3415.1584 | 2.3966 | 2276.7723 | 5.9915 | 5691.9308
| Grounding to Building 3/4" RGS 1 #10 | 750 | LF | 2.8587 | 2144.0232 | 1.9058 | 1429.3488 | 4.7645 | 3573.372
| Fire Alarm Quote as per Simplex Grinnell (Kevin Q.) | 1 | LSQ | 83127 | 83127 | 55418 | 55418 | 138545 | 138545
DISTRIBUTION EQUIPMENT & FEEDERS
| 112 Kva transformer K- rated w/ (1) 4LF 2" Flex 3# 2/0, 1 #6grd & (1) 4LF 4" 5 #500, 1# 1/0 grd | 3 | EA | 8954.0298 | 26862.0893 | 5969.3532 | 17908.0595 | 14923.3829 | 44770.1488
| 400 Amp, 480/277V, 3PH, 4W | 3 | EA | 3648.513 | 10945.539 | 2432.342 | 7297.026 | 6080.855 | 18242.565
| 400 Amp, 208/120V, 3PH, 4W | 3 | EA | 2333.5455 | 7000.6365 | 1555.697 | 4667.091 | 3889.2425 | 11667.7275
| 150 Amp, 208/120V, 3PH, 4W (2 Section Panels) | 18 | EA | 3438.1182 | 61886.1276 | 2292.0788 | 41257.4184 | 5730.197 | 103143.546
| 3 1/2" EMT 4#500, 1#3 grd | 750 | LF | 56.6752 | 42506.4288 | 37.7835 | 28337.6192 | 94.4587 | 70844.048
| 4" EMT 5#500, 1# 1/0 grd | 30 | LF | 67.5796 | 2027.3877 | 45.0531 | 1351.5918 | 112.6326 | 3378.9794
| 21/2" EMT 5# 1/0, 2#6 grd | 765 | LF | 20.5658 | 15732.8556 | 13.7105 | 10488.5704 | 34.2764 | 26221.426
| 2" EMT 3# 2/0, 1# 6 grd | 30 | LF | 13.1719 | 395.1582 | 8.7813 | 263.4388 | 21.9532 | 658.5969
| 1: EMT 1# 1/0 grd | 30 | LF | 3.9045 | 117.1365 | 2.603 | 78.091 | 6.5076 | 195.2274
| Ground rod | 3 | EA | 43.4148 | 130.2444 | 28.9432 | 86.8296 | 72.358 | 217.074
| HVAC EQUIPMENT CONNECTIONS & FEEDERS | [6 empty] | 0
| AHU-301 & 401 7 HRU-1: 60 Amps / 3PH w/ 1" Flex 4#8 (3LF) | 9 | EA | 235.2795 | 2117.5151 | 156.853 | 1411.6767 | 392.1324 | 3529.1919
| RF-301 & RF401& EF-401: 30 Amps / 3PH,w/ 3/4" Flex 3#10 (3LF) | 36 | EA | 144.3078 | 5195.0818 | 96.2052 | 3463.3878 | 240.513 | 8658.4696
| Exhaust fan Connections w/ 3/4" Flex 3#10 (3LF) | 33 | EA | 28.8167 | 950.9511 | 19.2111 | 633.9674 | 48.0278 | 1584.9185
| 1" EMT 4#8 | 1080 | LF | 3.219 | 3476.5236 | 2.146 | 2317.6824 | 5.365 | 5794.206
| 3/4" EMT 3#10 | 5520 | LF | 1.7182 | 9484.464 | 1.1455 | 6322.976 | 2.8637 | 15807.44
| Lab Exhaust Heat recovery (175 Amps 2 1/2" EMT 4#2/0 | 1380 | LF | 27.9649 | 38591.5827 | 18.6433 | 25727.7218 | 46.6082 | 64319.3045
| ATTIC WIRING |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Duplex w/ J.B. & 25 LF 3/4" EMT 3#12 | 12 | EA | 57.366 | 688.3917 | 38.244 | 458.9278 | 95.61 | 1147.3196
| Switch w/ J.B. & 25 LF 3/4" EMT 3#12 | 6 | EA | 57.2964 | 343.7784 | 38.1976 | 229.1856 | 95.494 | 572.964
| Globe Light Fixtures | 12 | EA | 92.3956 | 1108.7472 | 61.5971 | 739.1648 | 153.9927 | 1847.912
| Branch Circuits: 3/4" EMT 3#12 | 750 | LF | 6.3853 | 4788.9864 | 4.2569 | 3192.6576 | 10.6422 | 7981.644
| CARD ACCESS SYSTEM |  |  | 0 | 0 | 0 | 0 | 0 | 0
| Card readers w/ 3/4" EMT & Cabling (15LF) | 81 | EA | 39.028 | 3161.2654 | 26.0186 | 2107.5102 | 65.0466 | 5268.7756
| Power to Card Access Control panel: 3/4" EMT 4#12 | 60 | LF | 6.6152 | 396.9115 | 4.4101 | 264.6076 | 11.0253 | 661.5191
| 3/4" EMT w/ Cabling from each Card Acces Point to Control panel | 12330 | LF | 1.6715 | 20609.256 | 1.1143 | 13739.504 | 2.7858 | 34348.76
MISCELLANEOUS
| FIRE ALARM PROGRAMMING & TESTING | 3 | BLDG | 4827.9 | 14483.7 | 3218.6 | 9655.8 | 8046.5 | 24139.5
| TEMPORARY LIGHT & POWER | 81300 | SF | 0.45 | 36585 | 0.3 | 24390 | 0.75 | 60975
| PENETRATION & FIRE STOPPING | 81300 | SF | 0.3 | 24390 | 0.2 | 16260 | 0.5 | 40650
| Ground, lighting protection, Elect-Stat | 27100 | GSF | 0.24459 | 6628.38 | 0.16306 | 4418.92 | 0.40765 | 11047.3
[5 empty] | - |  | - |  | -
[5 empty] | 1288294.1089 |  | 858862.7392 |  | 2147156.8481
[5 empty] | 11614744.6089 |  | 8044773.0726 |  | 19659517.6814
[7 empty] | 0 |  | 19659517.6814

## TRADE - SITEWORK
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
| DESCRIPTION |  | AMOUNT
2 | SITE PREPARATION & IMPROVEMENTS |  | 6628518.9815
-
| SUB TOTAL |  | 6628518.9815
| GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 994277.8472
-
| SUB TOTAL |  | 7622796.8287
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 7622796.8287
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 7622796.8287 | 7622796.8287
2A | MECHANICAL UTILITIES INCLUDING CHILLED WATER UTILITIES |  | 9223505.0506
-
| SUB TOTAL |  | 9223505.0506
| GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 1383525.7576
-
| SUB TOTAL |  | 10607030.8081
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 10607030.8081
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 10607030.8081 | 10607030.8081
2A | ELECTRICAL UTILITIES |  | 10427392.921
-
| SUB TOTAL |  | 10427392.921
| GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 1564108.9382
-
| SUB TOTAL |  | 11991501.8591
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 11991501.8591
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 11991501.8591 | 11991501.8591
2B | LN2 & GN2 DISTRIBUTION SYSTEM |  | 885000
| GEN. CONDITIONS, OVERHEAD & PROFIT | 15% | 132750
-
| SUB TOTAL |  | 1017750
| DESIGN CONTINGENCY * | 0% | 0
-
| SUB TOTAL |  | 1017750
| ESCALATION * | 0% | 0
-
| TOTAL COST |  | 1017750 | 1017750
* SEE MAIN SUMMARY SHEET

## EST - SITEWORK
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
SITEWORK - CSI TRADE ESTIMATE
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
2 | SITEWORK PREPARATION AND IMPROVEMENTS | 1.6.3.2
A | TEMPORARY FACILITIES AND CONTROL
| Erect and maintain temporary 4' high vinyl saftey fence around excavated site. | 3200 | LF | 5.4 | 17280 | 3.6 | 11520 | 9 | 28800
| Provide entrance gates and hardware at perimeter construction fence. | 4 | PR | 1368 | 5472 | 912 | 3648 | 2280 | 9120
| Relocation of underground electric utility line | 1100 | LF | 24 | 26400 | 16 | 17600 | 40 | 44000
| Relocation of underground communications utility line | 1100 | LF | 18 | 19800 | 12 | 13200 | 30 | 33000
| Relocation of water utility line | 1100 | LF | 36 | 39600 | 24 | 26400 | 60 | 66000
B | SITE PREPARATION
Site Demolition - Remove the following underground utilities. Include all trenching
| Remove communications lines | 3800 | LF | 2.535 | 9633 | 1.69 | 6422 | 4.225 | 16055
| Remove communications structures 27' x 27' | 5 | EA | 468 | 2340 | 312 | 1560 | 780 | 3900
| Remove electric lines | 3200 | LF | 2.73 | 8736 | 1.82 | 5824 | 4.55 | 14560
| Remove electric structures / manholes | 3 | EA | 234 | 702 | 156 | 468 | 390 | 1170
| Cap electric line and make safe | 4 | EA | 306 | 1224 | 204 | 816 | 510 | 2040
| Remove 2" and 4" water lines | 1300 | LF | 3.9 | 5070 | 2.6 | 3380 | 6.5 | 8450
| Remove 8" water lines | 1500 | LF | 5.85 | 8775 | 3.9 | 5850 | 9.75 | 14625
| Remove 6" water lines | 1500 | LF | 5.4 | 8100 | 3.6 | 5400 | 9 | 13500
| Cap water lines | 6 | EA | 222 | 1332 | 148 | 888 | 370 | 2220
| Remove 6" sanitary lines | 1750 | LF | 3.9 | 6825 | 2.6 | 4550 | 6.5 | 11375
| Remove 8" sanitary lines | 1650 | LF | 5.85 | 9652.5 | 3.9 | 6435 | 9.75 | 16087.5
| Remove 10" sanitary lines | 540 | LF | 5.85 | 3159 | 3.9 | 2106 | 9.75 | 5265
| Remove sanitary manholes | 18 | EA | 195 | 3510 | 130 | 2340 | 325 | 5850
| Remove 6" force main | 700 | LF | 3.9 | 2730 | 2.6 | 1820 | 6.5 | 4550
| Cap sanitary lines | 10 | EA | 1200 | 12000 | 800 | 8000 | 2000 | 20000
| Remove 8" storm lines | 110 | LF | 5.85 | 643.5 | 3.9 | 429 | 9.75 | 1072.5
| Remove 12" storm lines | 1400 | LF | 7.8 | 10920 | 5.2 | 7280 | 13 | 18200
| Remove 18" storm lines | 270 | LF | 8.58 | 2316.6 | 5.72 | 1544.4 | 14.3 | 3861
| Cap storm lines | 3 | EA | 81.6 | 244.8 | 54.4 | 163.2 | 136 | 408
| Remove storm manholes | 10 | EA | 136.5 | 1365 | 91 | 910 | 227.5 | 2275
| Demolition of existing pavements and curbs within rough grading ( mass excavation ) area | 457000 | SF | 0.3 | 137100 | 0.2 | 91400 | 0.5 | 228500
| Demolition of existing railroad tracks, ties and bed within the rough grading ( mass Excavation ) area | 1230 | LF | 5.07 | 6236.1 | 3.38 | 4157.4 | 8.45 | 10393.5
| Demolition of existing building foundations - based on building footprint. ( six buildings ) | 49000 | SF | 2.4 | 117600 | 1.6 | 78400 | 4 | 196000
| Remove unsuitable materials from site and legally dispose. | [7 empty] | With above costs
| Cutting, capping and relocation of monitoring wells | 4 | EA | 4368 | 17472 | 2912 | 11648 | 7280 | 29120
C | EARTHWORK
Scope of work includes existing elevations to rough grade elevations only.
| Earth cut and stockpile on site. Note : All Bulkcut earthwork based on a crew consisting of one equipment operator, laborer assistant, 2.25 cy - front end loader - haul sand / gravel by haul truck a maximum distance of 300' | 132500 | CY | 8.4 | 1113000 | 5.6 | 742000 | 14 | 1855000
| Topsoil cut and stockpile on site ( based on 10 acres +/- x 4" thick | 5200 | CY | 8.4 | 43680 | 5.6 | 29120 | 14 | 72800
| Earth fill from excavated earth | 15400 | CY | 8.4 | 129360 | 5.6 | 86240 | 14 | 215600
| Compaction at earth fill - use 10% of total | 1540 | CY | 8.4 | 12936 | 5.6 | 8624 | 14 | 21560
| Clear and grub within rough grading areas | 10 | ACRE | 3888 | 38880 | 2592 | 25920 | 6480 | 64800
| Layout, survey and stake | 1 | LS | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
| Protection of existing trees to remain as required | 50 | EA | 73.5 | 3675 | 49 | 2450 | 122.5 | 6125
D | SOIL EROSION / SEDIMENT CONTROL
| Soil erosion and sediment control | 20 | ACRE | 6360 | 127200 | 4240 | 84800 | 10600 | 212000
| Gravel haul road ( loop road ) - 10" deep x 20' wide | 1300 | CY | 24 | 31200 | 16 | 20800 | 40 | 52000
| Temporary seeding at disturbed areas | [7 empty] | INCLUDED IN ABOVE
| Temporary sediment basins - located in each watershed badin within proposed permanent extended detention and retention stormwater ponds. | 130000 | SF | [5 empty] | INCLUDED IN ABOVE
| Temporary dry and wet swales | [7 empty] | INCLUDED IN ABOVE
| Check dams and rock dams - located in drainage swales to help filter out sediments | [7 empty] | INCLUDED IN ABOVE
| Stone base at all construction entrances and exits to prevent mud from being tracked on roads beyond site. | 47000 | SF | [5 empty] | INCLUDED IN ABOVE
E | SITE MAINTENANCE
| Provide site observation and ongoing maintenance of rough graded site during the six month period the project will lay dormant. | 1 | LS | 25350 | 25350 | 16900 | 16900 | 42250 | 42250
F | SITE STRUCTURES | [8 empty] | Site Preparation
| Expansion of existing Substation Building 603. Include all structural steel, concrete, metal panel walls, interiors, doors, and MEP's to add 200 SF. To existing building | 200 | SF | 105 | 21000 | 70 | 14000 | 175 | 35000 | 3392532.5
G | SITE IMPROVEMENTS
| Asphalt paving and aggregate base at parking areas. See drawing C-109. | 161200 | SF | 2.1 | 338520 | 1.4 | 225680 | 3.5 | 564200
| Asphalt paving and aggregate base at LOB 3 and LOB 4 parking areas are with alternate costs. See drawing C-109. | 69800 | SF | [5 empty] | With Alternate
| Asphalt paving and aggregate base at roads outside Ring Building. See drawing C-109. | 115800 | SF | 2.4 | 277920 | 1.6 | 185280 | 4 | 463200
| Asphalt paving and aggregate base at roads inside Ring Building. See drawing C-109. | 45600 | SF | 2.4 | 109440 | 1.6 | 72960 | 4 | 182400
| Asphalt patching where new asphalt roads meet exisitng roads. See drawing C-109. | 360 | LF | 6 | 2160 | 4 | 1440 | 10 | 3600
| Reinforced heavy duty concrete paving at loading docks. See drawing C-109. | 32500 | SF | 7.2 | 234000 | 4.8 | 156000 | 12 | 390000
| Reinforced heavy duty concrete paving at road under ring building. See drawing C-109. | 14700 | SF | 7.2 | 105840 | 4.8 | 70560 | 12 | 176400
| Concrete retaining walls at load dock areas at inner ring. Include all reinforcing and formwork. Say avg 10' deep x 502' long | 185.9259 | CY | 300 | 55777.7778 | 200 | 37185.1852 | 500 | 92962.963
| Concrete retaining walls at road under ring building to inner ring. Include all reinforcing and formwork. Say avg 10' deep x 1,035' long | 383.3333 | CY | 300 | 115000 | 200 | 76666.6667 | 500 | 191666.6667
| Concrete wall footings at above retaining walls. Include all reinforcing and formwork. Say avg 4' wide x 1.0' deep x 1537' long | 227.7037 | CY | 300 | 68311.1111 | 200 | 45540.7407 | 500 | 113851.8519
| Assume perforated drain at base of retaining walls | 1537 | LF | 12 | 18444 | 8 | 12296 | 20 | 30740
| Concrete sidewalks include wwm and gravel fill adjacent to main building entry and all parking areas. See drawing C-109. | 16600 | SF | 4.5 | 74700 | 3 | 49800 | 7.5 | 124500
| Specialty paving ( concrete and concrete pavers) at main entry. See drawing C-109. | 9800 | SF | 9 | 88200 | 6 | 58800 | 15 | 147000
| 4'-0" Wide gravel mow strip at building perimeter | 27200 | SF | 1.2 | 32640 | 0.8 | 21760 | 2 | 54400
| Concrete curbs at main entrance only as shown on drawing C-109. | 4300 | LF | 9.6 | 41280 | 6.4 | 27520 | 16 | 68800
| Reinforced concrete pad at nitrogen tank - 25' x 63' | 1575 | SF | 9 | 14175 | 6 | 9450 | 15 | 23625
| Misc reinforced concrete pads | 800 | SF | 9 | 7200 | 6 | 4800 | 15 | 12000
| Assume chain link fence and gate at nitrogen tank pad | 176 | LF | 18 | 3168 | 12 | 2112 | 30 | 5280
| Precast bumpers at car parking ( exclude parking at LOB 3 and LOB 4) | 521 | EA | 30 | 15630 | 20 | 10420 | 50 | 26050
| Paint car lines at parking lots (exclude parking at LOB 3 and LOB 4). | 521 | EA | 6 | 3126 | 4 | 2084 | 10 | 5210
| Misc site signage, traffic arrows, stop lines, handicap markings etc. | 1 | LS | 9000 | 9000 | 6000 | 6000 | 15000 | 15000
LANDSCAPING
| Trees at main entrance shown on drawing C-109. Include all trenching, topsoil, guy wires and stakes | 86 | EA | 210 | 18060 | 140 | 12040 | 350 | 30100
| Allow for trees at all other parking areas. Include all trenching, topsoil, guy wires and stakes. Not shown on plans | 500 | EA | 210 | 105000 | 140 | 70000 | 350 | 175000
| Grass areas | 950000 | SF | 0.12 | 114000 | 0.08 | 76000 | 0.2 | 190000 | Site Improvements
| Mulched areas - planters, shrubs, import topsoil etc. | 1 | LS | 90000 | 90000 | 60000 | 60000 | 150000 | 150000 | 3235986.4815
| Irrigation of landscaped areas | [7 empty] | Exclude
-
[9 empty] | 6628518.9815 |  | 6628518.9815 | 3977111.3889 | 2651407.5926
H | MECHANICAL UTILITIES | 1.6.3.6
HVAC Systems
Chilled water system
| Conn. to the exist. chilled water plant main | 2 | Conn. | 4222.5 | 8445 | 2815 | 5630 | 7037.5 | 14075
Chilled water pipe, U/ground., D.I.P.
| 6" | 3780 | LF | 57.5639 | 217591.4664 | 38.3759 | 145060.9776 | 95.9398 | 362652.444
| Say 12" | 2460 | LF | 102.7267 | 252707.805 | 68.4845 | 168471.87 | 171.2113 | 421179.675
| Valves, butterfly, 6" & 12" | 12 | EA | 1144.5 | 13734 | 763 | 9156 | 1907.5 | 22890
| Fittings : 90 deg elbows & tee | 16 | EA | 825 | 13200 | 675 | 10800 | 1500 | 24000
| Insulation | 1 | LS | 124308.3178 | 124308.3178 | 83372.2119 | 83372.2119 | 207680.5297 | 207680.5297
| Hangers, anchors, guides, supports | 1 | LS | 198893.3086 | 198893.3086 | 133395.539 | 133395.539 | 332288.8476 | 332288.8476
Condenser water system
Equipment
| Cooling tower, 3 sells at 1350 Tn each | 4050 | Tn | 217.2675 | 879933.375 | 144.845 | 586622.25 | 362.1125 | 1466555.625
| Pumps | 3 | EA | 5000 | 15000 | 25000 | 75000 | 30000 | 90000
Piping ( CT)
Underground condenser. water pipe distr., black steel, sch 40,
| 6" incl. 140' tunnel mtd | 1800 | LF | 51.315 | 92367 | 34.21 | 61578 | 85.525 | 153945
| 16" | 4680 | LF | 120.855 | 565601.4 | 80.57 | 377067.6 | 201.425 | 942669
| Hangers, anchors, guides, supports | 1 | LS | 90000 | 90000 | 60000 | 60000 | 150000 | 150000
Valves, butterfly
| 6" | 10 | EA | 64.38 | 643.8 | 42.92 | 429.2 | 107.3 | 1073
| 16" | 4 | EA | 125.115 | 500.46 | 83.41 | 333.64 | 208.525 | 834.1
Fittings
| 16", 90 deg elbows | 10 | EA | 580.59 | 5805.9 | 387.06 | 3870.6 | 967.65 | 9676.5
| 16" tee | 12 | EA | 550.815 | 6609.78 | 367.21 | 4406.52 | 918.025 | 11016.3
| 16" cooling tower final conn. (assume valves incl. in equipm) | 1 | Set | 4308.15 | 4308.15 | 2872.1 | 2872.1 | 7180.25 | 7180.25
Insulation, as per spec.
| Pipe wrapping | 6480 | LF | 12 | 77760 | 8 | 51840 | 20 | 129600
Steam & condensate system
| 6" high pressure steam supply Conn. to exist. steam & 2-1/2" condens. Pipes. | 2 | CONN | 6000 | 12000 | 4000 | 8000 | 10000 | 20000
| PRV station one stage ( Mech room, underground by GC) | 1 | LS | 60000 | 60000 | 40000 | 40000 | 100000 | 100000
| Condenser duplex pump with condenser piping | 1 | SET | 24000 | 24000 | 16000 | 16000 | 40000 | 40000
Ductile iron piping, pre - insulated with protective jacket. Based on Perma Pipe material prices
| 6"HP 300 psi | 1410 | LF | 43.53 | 61377.3 | 92 | 129720 | 135.53 | 191097.3
| 5" LP steam | 1890 | LF | 38.63 | 73010.7 | 66 | 124740 | 104.63 | 197750.7
| 2" & 2-1/2" CPD | 3300 | LF | 23.39 | 77187 | 53 | 174900 | 76.39 | 252087
| Valves 6" tru 2-1/2" | 12 | EA | 2200 | 26400 | 1800 | 21600 | 4000 | 48000
| Fittings, anchors, guides, supports | 1 | LS | 118987.5 | 118987.5 | 225480 | 225480 | 344467.5 | 344467.5
| Insulation | 1 | LS | 89240.625 | 89240.625 | 169110 | 169110 | 258350.625 | 258350.625
| Extra cost for conduit encasing steam lines | [7 empty] | Included with piping
| Excavation of trench related w/HVAC pipes above (b/fill & finish grade - by GC) | 12590 | CY | 6 | 75540 | 4 | 50360 | 10 | 125900
| Conc. work for support | 70 | EA | 600 | 42000 | 400 | 28000 | 1000 | 70000
| Manholes | 7 | EA | 60000 | 420000 | 40000 | 280000 | 100000 | 700000
Utility
Water
| Conn. new pipe to existing water main. | 1 | CONN | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
| Remove exist. u/g pipe w/ valves & MH, inc. excav. work (b/fill -by GC) | 5400 | LF | 18 | 97200 | 12 | 64800 | 30 | 162000
| Remove exist. u/g pipe w/ assocc. appurtenances incl. excav.work (b/fill -by GC) | 1 | Locat. | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
New pipe, say D.I.P
| 3"& 4" (hydrant) | 2650 | LF | 18.69 | 49528.5 | 12.46 | 33019 | 31.15 | 82547.5
| 6" (loop) | 5599 | LF | 22.9125 | 128287.0875 | 15.275 | 85524.725 | 38.1875 | 213811.8125
| 8" Main | 750 | LF | 26.535 | 19901.25 | 17.69 | 13267.5 | 44.225 | 33168.75
| Fittings & Valves, 3" tru 8" | 1 | LS | 40464 | 40464 | 26976 | 26976 | 67440 | 67440
| Hydrant, say 4" incl. tee, excav, identific., etc | 17 | EA | 3600 | 61200 | 2400 | 40800 | 6000 | 102000
| Excavation of trench related w/Plumbing pipes above (b/fill & finish grade - by GC) | [7 empty] | Included
Sanitary Sewer System
| Remove exist. pump station | 1 | Set | 12000 | 12000 | 8000 | 8000 | 20000 | 20000
| Remove exist. underground sanitary sewers pipes, say 6" (MH assocc. w/ pipes to be abandoned) | 4300 | LF | 6 | 25800 | 4 | 17200 | 10 | 43000
| Remove exist. MH | 8 | EA | 1800 | 14400 | 1200 | 9600 | 3000 | 24000
| Excavation to remove u/g pipe, l=4700', say w=2', deep 5' (b/fill & finish work by GC) | 1592.5926 | CY | 7.8 | 12422.2222 | 5.2 | 8281.4815 | 13 | 20703.7037
Provide new u/g sanitry sewer pipe as per specifications
| 6" | 1530 | LF | 15.1214 | 23135.7573 | 10.0809 | 15423.8382 | 25.2023 | 38559.5955
| 10" | 2550 | LF | 26.4606 | 67474.53 | 17.6404 | 44983.02 | 44.101 | 112457.55
| Excavation u/g pipe, l=4080', say w=2', deep 5' (b/fill & finish work by GC) | 1510 | CY | 7.8 | 11778 | 5.2 | 7852 | 13 | 19630
| Pump station | 1 | Stat. | 60000 | 60000 | 40000 | 40000 | 100000 | 100000
| New manhole (MH) | 12 | EA | 9000 | 108000 | 6000 | 72000 | 15000 | 180000
| Conn. new pipe to exist. MH | 2 | Conn. | 6000 | 12000 | 4000 | 8000 | 10000 | 20000
| Conn. exist. sanitary sewers to new sanitary sewer MH | 2 | Conn. | 6000 | 12000 | 4000 | 8000 | 10000 | 20000
| Modify exist. MH | 1 | LS | 9000 | 9000 | 6000 | 6000 | 15000 | 15000
Storm drain/Roof drain system
| Conn. new storm drain to exist. MH | 2 | Conn | 4500 | 9000 | 3000 | 6000 | 7500 | 15000
| Conn. new storm drain to exist. Ditch, 60" & 36" | 2 | Conn | 3000 | 6000 | 2000 | 4000 | 5000 | 10000
New pipes, assume RCP
| 12" | 1760 | LF | 23.904 | 42071.04 | 15.936 | 28047.36 | 39.84 | 70118.4
| 15" | 180 | LF | 25.104 | 4518.72 | 16.736 | 3012.48 | 41.84 | 7531.2
| 18" | 710 | LF | 28.1358 | 19976.418 | 18.7572 | 13317.612 | 46.893 | 33294.03
| 24" | 170 | LF | 38.256 | 6503.52 | 25.504 | 4335.68 | 63.76 | 10839.2
| 30" | 140 | LF | 53.6142 | 7505.988 | 35.7428 | 5003.992 | 89.357 | 12509.98
| 36" | 850 | LF | 69.4941 | 59069.985 | 46.3294 | 39379.99 | 115.8235 | 98449.975
| 48" | 260 | LF | 95.1937 | 24750.375 | 63.4625 | 16500.25 | 158.6562 | 41250.625
| 60" | 430 | LF | 138.7412 | 59658.6945 | 92.4941 | 39772.463 | 231.2353 | 99431.1575
| New storm manholes | 6 | EA | 3000 | 18000 | 2000 | 12000 | 5000 | 30000
| New catch basins | 28 | EA | 1500 | 42000 | 1000 | 28000 | 2500 | 70000
| Leaching basins @ 12" storm drain , approx. | 200 | LF | 8.4 | 1680 | 5.6 | 1120 | 14 | 2800
| Excavation u/g pipe, l=4500', say w=5', deep 5' (b/fill & finish work by GC) | 4658 | CY | 5.4 | 25153.2 | 3.6 | 16768.8 | 9 | 41922
Compressed air system
| Air compressor, duplex, 100 scfm oil free back-up, incl. hook-up, specialties, etc | 1 | Set | 25845 | 25845 | 17230 | 17230 | 43075 | 43075
Pipe, u/ground, copper, hard drawn with wrapping
| 1" | 980 | LF | 10.5971 | 10385.1825 | 8.6704 | 8496.9675 | 19.2675 | 18882.15
| 3" | 2220 | LF | 20.8388 | 46262.1637 | 17.0499 | 37850.8612 | 37.8887 | 84113.025
| Fittings, valves, etc | 1 | LS | 27500 | 27500 | 22500 | 22500 | 50000 | 50000
Misc.
| Commissioning, submittal, shop dwg, "as built" dwg, testing, rinsing, identification, mobilization, watching, fencing, signs, etc | 1 | LS | 400000 | 400000 | 100000 | 100000 | 500000 | 500000
[5 empty] | - |  | - |  | -
[5 empty] | 5256624.5216 |  | 3966880.529 |  | 9223505.0506 |  | 9223505.0506 | 5256624.5216 | 3966880.529
J | ELECTRICAL UTILITIES | 1.6.3.9
POWER EQUIPMENT
| Connections to Substations to Exisitng Spare Circuit Breaker in Building #603 SWG BUS #0 & SWG BUS #2 | 4 | LS | 12342 | 49368 | 8228 | 32912 | 20570 | 82280
| Installlation Of All :2500 /2800 Kva, (550A/650A) 13800-480Y/277Y Oil Filled Sub Trans../w misc Material | 8 | EA | 33650.1 | 269200.8 | 22433.4 | 179467.2 | 56083.5 | 448668
POWER DISTRIBUTION FEEDERS
| Building #603 SWG Bus #0 & SWG Bus #2 - Substation-LB: (4) 5" PVC SCH 40 4#1000MCM 15kva (MV105) 133% EPR Copper | 7340 | LF | 115.6155 | 848617.77 | 77.077 | 565745.18 | 192.6925 | 1414362.95
| Sub-LB - Sub-2: (4) 5" PVC SCH 40 4#1000MCM 15kva (MV105) 133% EPR Copper | 848 | LF | 115.6152 | 98041.6536 | 77.0768 | 65361.1024 | 192.6919 | 163402.756
| Sub-2 - Sub-3: (4) 5" PVC SCH 40 4#1000MCM 15kva (MV105) 133% EPR Copper | 1440 | LF | 115.6155 | 166486.32 | 77.077 | 110990.88 | 192.6925 | 277477.2
| Sub-3 - Sub-4: (4) 5" PVC SCH 40 4#1000MCM 15kva (MV105) 133% EPR Copper | 1400 | LF | 115.6155 | 161861.7 | 77.077 | 107907.8 | 192.6925 | 269769.5
| Sub-4 - Sub-5: (4) 5" PVC SCH 40 4#1000MCM 15kva (MV105) 133% EPR Copper | 1460 | LF | 115.6155 | 168798.63 | 77.077 | 112532.42 | 192.6925 | 281331.05
| Sub-5 - Sub-RF1: (4) 5" PVC SCH40 4#1000MCM 15kva (MV105) 133% EPR Copper | 448 | LF | 115.6149 | 51795.4536 | 77.0766 | 34530.3024 | 192.6914 | 86325.756
| Sub-RF1 - Sub-CP: (4) 5" PVC SCH40 4#1000MCM 15kva (MV105) 133% EPR Copper | 120 | LF | 115.6155 | 13873.86 | 77.077 | 9249.24 | 192.6925 | 23123.1
| Sub-RF1 - Future Sub-RF2: (4) 5" PVC SCH40 w/ Drag Line | 80 | LF | 38.6051 | 3088.404 | 25.7367 | 2058.936 | 64.3418 | 5147.34
| Sub-CP - Sub-1: (4) 5" PVC SCH40 4#1000MCM 15kva (MV105) 133% EPR Copper | 880 | LF | 115.6155 | 101741.64 | 77.077 | 67827.76 | 192.6925 | 169569.4
| 5" PVC SCH40 Spare (In Duct Bank Detail 6/E501) | 7000 | LF | 38.6087 | 270260.76 | 25.7391 | 180173.84 | 64.3478 | 450434.6
|  |  |  | 0 | 0 | 0 | 0 |  | 0
| Sub-LB - SWG-LB: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 980 | LF | 100.2028 | 98198.76 | 66.8019 | 65465.84 | 167.0047 | 163664.6
| Sub-2 - SWG-2: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 1610 | LF | 100.2024 | 161325.912 | 66.8016 | 107550.608 | 167.004 | 268876.52
| Sub-3 - SWG-3: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 1400 | LF | 100.2025 | 140283.528 | 66.8017 | 93522.352 | 167.0042 | 233805.88
| Sub-4 - SWG-4: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 1960 | LF | 100.2024 | 196396.794 | 66.8016 | 130931.196 | 167.0041 | 327327.99
| Sub-5 - SWG-5: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 1960 | LF | 100.2024 | 196396.794 | 66.8016 | 130931.196 | 167.0041 | 327327.99
| Sub-RF1 - SWG-RF1: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 1120 | LF | 100.2023 | 112226.532 | 66.8015 | 74817.688 | 167.0038 | 187044.22
| Sub-CP - SWG-CP: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 840 | LF | 100.2027 | 84170.262 | 66.8018 | 56113.508 | 167.0045 | 140283.77
| Sub-1 - SWG-1: (14) Sets 4" PVC Sch 40 4#600, 1# 500grd | 1540 | LF | 100.2026 | 154312.026 | 66.8017 | 102874.684 | 167.0044 | 257186.71
| 5" PVC SCH40 Spare (In Duct Bank Detail 9/E501) | 3260 | LF | 38.6087 | 125864.442 | 25.7391 | 83909.628 | 64.3479 | 209774.07
| Sub-3 - GEN #1: (1) Sets 4" PVC Sch 40 4#500, 1# 500grd | 130 | LF | 84.7968 | 11023.584 | 56.5312 | 7349.056 | 141.328 | 18372.64
| Sub-CP- GEN #2: (1) Sets 4" PVC Sch 40 4#500, 1# 500grd | 140 | LF | 84.7968 | 11871.552 | 56.5312 | 7914.368 | 141.328 | 19785.92
| 4" PVC SCH40 Spare (In Duct Bank Detail 9/E501) | 270 | LF | 38.6098 | 10424.634 | 25.7398 | 6949.756 | 64.3496 | 17374.39
| HV Manhole, Splicing | 8 | EA | 14799.51 | 118396.08 | 9866.34 | 78930.72 | 24665.85 | 197326.8
| Grounding for duct banks: # 4/0 Bare Copper | 4150 | LF | 4.3944 | 18236.757 | 2.9296 | 12157.838 | 7.324 | 30394.595
| TELECOMMUNICATION |  |  | 0 | 0 | 0 | 0 |  | 0
| 4" PVC SCH40 Spare (In Duct Bank Detail 7/E501) (including to MFD for each LOB Section) | 5800 | LF | 38.6087 | 223930.344 | 25.7391 | 149286.896 | 64.3478 | 373217.24
| 4" EMT From Incoming PVC to Ceiling mounted Cable Tray (4) Sets @ 15LF ea ( As per section 16774 part 2.3 note B) | 300 | LF | 32.3796 | 9713.88 | 21.5864 | 6475.92 | 53.966 | 16189.8
| Tel Manhole | 1 | EA | 4991.5404 | 4991.5404 | 3327.6936 | 3327.6936 | 8319.234 | 8319.234
| Fiber Optic Distr Cable | 4000 | LF | 10.331 | 41323.92 | 6.8873 | 27549.28 | 17.2183 | 68873.2
| Multi - Pair Cu Distr Cable | 4000 | EA | 11.4599 | 45839.64 | 7.6399 | 30559.76 | 19.0998 | 76399.4
| MISC ITEMS |  |  | 0 | 0 | 0 | 0 |  | 0
| Trench, Concrete, Backfill for All duct bank as per details | 980 | CY | 508.2 | 498036 | 338.8 | 332024 | 847 | 830060
| Allowance for electrical works for cooling tower system | 1 | LS | 21801.78 | 21801.78 | 14534.52 | 14534.52 | 36336.3 | 36336.3
| Light poles with wiring and conduit (for 2,000,000 SF of parking and road ways -Considered 1pole per 5,000SF) | 400 | EA | 4377.78 | 1751112 | 2918.52 | 1167408 | 7296.3 | 2918520
| Fire Stopping & Penetrations | 1 | LS | 17424 | 17424 | 11616 | 11616 | 29040 | 29040
[5 empty] | - |  | - |  | -
[5 empty] | 6256435.7526 |  | 4170957.1684 |  | 10427392.921 |  | 10427392.921 | 6256435.7526 | 4170957.1684
K | LN2 & GN2 DISTRIBUTION SYSTEM
| Liquid nitrogen and gas nitrogen tanks and distribution piping and valves | 1 | LS | 531000 | 531000 | 354000 | 354000 | 885000 | 885000
26279416.953
26279416.953

## TRADE-VALUE ENGINEERING
VJ ASSOCIATES
NSLS II - 90% TITLE I ESTIMATE
BROOKHAVEN NATIONAL LABORATORY
NATIONAL SYNCHROTRON LIGHT SOURCE II
UPTON, NEW YORK
2007-09-20
VALUE ENGINEERING STUDIES
TOTAL
| VE ITEM |  | AMOUNT
1 | SHELL LAB OFFICE BUILDING NO. 4 | savings | -3549711.9722 | DEDUCT
2 | LEED GOLD FOR LOB'S AND OP'S CENTER |  | HOLD
3 | REVISED LINAC LAYOUT |  | HOLD
4 | REDUCE WIDTH OF RING BUILDING BY 3'-0" |  | -824872.0852 | DEDUCT
5 | MOVE PROCESS COOLING TOWER LOCATION |  | -100740 | DEDUCT
6 | USE SHORTER UTILITY ROUTING - LOB 1 & 2 IN LIEU OF LOB 5 & 1 |  | -34500 | DEDUCT
7 | OP'S BUILDING MAIN LOBBY - TWO STORY IN LIEU OF THREE STORY |  | -179390.8 | DEDUCT
8 | REDUCE FRONT END AREA HEIGHT AT RING BUILDING BY 40 CM |  | HOLD
9 | REDUCE FLOOR SLAB THICKNESSES AT RING BUILDING |  | -1028048.1222 | DEDUCT
10 | ELIMINATE RETURN DUCT IN STORAGE RING BUILDING |  | -43125 | DEDUCT
11 | DISTRIBUTE UTILITIES AT HALF OF RING CIRCUMFERENCE |  | -227700 | DEDUCT
12 | ALTERNATE OPTION FOR FUTURE FOOTINGS AT ELEVATED WALKWAYS |  | -3513.8889 | DEDUCT
at raised platform (thicken slab vs. wall and footing)
NOTE: ABOVE VE STUDIES DO NOT INCLUDE 10% DESIGN CONTINGENCY
OR 20% ESCALATION COSTS.
-5991601.8685

## EST-VALUE ENGINEERING
VJ ASSOCIATES
BROOKHAVEN NATIONAL LABORATORY
| NATIONAL SYNCHROTRON LIGHT SOURCE II | [8 empty] | 2007-09-20
UPTON, NEW YORK
NSLS II - 90% TITLE I ESTIMATE
VALUE ENGINEERING STUDIES
VE ITEM 1 - COST OF SHELL LAB OFFICE BUILDING NO. 4
|  |  |  | LABOR |  | MATERIAL |  | TOTAL
| DESCRIPTION | QUANTITY | UNIT | UNIT PR | AMOUNT | UNIT PR | AMOUNT | UNIT PR | AMOUNT
`
2 | SITEWORK | [7 empty] | Not included
BUILDING EARTHWORK
| Building mass cut excavation and disposal on site | 950 | CY | 5.4 | 5130 | 3.6 | 3420 | 9 | 8550
| Building isolated cut excavation and disposal on site | 1400 | CY | 5.4 | 7560 | 3.6 | 5040 | 9 | 12600
| Backfill from excavated material | 900 | CY | 6 | 5400 | 4 | 3600 | 10 | 9000
| Disposal on site | 1450 | CY | 5.4 | 7830 | 3.6 | 5220 | 9 | 13050
| Crushed stone base at concrete slab on grade | 850 | CY | 21 | 17850 | 14 | 11900 | 35 | 29750
| Pumping / dewatering during construction | [7 empty] | Not included
| Provide drainage below concrete slab on grade | [7 empty] | Not included
| Misc earthwork, mechanical trenching, earth ramps, hand trim etc. | 1 | BLDG | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
[5 empty] | - |  | - |  | -
[5 empty] | 46770 |  | 31180 |  | 77950
3 | CONCRETE
FOUNDATION CONCRETE
| Concrete column footings and piers - include all formwork and reinforcing. See drawing S-103 | 92 | CY | 315 | 28980 | 210 | 19320 | 525 | 48300
| Concrete slab on grade. Include wwm and vapor barrier. 6" thick | 22800 | SF | 4.8 | 109440 | 3.2 | 72960 | 8 | 182400
| Concrete wall footings and grade beams at building perimeter | 361.0926 | CY | 315 | 113744.1667 | 210 | 75829.4444 | 525 | 189573.6111
| Misc foundation concrete | 1 | BLDG | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
SUPERSTRUCTURE CONCRETE
| Concrete fill on metal deck at attic space | [7 empty] | None required
| Misc concrete equipment pads and curbs | 1 | BLDG | 3000 | 3000 | 2000 | 2000 | 5000 | 5000
PRECAST CONCRETE
| Architectural exterior precast concrete panel at Lab office Buildings at grade. 8" x 1'-0" high. See wall section 1 - drawing A-309 | 520 | SF | 36 | 18720 | 24 | 12480 | 60 | 31200
[5 empty] | - |  | - |  | -
[5 empty] | 276884.1667 |  | 184589.4444 |  | 461473.6111
4 | MASONRY
| Cmu walls between ring building and LOB Buildings if required | 3648 | SF | 7.2 | 26265.6 | 4.8 | 17510.4 | 12 | 43776
[5 empty] | - |  | - |  | -
[5 empty] | 26265.6 |  | 17510.4 |  | 43776
5 | METALS
STRUCTURAL STEEL
| Structural steel roof framing including steel beams, columns, baseplates and windbracing. See drawings S-104 and S-105. | 174 | TON | 1980 | 344520 | 1320 | 229680 | 3300 | 574200
| Shear studs at mezzanine | 522 | EA | 2.1 | 1096.2 | 1.4 | 730.8 | 3.5 | 1827
| Moment connections | [7 empty] | None required
| Anchor bolts at column base plates | 180 | EA | 60 | 10800 | 40 | 7200 | 100 | 18000
| Grout at steel baseplates | 45 | EA | 90 | 4050 | 60 | 2700 | 150 | 6750
METAL DECK
| 1 1/2" Deep 18 Gauge Type B roof deck - no concrete fill - at main roof sloping roof | 24910 | SF | 1.65 | 41101.5 | 1.1 | 27401 | 2.75 | 68502.5
| 1 1/2" Deep 18 Gauge Type B roof deck - no concrete fill - at flat low roof | 3066 | SF | 1.5 | 4599 | 1 | 3066 | 2.5 | 7665
| 3" Deep 18 Gauge - Lok - metal deck at attic space | 4950 | SF | 2.1 | 10395 | 1.4 | 6930 | 3.5 | 17325
MISC IRONWORK
| General misc ironwork | 22800 | SF | 0.3 | 6840 | 0.2 | 4560 | 0.5 | 11400
EXTERIOR METAL PANEL WALLS
| Exterior flat metal panel sandwich wall system with liner including all supports. See wall section 1 drawing A-309. | 3400 | SF | 19.2 | 65280 | 12.8 | 43520 | 32 | 108800
| Exterior preformed metal panel sandwich wall system with liner including all supports | 1660 | SF | 19.2 | 31872 | 12.8 | 21248 | 32 | 53120
| Exterior metal panel fascia including all supports | 910 | SF | 21 | 19110 | 14 | 12740 | 35 | 31850
[5 empty] | - |  | - |  | -
[5 empty] | 539663.7 |  | 359775.8 |  | 899439.5
6 | WOOD AND PLASTICS
CARPENTRY
| Install exterior HM doors, frames and finish hardware LABOR COST ONLY | 7 | LEAF | 150 | 1050 | 0 | 0 | 150 | 1050
| Wood blocking at gravel stop at edge of low roof | 340 | LF | 12 | 4080 | 8 | 2720 | 20 | 6800
| Misc wood blocking, protection and scaffolding at Lab Building | 22800 | SF | 0.3 | 6840 | 0.2 | 4560 | 0.5 | 11400
MILLWORK
| Interior millwork allowance | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 11970 |  | 7280 |  | 19250
7 | THERMAL & MOISTURE PROTECTION
ROOFING AND FLASHING
| Sloping standing seam roofing system including rigid insulation and exterior grade gypsum board sheathing ( on metal roof deck). See drawing A-303 | 24910 | SF | 9 | 224190 | 6 | 149460 | 15 | 373650
| Flat membrane roofing system including rigid insulation at low flat roof. See drawing A-309 | 3066 | SF | 7.2 | 22075.2 | 4.8 | 14716.8 | 12 | 36792
| Metal soffit and fascia at sloping standing seam roof | 3200 | SF | 12 | 38400 | 8 | 25600 | 20 | 64000
| Metal gutter assembly at sloping standing seam roof | 320 | LF | 45 | 14400 | 30 | 9600 | 75 | 24000
| Assume gravel stop at edge of flat roofs | 340 | LF | 15 | 5100 | 10 | 3400 | 25 | 8500
| Base flashing at roof / clearstory glass intersection | 320 | LF | 15 | 4800 | 10 | 3200 | 25 | 8000
| Misc flashing at rooftop equipment curbs, thru roof vents and roof drains | 1 | BLDG | 6000 | 6000 | 4000 | 4000 | 10000 | 10000
FIRE PROOFING
| Spray on fireproofing @ beams and columns | 22800 | SF | 1.5 | 34200 | 1 | 22800 | 2.5 | 57000
INSULATION
| Misc insulation ( all wall insulation with GB ) | [7 empty] | With Exterior wall systems
CAULKING
| Include all caulking and sealants with exterior wall systems | [7 empty] | With Exterior wall systems
[5 empty] | - |  | - |  | -
[5 empty] | 349165.2 |  | 232776.8 |  | 581942
8 | DOORS AND WINDOWS / CURTAINWALL
DOORS, FRAMES AND FINISH HARDWARE
Furnish HM Exterior doors and frames
| HM doors, frames and finish hardware | 3 | EA | 1000 | 3000 | 0 | 0 | 1000 | 3000
|  | 2 | PR | 2000 | 4000 | 0 | 0 | 2000 | 4000
CURTAIN WALL
| Exterior storefront glass wall system at first floor lobby entry | 500 | SF | 66 | 33000 | 44 | 22000 | 110 | 55000
| Exterior insulated curtain wall system including all supports | 4420 | SF | 51 | 225420 | 34 | 150280 | 85 | 375700
| Exterior insulated clearstory glass wall system including all supports. 384' x 4' ht | 1536 | SF | 51 | 78336 | 34 | 52224 | 85 | 130560
| Extra cost for horizontal window louvers at first floor curtain wall | 490 | LF | 30 | 14700 | 20 | 9800 | 50 | 24500
| Extra cost for horizontal window louvers at second floor clear story | 385 | LF | 30 | 11550 | 20 | 7700 | 50 | 19250
[5 empty] | - |  | - |  | -
[5 empty] | 370006 |  | 242004 |  | 612010
9 | FINISHES
INTERIOR WALLS
| Fire rated gypsum board walls | [7 empty] | None
| Gypsum board shaft walls | 1400 | SF | 6 | 8400 | 4 | 5600 | 10 | 14000
| Gypsum board chase walls - one side at toilets | 1120 | SF | 3.6 | 4032 | 2.4 | 2688 | 6 | 6720
MISC
| Paint exterior HM doors and frames | 7 | LEAF | 39 | 273 | 26 | 182 | 65 | 455
| Misc interior painting | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 12705 |  | 8470 |  | 21175
10 | SPECIALTIES
| Door signs | 5 | EA | 90 | 450 | 60 | 300 | 150 | 750
| Misc signage | 1 | BLDG | 900 | 900 | 600 | 600 | 1500 | 1500
| Fire extinguishers - not shown allow two per floor | 6 | EA | -50 | -300 | 200 | 1200 | 150 | 900
[5 empty] | - |  | - |  | -
[5 empty] | 1050 |  | 2100 |  | 3150
11 | EQUIPMENT | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
12 | FURNISHINGS | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
13 | SPECIAL CONSTRUCTION | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 0 |  | 0 |  | None
14 | CONVEYING SYSTEMS
| Allow for metal pan fire stairs to attic including all riser / tread and platform assemblies, and stringers. | 2 | FLT | 9000 | 18000 | 6000 | 12000 | 15000 | 30000
[5 empty] | - |  | - |  | -
[5 empty] | 18000 |  | 12000 |  | 30000
15.1 | HVAC
| Provide HVAC equipment, trunk ductwork, insulation and risers, piping, controls and heating and exhaust. | 22800 | SF | 6 | 136800 | 4 | 91200 | 10 | 228000
[5 empty] | - |  | - |  | -
[5 empty] | 136800 |  | 91200 |  | 228000
15.2 | PLUMBING
| Rough in for future plumbing fixtures | 19 | EA | 300 | 5700 | 200 | 3800 | 500 | 9500
| Cold & hot water, recirc., pump, electr. DHWH, sanitary, vent, storm, traps, etc | 22800 | SF | 3 | 68400 | 2 | 45600 | 5 | 114000
| Process system piping (nitrogen, liquid nitrogen, compressed air, deionized water | [7 empty] | None
[5 empty] | - |  | - |  | -
[5 empty] | 74100 |  | 49400 |  | 123500
15.3 | FIRE PROTECTION
| Fire protection for Lab / Office Building | 22800 | SF | 2.4 | 54720 | 1.6 | 36480 | 4 | 91200
[5 empty] | - |  | - |  | -
[5 empty] | 54720 |  | 36480 |  | 91200
16 | ELECTRICAL
| Furnish & install main electric service and feeders, minimum lighting and power, fire alarm and grounding. | 22800 | SF | 7.2 | 164160 | 4.8 | 109440 | 12 | 273600
[5 empty] | - |  | - |  | -
[5 empty] | 164160 |  | 109440 |  | 273600
| SUB TOTAL - SHELL LOB |  |  |  | 2082259.6667 |  | 1384206.4444 |  | 3466466.1111
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | 519969.9167
-
| TOTAL - SHELL LOB NO. 4 | [7 empty] | 3986436.0278
| Full Buildout (typical LOB) | [7 empty] | 7536148
| savings | [7 empty] | -3549711.9722
VE ITEM 2 - LEED GOLD
| LEED to strive for minimal cost in LOB's and OP's Center and minimal cost sustainable goals in Accelerator / Experimental Bldgs. | 1 | LS | 0 | 0 | 0 | 0 |  | 0 | HOLD
| VE ITEM 3 - REVISED LINAC LAYOUT | [8 empty] | HOLD
|  |  |  | 0 | 0 | 0 |  |  | 0
|  |  |  | 0 | 0 | 0 |  |  | 0
|  |  |  | 0 | 0 | 0 |  |  | 0
[5 empty] | - |  | - |  | -
| SUB TOTAL - REVISED LINAC LAYOUT |  |  |  | 0 |  | 0 |  | 0
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | 0
-
| TOTAL - REVISED LINAC LAYOUT | [7 empty] | 0
VE ITEM 4 - REDUCE WIDTH OF RING BLDG BY 3'-0"
| Deduct building isolated cut excavation and disposal on site | -1200 | CY | 5.4 | -6480 | 3.6 | -4320 | 9 | -10800
| Deduct crushed stone base at concrete slab on grade | -325.9259 | CY | 21 | -6844.4444 | 14 | -4562.963 | 35 | -11407.4074
| Vapor barrier at concrete slab on grade | -8800 | SF | 0.15 | -1320 | 0.1 | -880 | 0.25 | -2200
Deduct concrete slab on grade. Include all reinforcing and formwork
| 1'-6" Thick - 8,800 SF | -488.8889 | CY | 315 | -154000 | 210 | -102666.6667 | 525 | -256666.6667
| Deduct misc foundation concrete | -1 | LS | 6000 | -6000 | 4000 | -4000 | 10000 | -10000
| Deduct structural steel framing including steel beams, columns, baseplates and roof trusses. | -26.12 | TON | 2280 | -59553.6 | 1520 | -39702.4 | 3800 | -99256
| Deduct -1 1/2" Deep 20 Gauge acoustic steel roof deck - no concrete fill - at main roof truss | -9000 | SF | 1.65 | -14850 | 1.1 | -9900 | 2.75 | -24750
| Allow for deduction of some exterior metal panel sandwich wall system with liner including all supports | -2000 | SF | 19.2 | -38400 | 12.8 | -25600 | 32 | -64000
| Deduct sloping standing seam roofing system including rigid insulation and exterior grade gypsum board sheathing ( on metal roof deck). | -9000 | SF | 9 | -81000 | 6 | -54000 | 15 | -135000
| Allow for deduction of some exterior soffits, fascias, gutters, flashings etc. | -1 | LS | 9000 | -9000 | 6000 | -6000 | 15000 | -15000
| Deduct concrete sealer at experimental hall | -8800 | SF | 0.9 | -7920 | 0.6 | -5280 | 1.5 | -13200
| Allow for some HVAC deductions due to decreased building volume | -1 | LS | 30000 | -30000 | 20000 | -20000 | 50000 | -50000
| Allow for some lighting and conduit run decreases | -1 | LS | 15000 | -15000 | 10000 | -10000 | 25000 | -25000
[5 empty] | - |  | - |  | -
| SUB TOTAL - REDUCE RING BLDG BY 3'-0" |  |  |  | -430368.0444 |  | -286912.0296 |  | -717280.0741
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -107592.0111
-
| TOTAL - REDUCE RING BLDG BY 3'-0" | [7 empty] | -824872.0852 | DEDUCT
VE ITEM 5 - MOVE PROCESS WATER COOLING TOWER TO INTERIOR OF RING BUILDING
| Deduct process water piping | -1 | LS | 150000 | -150000 | 100000 | -100000 | 250000 | -250000
| Add prefabricated building around cooling tower. Include exhaust louvers in exterior façade. 40' x 70' building. | 2800 | SF | 24 | 67200 | 16 | 44800 | 40 | 112000
| Add lighting at prefab building | 2800 | SF | 3 | 8400 | 2 | 5600 | 5 | 14000
| Add drainage at prefab building | 2800 | SF | 7.8 | 21840 | 5.2 | 14560 | 13 | 36400
[5 empty] | - |  | - |  | -
| SUB TOTAL - MOVE PROCESS COOLING TOWER |  |  |  | -52560 |  | -35040 |  | -87600
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -13140
-
| TOTAL - MOVE PROCESS COOLING TOWER | [7 empty] | -100740 | DEDUCT
VE ITEM 6 - USE SHORTER UTILITY ROUTING - LOB1&2 IN LIEU OF LOB 5&1
| Use shorter utility routing. Bring utilities between LOB-1 and LOB-2 instead of LOB-5 and LOB-1. | -1 | LS | 18000 | -18000 | 12000 | -12000 | 30000 | -30000
[5 empty] | - |  | - |  | -
| SUB TOTAL - SHORTER UTILITY ROUTING |  |  |  | -18000 |  | -12000 |  | -30000
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -4500
-
| TOTAL - SHORTER UTILITY ROUTING | [7 empty] | -34500 | DEDUCT
VE ITEM 7 - OP'S BLDG MAIN LOBBY - 2 STORY IN LIEU OF 3 STORY
| Deduct exterior glass curtain wall | -1064 | SF | 51 | -54264 | 34 | -36176 | 85 | -90440
| Deduct exterior metal panel sandwich wall system with liner including all supports | -1736 | SF | 19.2 | -33331.2 | 12.8 | -22220.8 | 32 | -55552
| Deduct structural columns at reduced height roof | -1 | LS | 6000 | -6000 | 4000 | -4000 | 10000 | -10000
[5 empty] | - |  | - |  | -
| SUB TOTAL - MAIN LOBBY - 2 STORY IN LIEU OF 3 STORY |  |  |  | -93595.2 |  | -62396.8 |  | -155992
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -23398.8
-
| TOTAL - MAIN LOBBY - 2 STORY IN LIEU OF 3 STORY | [7 empty] | -179390.8 | DEDUCT
| VE ITEM 8 - REDUCE FRONT END AREA HT BY 40 CM | [8 empty] | HOLD
|  |  |  | 0 | 0 | 0 |  |  | 0
|  |  |  | 0 | 0 | 0 |  |  | 0
|  |  |  | 0 | 0 | 0 |  |  | 0
|  |  |  | 0 | 0 | 0 |  |  | 0
[5 empty] | - |  | - |  | -
| SUB TOTAL - REDUCE FRONT END AREA HT BY 40 CM. |  |  |  | 0 |  | 0 |  | 0
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | 0
-
| TOTAL - REDUCE FRONT END AREA HT BY 40 CM. | [7 empty] | 0
VE ITEM 9 - REDUCE THICKNESS OF FLOOR SLAB IN EXPERIMENTAL AREA
TO 15" AND IN STORAGE RING TUNNEL TO 36"
Concrete slab on grade. Include all reinforcing and formwork at Experimental Hall
| Deduct 1'-6" Thick - 131,000 SF | -7277.7778 | CY | 315 | -2292500 | 210 | -1528333.3333 | 525 | -3820833.3333
| Add 1'-3" Thick - 131,000 SF | 6064.8148 | CY | 315 | 1910416.6667 | 210 | 1273611.1111 | 525 | 3184027.7778
Concrete slab on grade. Include all reinforcing and formwork at Storage Ring Tunnel
| Deduct 3'-3" Thick - 49,800 SF | -5994.4444 | CY | 315 | -1888250 | 210 | -1258833.3333 | 525 | -3147083.3333
| Add 3'-0" Thick - 49,800 SF | 5533.3333 | CY | 315 | 1743000 | 210 | 1162000 | 525 | 2905000
| Deduct building isolated cut excavation and disposal on site | -1674 | CY | 5.4 | -9039.6 | 3.6 | -6026.4 | 9 | -15066
[5 empty] | - |  | - |  | -
| SUB TOTAL - REDUCE FLOOR SLAB THICKNESS |  |  |  | -536372.9333 |  | -357581.9556 |  | -893954.8889
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -134093.2333
-
| TOTAL - REDUCE FLOOR SLAB THICKNESS | [7 empty] | -1028048.1222 | DEDUCT
VE ITEM 10 - ELIMINATE RETURN DUCT IN STORAGE RING TUNNEL
| Eliminate HVAC return duct in storage ring tunnel. Use common return near each service building. | -1 | LS | 22500 | -22500 | 15000 | -15000 | 37500 | -37500
[5 empty] | - |  | - |  | -
| SUB TOTAL - ELIMINATE DUCT IN RING TUNNEL |  |  |  | -22500 |  | -15000 |  | -37500
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -5625
-
| TOTAL - ELIMINATE DUCT IN RING TUNNEL | [7 empty] | -43125 | DEDUCT
VE ITEM 11 - DISTRIBUTE UTILITIES AT HALF OF RING CIRCUMFERENCE
Distribute beamline utilities only around half of ring circumference from BL 15A thru BL 30A.
| Delete ductwork | -1 | LS | 57000 | -57000 | 38000 | -38000 | 95000 | -95000
| Deduct deionized water piping | -1 | LS | 16800 | -16800 | 11200 | -11200 | 28000 | -28000
| Deduct potable water piping | -1 | LS | 24000 | -24000 | 16000 | -16000 | 40000 | -40000
| Deduct Liquified nitrogen piping | -1 | LS | 9000 | -9000 | 6000 | -6000 | 15000 | -15000
| Deduct Gaseous nitrogen piping | -1 | LS | 12000 | -12000 | 8000 | -8000 | 20000 | -20000
[5 empty] | - |  | - |  | -
| SUB TOTAL - DISTRIBUTE UTILITIES AT HALF OF RING CIRCUMFERENCE |  |  |  | -118800 |  | -79200 |  | -198000
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -29700
-
| TOTAL - DISTRIBUTE UTILITIES AT HALF OF RING CIRCUMFERENCE | [7 empty] | -227700 | DEDUCT
VE ITEM 12 - ALTERNATE OPTION FOR FUTURE FOOTINGS AT ELEVATED WALKWAY
| Delete 2' x 1' concrete footings and 1' x 1'-6" grade beam at two future elevated platform locations at Ring Building as shown on drawing A101-A OPT. | -88.8889 | CY | 330 | -29333.3333 | 220 | -19555.5556 | 550 | -48888.8889
| Add 36" x 30" deep mass footing at two future elevated platform locations at Ring Building as shown on drawing A101-A OPT. | 83.3333 | CY | 330 | 27500 | 220 | 18333.3333 | 550 | 45833.3333
[5 empty] | - |  | - |  | -
| SUB TOTAL |  |  |  | -1833.3333 |  | -1222.2222 |  | -3055.5556
| GEN. CONDITIONS, OVERHEAD & PROFIT |  | 15% | [5 empty] | -458.3333
-
| TOTAL - ALTERNATE OPTION FOR ELEVATED WALKWAY FOOTINGS | [7 empty] | -3513.8889 | DEDUCT