## Table
Top 4 Bituminous |  | Top 4 Subbituminous |  | Top 5 Lignite |  | Top Waste |  | Top IGCC
Mecklenburg Cogeneration | GEN 1 | AES Hawaii, Inc. | A | R.M. Heskett Station | B2 | Kline Township Cogen Facility | GEN1 | Wabash River Generating Station | 1 + 1A
Dwayne Collier Battle Cogen | 2B | Clay Boswell | 2 | Antelope Valley Station | B1 | Scrubgrass Generating | GEN1 | Polk Power | 1
Valmont | 5 | Craig | C3 | Leland Olds Station | 2
Stockton | 1 | Cholla | 3 | Stanton Station | 10
|  |  |  | Stanton Station | 1

## MACTepa
Scenario | MACT Floor (lb/TBtu)
Top 4 Bit. | 1.9679
Top 4 Sub. | 5.7707
Top 5 Lignite | 9.2432

## Lig
MACT Analysis for Top 5 Lignite Units - 97.5th Percentile Values
Plant | Unit | Particulate Control | SO2 Control | Measured Fraction Hg Removal | Correlation Used? (Y/N) | "Alpha" | "Beta" | Measured lb/TBtu | 97.5th Percentile, lb/TBtu
R.M. Heskett Station | B2 | ESP- CS | FBC | 0.4036 | N | 0 | 0.5964 | 3.9768 | 7.7985
Antelope Valley Station | B1 | BAGHOUSE | SDA | 0.3333 | Y | 0.002164 | 0.81882 | 4.0042 | 7.087
Leland Olds Station | 2 | ESP- CS | NONE | 0.0487 | N | 0 | 0.9513 | 4.0233 | 9.5323
Stanton Station | 10 | BAGHOUSE | SDA | 0.0147 | Y | 0.002164 | 0.81882 | 6.2517 | 8.0289
Stanton Station | 1 | ESP- CS | NONE | 0.4409 | N | 0 | 0.5591 | 6.9024 | 6.3056
Mean | [7 empty] | 5.0317 | 7.7505
Standard Deviation | [7 empty] | 1.4295 | 1.2024
UCL97.5 of the Mean | [7 empty] | 6.8063 | 9.2432

## Sub
MACT Analysis for Top 4 Subbituminous Units - 97.5th Percentile Values
Plant | Unit | Particulate Control | SO2 Control | Measured Fraction Hg Removal | Correlation Used? (Y/N) | "Alpha" | "Beta" | Measured lb/TBtu | 97.5th Percentile, lb/TBtu
AES Hawaii, Inc. | A | BAGHOUSE | FBC | 0.5252 | N | 0 | 0.4748 | 0.4606 | 2.1349
Clay Boswell | 2 | BAGHOUSE | COMP COAL | 0.8257 | N | 0 | 0.1743 | 0.6633 | 1.9912
Craig | C3 | BAGHOUSE | SDA | 0.336 | N | 0 | 0.664 | 0.7248 | 2.6351
Cholla | 3 | ESP- HS | NONE | 0.642 | N | 0 | 0.358 | 1.2066 | 5.583
Mean | [7 empty] | 0.76382 | 3.0861
Standard Deviation | [7 empty] | 0.31603 | 1.6874
UCL97.5 of the Mean | [7 empty] | 1.2666 | 5.7707

## Bit
MACT Analysis for Top 4 Bituminous Units - 97.5th Percentile Values
Plant | Unit | Particulate Control | SO2 Control | Measured Fraction Hg Removal | Correlation Used? (Y/N) | "Alpha" | "Beta" | Measured lb/Tbtu | 97.5th Percentile, lb/TBtu
Mecklenburg Cogeneration Facility | GEN 1 | BAGHOUSE | SDA | 0.9881 | Y | 0.002164 | 0.81882 | 0.1062 | 1.8051
Dwayne Collier Battle Cogeneration Facility | 2B | BAGHOUSE | SDA | 0.9366 | Y | 0.002164 | 0.81882 | 0.1074 | 1.2376
Valmont | 5 | BAGHOUSE | COMP COAL | 0.8652 | N | 0 | 0.1348 | 0.1268 | 0.69439
Stockton | 1 | BAGHOUSE | FBC/SNCR | 0.9182 | Y | 0.0068608 | 0.31857 | 0.1316 | 0.60945
Mean | [7 empty] | 0.118 | 1.0866
Standard Deviation | [7 empty] | 0.013089 | 0.55392
UCL97.5 of the Mean | [7 empty] | 0.13883 | 1.9679

## Waste
MACT Analysis for Top Waste Coal Units - 97.5th Percentile
Plant | Unit | Particulate Control | SO2 Control | Measured Fraction Hg Removal | Correlation Used? (Y/N) | "Alpha" | "Beta" | Measured lb Hg/Tbtu | 97.5th Percentile lb Hg/TBtu
Kline Township Cogen Facility | GEN1 | BAGHOUSE | FBC | 0.9975 | N | 0 | 0.0025 | 0.0816 | 0.11823
Scrubgrass Generating Company L. P. | GEN1 | BAGHOUSE | FBC | 0.9989 | N | 0 | 0.011 | 0.0936 | 0.15715
Mean | [7 empty] | 0.0876 | 0.13769
Standard Deviation | [7 empty] | 0.0084853 | 0.027524
UCL97.5 of the Mean | [7 empty] | 0.16384 | 0.38498

## IGCC
MACT Analysis for Top IGCC Units - 97.5th Percentile
Plant | Unit | Particulate Control | SO2 Control | Measured Fraction Hg Removal | Correlation Used? (Y/N) | "Alpha" | "Beta" | Measured lb/Tbtu | 97.5th Percentile lb/TBtu
Wabash River Generating Station | 1 + 1A | COAL GAS | COAL GAS | 0.3253 | N | 0 | 0.6747 | 5.3343 | 7.335
Polk Power | 1 | COAL GAS | COAL GAS | 0.3399 | N | 0 | 0.6601 | 5.4713 | 5.392
Mean | [7 empty] | 5.4028 | 6.3635
Standard Deviation | [7 empty] | 0.096874 | 1.374
UCL97.5 of the Mean | [7 empty] | 6.2732 | 18.708

## Summary
MACT Analysis for Top 4 Bituminous Units - 97.5th Percentile Values
Plant | Unit | Particulate control | SO2 Control | Measured fraction Hg removal | Correlation used? (Y/N) | "Alpha" | "Beta" | Measured lb/TBtu | 97.5th Percentile, lb/TBtu
Mecklenburg Cogeneration Facility | GEN 1 | BAGHOUSE | SDA | 0.9881 | Y | 0.002164 | 0.81882 | 0.1062 | 1.8051
Dwayne Collier Battle Cogeneration Facility | 2B | BAGHOUSE | SDA | 0.9366 | Y | 0.002164 | 0.81882 | 0.1074 | 1.2376
Valmont | 5 | BAGHOUSE | COMP COAL | 0.8652 | N | 0 | 0.1348 | 0.1268 | 0.69439
Stockton | 1 | BAGHOUSE | FBC/SNCR | 0.9182 | Y | 0.0068608 | 0.31857 | 0.1316 | 0.60945
Mean | [7 empty] | 0.118 | 1.0866
Standard Deviation | [7 empty] | 0.013089 | 0.55392
UCL97.5 of the Mean | [7 empty] | 0.13883 | 1.9679
MACT Analysis for Top 4 Subbituminous Units - 97.5th Percentile Values
Plant | Unit | Particulate control | SO2 Control | Measured fraction Hg removal | Correlation used? (Y/N) | "Alpha" | "Beta" | Measured lb/TBtu | 97.5th Percentile, lb/TBtu
AES Hawaii, Inc. | A | BAGHOUSE | FBC | 0.5252 | N | 0 | 0.4748 | 0.4606 | 2.1349
Clay Boswell | 2 | BAGHOUSE | COMP COAL | 0.8257 | N | 0 | 0.1743 | 0.6633 | 1.9912
Craig | C3 | BAGHOUSE | SDA | 0.336 | N | 0 | 0.664 | 0.7248 | 2.6351
Cholla | 3 | ESP- HS | NONE | 0.642 | N | 0 | 0.358 | 1.2066 | 5.583
Mean | [7 empty] | 0.76382 | 3.0861
Standard Deviation | [7 empty] | 0.31603 | 1.6874
UCL97.5 of the Mean | [7 empty] | 1.2666 | 5.7707
MACT Analysis for Top 5 Lignite Units - 97.5th Percentile Values
Plant | Unit | Particulate control | SO2 Control | Measured fraction Hg removal | Correlation used? (Y/N) | "Alpha" | "Beta" | Measured lb/TBtu | 97.5th Percentile, lb/TBtu
R.M. Heskett Station | B2 | ESP- CS | FBC | 0.4036 | N | 0 | 0.5964 | 3.9768 | 7.7985
Antelope Valley Station | B1 | BAGHOUSE | SDA | 0.3333 | Y | 0.002164 | 0.81882 | 4.0042 | 7.087
Leland Olds Station | 2 | ESP- CS | NONE | 0.0487 | N | 0 | 0.9513 | 4.0233 | 9.5323
Stanton Station | 10 | BAGHOUSE | SDA | 0.0147 | Y | 0.002164 | 0.81882 | 6.2517 | 8.0289
Stanton Station | 1 | ESP- CS | NONE | 0.4409 | N | 0 | 0.5591 | 6.9024 | 6.3056
Mean | [7 empty] | 5.0317 | 7.7505
Standard Deviation | [7 empty] | 1.4295 | 1.2024
UCL97.5 of the Mean | [7 empty] | 6.8063 | 9.2432
MACT Analysis for Top Waste Coal Units - 97.5th Percentile
Plant | Unit | Particulate control | SO2 Control | Measured fraction Hg removal | Correlation used? (Y/N) | "Alpha" | "Beta" | Measured lb/TBtu | 97.5th Percentile, lb/TBtu
Kline Township Cogen Facility | GEN1 | BAGHOUSE | FBC | 0.9975 | N | 0 | 0.0025 | 0.0816 | 0.11823
Scrubgrass Generating Company L. P. | GEN1 | BAGHOUSE | FBC | 0.9989 | N | 0 | 0.011 | 0.0936 | 0.15715
Mean | [7 empty] | 0.0876 | 0.13769
Standard Deviation | [7 empty] | 0.0084853 | 0.027524
UCL97.5 of the Mean | [7 empty] | 0.16384 | 0.38498
MACT Analysis for Top IGCC Units - 97.5th Percentile
Plant | Unit | Particulate control | SO2 Control | Measured fraction Hg removal | Correlation used? (Y/N) | "Alpha" | "Beta" | Measured lb/TBtu | 97.5th Percentile, lb/TBtu
Wabash River Generating Station | 1 + 1A | COAL GAS | COAL GAS | 0.3253 | N | 0 | 0.6747 | 5.3343 | 7.335
Polk Power | 1 | COAL GAS | COAL GAS | 0.3399 | N | 0 | 0.6601 | 5.4713 | 5.392
Mean | [7 empty] | 5.4028 | 6.3635
Standard Deviation | [7 empty] | 0.096874 | 1.374
UCL97.5 of the Mean | [7 empty] | 6.2732 | 18.708

## Mecklenburg
Mecklenburg 1
ALPHA | BETA
0.002164 | 0.81882
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
13075 | 0.2 | 1000 | 1.4387 | 0.025641 | 1 | 0.0067937 | 1.7563 | 38 | 0.97436
13081 | 0.18 | 1000 | 1.2942 | 0.051282 | 2 | 0.021009 | 3.7063 | 39 | 1
13480 | 0.07 | 1300 | 0.25517 | 0.076923 | 3 | 0.036454 | 97.5th Percentile | 1.8051
13480 | 0.05 | 1400 | 0.1468 | 0.10256 | 4 | 0.037333
13489 | 0.1 | 1400 | 0.2934 | 0.12821 | 5 | 0.044094 | Graph Title | Mecklenburg 1: 97.5th Percentile = 1.8051 lb Hg/TBtu
13489 | 0.07 | 1700 | 0.1073 | 0.15385 | 6 | 0.049797
13433 | 0.1 | 2000 | 0.080423 | 0.17949 | 7 | 0.059756
13433 | 0.05 | 2300 | 0.021009 | 0.20513 | 8 | 0.062485
13432 | 0.09 | 1700 | 0.13855 | 0.23077 | 9 | 0.062992
13607 | 0.09 | 2300 | 0.037333 | 0.25641 | 10 | 0.069559
13607 | 0.06 | 2900 | 0.0067937 | 0.28205 | 11 | 0.076765
13457 | 0.07 | 1700 | 0.10756 | 0.30769 | 12 | 0.076872
13457 | 0.07 | 2200 | 0.036454 | 0.33333 | 13 | 0.080423
12896 | 0.09 | 600 | 1.5599 | 0.35897 | 14 | 0.095678
12898 | 0.09 | 200 | 3.7063 | 0.38462 | 15 | 0.1073
13098 | 0.08 | 700 | 1.0995 | 0.41026 | 16 | 0.10756
13098 | 0.09 | 538 | 1.7563 | 0.4359 | 17 | 0.10789
13570 | 0.14 | 1100 | 0.78151 | 0.46154 | 18 | 0.11088
13892 | 0.06 | 1600 | 0.11088 | 0.48718 | 19 | 0.13257
13892 | 0.09 | 1800 | 0.10789 | 0.51282 | 20 | 0.13855
13866 | 0.09 | 1200 | 0.396 | 0.53846 | 21 | 0.1468
13925 | 0.1 | 2100 | 0.062485 | 0.5641 | 22 | 0.21687
13925 | 0.08 | 1800 | 0.095678 | 0.58974 | 23 | 0.25517
13813 | 0.1 | 2100 | 0.062992 | 0.61538 | 24 | 0.2617
13813 | 0.07 | 2100 | 0.044094 | 0.64103 | 25 | 0.2934
13978 | 0.09 | 2000 | 0.069559 | 0.66667 | 26 | 0.29584
13959 | 0.08 | 1900 | 0.076872 | 0.69231 | 27 | 0.396
13373 | 0.09 | 600 | 1.5042 | 0.71795 | 28 | 0.45492
13611 | 0.09 | 1400 | 0.2617 | 0.74359 | 29 | 0.59203
13711 | 0.08 | 900 | 0.68135 | 0.76923 | 30 | 0.59216
13556 | 0.07 | 1600 | 0.13257 | 0.79487 | 31 | 0.68135
13595 | 0.06 | 1300 | 0.21687 | 0.82051 | 32 | 0.78151
13313 | 0.19 | 1500 | 0.45492 | 0.84615 | 33 | 1.0995
13397 | 0.13 | 1200 | 0.59203 | 0.87179 | 34 | 1.2942
13468 | 0.06 | 1900 | 0.059756 | 0.89744 | 35 | 1.4387
13468 | 0.05 | 1700 | 0.076765 | 0.92308 | 36 | 1.5042
13468 | 0.05 | 1900 | 0.049797 | 0.94872 | 37 | 1.5599
13367 | 0.2 | 1400 | 0.59216 | 0.97436 | 38 | 1.7563
13378 | 0.1 | 1400 | 0.29584 | 1 | 39 | 3.7063

## DwayneCollier
Dwayne Collier 2B
ALPHA | BETA
0.002164 | 0.81882
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
13792 | 0.03 | 1300 | 0.10689 | 0.018519 | 1 | 0.031062 | 0.6258 | 52 | 0.96296
14072 | 0.04 | 1600 | 0.072977 | 0.037037 | 2 | 0.046056 | 1.567 | 53 | 0.98148
13710 | 0.06 | 1200 | 0.26701 | 0.055556 | 3 | 0.047568 | 97.5th Percentile | 1.2376
13738 | 0.07 | 1200 | 0.31087 | 0.074074 | 4 | 0.056135
13699 | 0.04 | 1100 | 0.22119 | 0.092593 | 5 | 0.072977 | Graph Title | Dwayne Collier 2B: 97.5th Percentile = 1.2376 lb Hg/TBtu
13946 | 0.07 | 1000 | 0.47208 | 0.11111 | 6 | 0.073832
13767 | 0.17 | 2400 | 0.056135 | 0.12963 | 7 | 0.082891
14099 | 0.05 | 1900 | 0.047568 | 0.14815 | 8 | 0.090479
13786 | 0.12 | 700 | 1.567 | 0.16667 | 9 | 0.093746
13736 | 0.16 | 1300 | 0.57238 | 0.18519 | 10 | 0.10689
13731 | 0.08 | 1100 | 0.44134 | 0.2037 | 11 | 0.11002
13780 | 0.11 | 1500 | 0.25445 | 0.22222 | 12 | 0.11562
14074 | 0.06 | 2000 | 0.046056 | 0.24074 | 13 | 0.13393
13815 | 0.08 | 1100 | 0.43866 | 0.25926 | 14 | 0.14188
13785 | 0.05 | 1500 | 0.11562 | 0.27778 | 15 | 0.14587
13693 | 0.05 | 1600 | 0.093746 | 0.2963 | 16 | 0.17724
13398 | 0.06 | 1400 | 0.17724 | 0.31481 | 17 | 0.17755
13770 | 0.07 | 1300 | 0.2498 | 0.33333 | 18 | 0.17914
13838 | 0.05 | 1300 | 0.17755 | 0.35185 | 19 | 0.20336
13819 | 0.08 | 1400 | 0.22912 | 0.37037 | 20 | 0.21549
13687 | 0.11 | 1300 | 0.39492 | 0.38889 | 21 | 0.22119
14235 | 0.08 | 1500 | 0.17914 | 0.40741 | 22 | 0.22912
13726 | 0.11 | 1100 | 0.60707 | 0.42593 | 23 | 0.24949
13475 | 0.04 | 1300 | 0.14587 | 0.44444 | 24 | 0.2498
13767 | 0.1 | 1200 | 0.44317 | 0.46296 | 25 | 0.25098
13886 | 0.13 | 1300 | 0.46004 | 0.48148 | 26 | 0.25445
13734 | 0.13 | 1400 | 0.37462 | 0.5 | 27 | 0.25873
14202 | 0.08 | 1000 | 0.5298 | 0.51852 | 28 | 0.25996
13724 | 0.22 | 900 | 1.8719 | 0.53704 | 29 | 0.26701
14033 | 0.05 | 800 | 0.5166 | 0.55556 | 30 | 0.27211
13702 | 0.09 | 1400 | 0.25996 | 0.57407 | 31 | 0.27794
13787 | 0.07 | 1300 | 0.24949 | 0.59259 | 32 | 0.31087
14063 | 0.1 | 1834 | 0.11002 | 0.61111 | 33 | 0.32026
13762 | 0.07 | 1100 | 0.3853 | 0.62963 | 34 | 0.37462
14092 | 0.04 | 1500 | 0.090479 | 0.64815 | 35 | 0.3853
14022 | 0.07 | 1000 | 0.46952 | 0.66667 | 36 | 0.38859
14006 | 0.05 | 2100 | 0.031062 | 0.68519 | 37 | 0.39492
13969 | 0.1 | 1200 | 0.43676 | 0.7037 | 38 | 0.40165
14061 | 0.04 | 1100 | 0.21549 | 0.72222 | 39 | 0.42923
13627 | 0.05 | 1100 | 0.27794 | 0.74074 | 40 | 0.43676
14003 | 0.05 | 1700 | 0.073832 | 0.75926 | 41 | 0.43866
14007 | 0.07 | 900 | 0.58359 | 0.77778 | 42 | 0.44134
13623 | 0.07 | 1400 | 0.20336 | 0.7963 | 43 | 0.44317
13901 | 0.06 | 800 | 0.6258 | 0.81481 | 44 | 0.46004
14064 | 0.07 | 1800 | 0.082891 | 0.83333 | 45 | 0.46952
13705 | 0.07 | 1300 | 0.25098 | 0.85185 | 46 | 0.47208
13910 | 0.11 | 1300 | 0.38859 | 0.87037 | 47 | 0.5166
14050 | 0.06 | 1000 | 0.40165 | 0.88889 | 48 | 0.5298
13947 | 0.05 | 1400 | 0.14188 | 0.90741 | 49 | 0.57238
13809 | 0.09 | 1300 | 0.32026 | 0.92593 | 50 | 0.58359
13919 | 0.05 | 1100 | 0.27211 | 0.94444 | 51 | 0.60707
13603 | 0.05 | 900 | 0.42923 | 0.96296 | 52 | 0.6258
13767 | 0.09 | 1400 | 0.25873 | 0.98148 | 53 | 1.567
14045 | 0.02 | 1000 | 0.13393 | 1 | 54 | 1.8719

## Valmont
Valmont 5
ALPHA | BETA
0 | 0.1348
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
12376 | 0.058 | 447 | 0.63174 | 0.052632 | 1 | 0.12901 | 0.68059 | 18 | 0.94737
12539 | 0.012 | 491 | 0.12901 | 0.10526 | 2 | 0.19196 | 0.70686 | 19 | 1
12484 | 0.051 | 449 | 0.55069 | 0.15789 | 3 | 0.21556 | 97.5th Percentile | 0.69439
12555 | 0.053 | 476 | 0.56905 | 0.21053 | 4 | 0.2895
12572 | 0.027 | 712 | 0.2895 | 0.26316 | 5 | 0.30089 | Graph Title | Valmont 5: 97.5th Percentile = 0.6944 lb Hg/TBtu
12502 | 0.03 | 501 | 0.32347 | 0.31579 | 6 | 0.30808
12544 | 0.028 | 565 | 0.30089 | 0.36842 | 7 | 0.32347
12526 | 0.063 | 423 | 0.67798 | 0.42105 | 8 | 0.36695
12423 | 0.038 | 516 | 0.41233 | 0.47368 | 9 | 0.37241
12669 | 0.035 | 435 | 0.37241 | 0.52632 | 10 | 0.37386
12676 | 0.064 | 662 | 0.68059 | 0.57895 | 11 | 0.40116
12777 | 0.067 | 610 | 0.70686 | 0.63158 | 12 | 0.41233
12689 | 0.029 | 1008 | 0.30808 | 0.68421 | 13 | 0.4179
12640 | 0.018 | 821 | 0.19196 | 0.73684 | 14 | 0.55069
12259 | 0.034 | 812 | 0.37386 | 0.78947 | 15 | 0.56905
12490 | 0.034 | 696 | 0.36695 | 0.84211 | 16 | 0.63174
12507 | 0.02 | 545 | 0.21556 | 0.89474 | 17 | 0.67798
12580 | 0.039 | 560 | 0.4179 | 0.94737 | 18 | 0.68059
12769 | 0.038 | 613 | 0.40116 | 1 | 19 | 0.70686

## Stockton
Stockton Cogen 1
ALPHA | BETA
0.0068608 | 0.31857
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
12323 | 0.046 | 460 | 0.050656 | 0.025 | 1 | 0.0051235 | 0.60945 | 39 | 0.975
12323 | 0.014 | 462 | 0.015207 | 0.05 | 2 | 0.0085902 | 0.62972 | 40 | 1
11678 | 0.052 | 222 | 0.30929 | 0.075 | 3 | 0.0096139 | 97.5th Percentile | 0.60945
11678 | 0.007 | 222 | 0.041636 | 0.1 | 4 | 0.0099676
12408 | 0.04 | 152 | 0.36196 | 0.125 | 5 | 0.011655 | Graph Title | Stockton Cogen 1: 97.5th Percentile = 0.6095 lb Hg/TBtu
12408 | 0.008 | 538 | 0.0051235 | 0.15 | 6 | 0.012109
12408 | 0.008 | 441 | 0.0099676 | 0.175 | 7 | 0.012451
12403 | 0.012 | 240 | 0.059396 | 0.2 | 8 | 0.015207
12403 | 0.014 | 400 | 0.023119 | 0.225 | 9 | 0.019066
12632 | 0.039 | 199 | 0.25111 | 0.25 | 10 | 0.022355
12632 | 0.029 | 188 | 0.20136 | 0.275 | 11 | 0.023119
11741 | 0.095 | 373 | 0.19945 | 0.3 | 12 | 0.034724
12847 | 0.052 | 510 | 0.038977 | 0.325 | 13 | 0.037161
11677 | 0.046 | 484 | 0.045343 | 0.35 | 14 | 0.038977
12161 | 0.026 | 498 | 0.022355 | 0.375 | 15 | 0.041636
12219 | 0.02 | 554 | 0.011655 | 0.4 | 16 | 0.041999
12534 | 0.026 | 633 | 0.0085902 | 0.425 | 17 | 0.045343
12562 | 0.065 | 263 | 0.27129 | 0.45 | 18 | 0.050359
12074 | 0.052 | 526 | 0.037161 | 0.475 | 19 | 0.050656
11751 | 0.043 | 425 | 0.063135 | 0.5 | 20 | 0.059396
11573 | 0.076 | 175 | 0.62972 | 0.525 | 21 | 0.063135
11546 | 0.063 | 164 | 0.56424 | 0.55 | 22 | 0.065118
12768 | 0.066 | 229 | 0.34222 | 0.575 | 23 | 0.066545
13063 | 0.117 | 225 | 0.60945 | 0.6 | 24 | 0.071412
12736 | 0.053 | 167 | 0.42156 | 0.625 | 25 | 0.08968
12970 | 0.03 | 240 | 0.142 | 0.65 | 26 | 0.12919
12407 | 0.056 | 515 | 0.041999 | 0.675 | 27 | 0.142
12988 | 0.019 | 187 | 0.12919 | 0.7 | 28 | 0.19945
11566 | 0.042 | 194 | 0.30565 | 0.725 | 29 | 0.20136
11327 | 0.023 | 288 | 0.08968 | 0.75 | 30 | 0.25111
12257 | 0.039 | 200 | 0.25702 | 0.775 | 31 | 0.25702
12481 | 0.017 | 263 | 0.071412 | 0.8 | 32 | 0.27129
12382 | 0.011 | 211 | 0.066545 | 0.825 | 33 | 0.30565
12935 | 0.026 | 612 | 0.0096139 | 0.85 | 34 | 0.30929
12429 | 0.021 | 549 | 0.012451 | 0.875 | 35 | 0.34222
11790 | 0.03 | 405 | 0.050359 | 0.9 | 36 | 0.36196
11997 | 0.03 | 365 | 0.065118 | 0.925 | 37 | 0.42156
10568 | 0.076 | 698 | 0.019066 | 0.95 | 38 | 0.56424
11339 | 0.09 | 625 | 0.034724 | 0.975 | 39 | 0.60945
12396 | 0.036 | 632 | 0.012109 | 1 | 40 | 0.62972

## AESHawaii
AES Hawaii A
ALPHA | BETA
0 | 0.4748
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
11110 | 0.05 | 100 | 2.1368 | 0.02381 | 1 | 0.73243 | 2.099 | 40 | 0.95238
11310 | 0.05 | 100 | 2.099 | 0.047619 | 2 | 0.73516 | 2.1368 | 41 | 0.97619
10840 | 0.05 | 100 | 2.19 | 0.071429 | 3 | 0.73721 | 97.5th Percentile | 2.1349
12431 | 0.02 | 0 | 0.7639 | 0.095238 | 4 | 0.73847
12133 | 0.03 | 0 | 1.174 | 0.11905 | 5 | 0.73905 | Graph Title | AES Hawaii A: 97.5th Percentile = 2.1349 lb Hg/TBtu
12859 | 0.02 | 0 | 0.73847 | 0.14286 | 6 | 0.74037
12511 | 0.03 | 0 | 1.1385 | 0.16667 | 7 | 0.74438
12566 | 0.02 | 0 | 0.75569 | 0.19048 | 8 | 0.74789
12345 | 0.03 | 50 | 1.1538 | 0.21429 | 9 | 0.75204
12425 | 0.03 | 50 | 1.1464 | 0.2381 | 10 | 0.75569
12362 | 0.02 | 60 | 0.76816 | 0.2619 | 11 | 0.75956
12471 | 0.02 | 50 | 0.76145 | 0.28571 | 12 | 0.75992
12263 | 0.03 | 50 | 1.1615 | 0.30952 | 13 | 0.76145
12527 | 0.03 | 50 | 1.1371 | 0.33333 | 14 | 0.7639
12051 | 0.03 | 50 | 1.182 | 0.35714 | 15 | 0.76816
12965 | 0.02 | 50 | 0.73243 | 0.38095 | 16 | 0.77474
12825 | 0.03 | 50 | 1.1106 | 0.40476 | 17 | 1.0826
13157 | 0.03 | 50 | 1.0826 | 0.42857 | 18 | 1.1106
12697 | 0.02 | 101 | 0.74789 | 0.45238 | 19 | 1.1171
12751 | 0.03 | 68 | 1.1171 | 0.47619 | 20 | 1.1203
12684 | 0.03 | 57 | 1.123 | 0.5 | 21 | 1.123
12826 | 0.02 | 111 | 0.74037 | 0.52381 | 22 | 1.1259
12269 | 0.03 | 61 | 1.161 | 0.54762 | 23 | 1.1281
12849 | 0.02 | 50 | 0.73905 | 0.57143 | 24 | 1.1327
12257 | 0.02 | 62 | 0.77474 | 0.59524 | 25 | 1.1335
12715 | 0.03 | 50 | 1.1203 | 0.61905 | 26 | 1.1357
12575 | 0.03 | 70 | 1.1327 | 0.64286 | 27 | 1.1371
12422 | 0.03 | 97 | 1.1467 | 0.66667 | 28 | 1.1385
12292 | 0.04 | 159 | 1.5451 | 0.69048 | 29 | 1.1464
12627 | 0.03 | 53 | 1.1281 | 0.71429 | 30 | 1.1465
12917 | 0.02 | 50 | 0.73516 | 0.7381 | 31 | 1.1467
12330 | 0.03 | 58 | 1.1552 | 0.7619 | 32 | 1.1517
12651 | 0.03 | 50 | 1.1259 | 0.78571 | 33 | 1.1538
12566 | 0.03 | 67 | 1.1335 | 0.80952 | 34 | 1.1552
12881 | 0.02 | 52 | 0.73721 | 0.83333 | 35 | 1.161
12757 | 0.02 | 50 | 0.74438 | 0.85714 | 36 | 1.1615
12496 | 0.02 | 103 | 0.75992 | 0.88095 | 37 | 1.174
12627 | 0.02 | 75 | 0.75204 | 0.90476 | 38 | 1.182
12542 | 0.03 | 81 | 1.1357 | 0.92857 | 39 | 1.5451
12502 | 0.02 | 71 | 0.75956 | 0.95238 | 40 | 2.099
12368 | 0.03 | 57 | 1.1517 | 0.97619 | 41 | 2.1368
12424 | 0.03 | 65 | 1.1465 | 1 | 42 | 2.19

## ClayBoswell
Clay Boswell 2
ALPHA | BETA
0 | 0.1743
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
12464 | 0.035 | 50 | 0.48945 | 0.020408 | 1 | 0.18049 | 1.7518 | 47 | 0.95918
12371 | 0.154 | 50 | 2.1698 | 0.040816 | 2 | 0.19598 | 2.0607 | 48 | 0.97959
12416 | 0.095 | 50 | 1.3336 | 0.061224 | 3 | 0.20858 | 97.5th Percentile | 1.9912
11811 | 0.07 | 50 | 1.033 | 0.081633 | 4 | 0.32033
12005 | 0.078 | 50 | 1.1325 | 0.10204 | 5 | 0.41839 | Graph Title | Clay Boswell 2: 97.5th Percentile = 1.9912 lb Hg/TBtu
12466 | 0.038 | 50 | 0.53132 | 0.12245 | 6 | 0.48945
11820 | 0.063 | 50 | 0.92901 | 0.14286 | 7 | 0.52097
11760 | 0.073 | 100 | 1.082 | 0.16327 | 8 | 0.53132
12539 | 0.056 | 100 | 0.77844 | 0.18367 | 9 | 0.53687
11643 | 0.062 | 100 | 0.92816 | 0.20408 | 10 | 0.59522
12554 | 0.013 | 100 | 0.18049 | 0.22449 | 11 | 0.6019
11929 | 0.069 | 100 | 1.0082 | 0.2449 | 12 | 0.66803
12479 | 0.094 | 100 | 1.3129 | 0.26531 | 13 | 0.67678
11939 | 0.071 | 100 | 1.0365 | 0.28571 | 14 | 0.7494
12342 | 0.086 | 100 | 1.2145 | 0.30612 | 15 | 0.77844
11932 | 0.101 | 100 | 1.4754 | 0.32653 | 16 | 0.8268
12515 | 0.068 | 100 | 0.94706 | 0.34694 | 17 | 0.88081
12504 | 0.074 | 100 | 1.0315 | 0.36735 | 18 | 0.92816
11838 | 0.072 | 100 | 1.0601 | 0.38776 | 19 | 0.92901
11879 | 0.085 | 50 | 1.2472 | 0.40816 | 20 | 0.94706
12263 | 0.047 | 50 | 0.66803 | 0.42857 | 21 | 0.96266
11864 | 0.076 | 50 | 1.1166 | 0.44898 | 22 | 1.0082
12270 | 0.088 | 50 | 1.2501 | 0.46939 | 23 | 1.0315
11769 | 0.065 | 50 | 0.96266 | 0.4898 | 24 | 1.033
12438 | 0.059 | 50 | 0.8268 | 0.5102 | 25 | 1.0344
12451 | 0.014 | 50 | 0.19598 | 0.53061 | 26 | 1.0365
11936 | 0.085 | 50 | 1.2412 | 0.55102 | 27 | 1.0601
12337 | 0.038 | 50 | 0.53687 | 0.57143 | 28 | 1.082
12301 | 0.073 | 50 | 1.0344 | 0.59184 | 29 | 1.0998
12362 | 0.048 | 50 | 0.67678 | 0.61224 | 30 | 1.1166
11940 | 0.12 | 50 | 1.7518 | 0.63265 | 31 | 1.1325
12299 | 0.042 | 50 | 0.59522 | 0.65306 | 32 | 1.1462
12515 | 0.023 | 50 | 0.32033 | 0.67347 | 33 | 1.1471
12165 | 0.08 | 50 | 1.1462 | 0.69388 | 34 | 1.2145
11926 | 0.089 | 50 | 1.3007 | 0.71429 | 35 | 1.2412
11924 | 0.089 | 50 | 1.301 | 0.73469 | 36 | 1.2472
12327 | 0.053 | 50 | 0.7494 | 0.7551 | 37 | 1.2501
11768 | 0.109 | 50 | 1.6144 | 0.77551 | 38 | 1.2877
12379 | 0.037 | 50 | 0.52097 | 0.79592 | 39 | 1.3007
12460 | 0.082 | 50 | 1.1471 | 0.81633 | 40 | 1.301
12436 | 0.108 | 50 | 1.5137 | 0.83673 | 41 | 1.3129
11886 | 0.075 | 50 | 1.0998 | 0.85714 | 42 | 1.3194
12418 | 0.094 | 50 | 1.3194 | 0.87755 | 43 | 1.3336
12535 | 0.015 | 50 | 0.20858 | 0.89796 | 44 | 1.4754
11926 | 0.141 | 50 | 2.0607 | 0.91837 | 45 | 1.5137
12318 | 0.091 | 50 | 1.2877 | 0.93878 | 46 | 1.6144
12269 | 0.062 | 50 | 0.88081 | 0.95918 | 47 | 1.7518
12452 | 0.043 | 50 | 0.6019 | 0.97959 | 48 | 2.0607
12498 | 0.03 | 50 | 0.41839 | 1 | 49 | 2.1698

## Craig
Craig C3
ALPHA | BETA
0 | 0.664
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
12165 | 0.03 | 50 | 1.6375 | 0.012195 | 1 | 1.0353 | 2.6035 | 79 | 0.96341
12659 | 0.03 | 50 | 1.5736 | 0.02439 | 2 | 1.0372 | 2.6368 | 80 | 0.97561
12120 | 0.03 | 50 | 1.6436 | 0.036585 | 3 | 1.0389 | 97.5th Percentile | 2.6351
12799 | 0.04 | 50 | 2.0752 | 0.04878 | 4 | 1.0417
12810 | 0.03 | 50 | 1.555 | 0.060976 | 5 | 1.0459 | Graph Title | Craig C3: 97.5th Percentile = 2.6351 lb Hg/TBtu
12685 | 0.03 | 50 | 1.5704 | 0.073171 | 6 | 1.0468
11918 | 0.03 | 60 | 1.6714 | 0.085366 | 7 | 1.0496
12236 | 0.02 | 50 | 1.0853 | 0.097561 | 8 | 1.0498
12319 | 0.02 | 50 | 1.078 | 0.10976 | 9 | 1.0507
12541 | 0.02 | 50 | 1.0589 | 0.12195 | 10 | 1.0508
12137 | 0.02 | 50 | 1.0942 | 0.13415 | 11 | 1.0525
12532 | 0.02 | 50 | 1.0597 | 0.14634 | 12 | 1.0555
12382 | 0.03 | 50 | 1.6088 | 0.15854 | 13 | 1.0583
12653 | 0.02 | 50 | 1.0496 | 0.17073 | 14 | 1.0589
12123 | 0.03 | 50 | 1.6432 | 0.18293 | 15 | 1.0597
11912 | 0.06 | 50 | 3.3445 | 0.19512 | 16 | 1.0609
12632 | 0.03 | 50 | 1.5769 | 0.20732 | 17 | 1.061
12431 | 0.02 | 50 | 1.0683 | 0.21951 | 18 | 1.0624
12418 | 0.02 | 50 | 1.0694 | 0.23171 | 19 | 1.063
12350 | 0.03 | 50 | 1.613 | 0.2439 | 20 | 1.064
12432 | 0.02 | 50 | 1.0682 | 0.2561 | 21 | 1.0642
12518 | 0.02 | 50 | 1.0609 | 0.26829 | 22 | 1.0681
12247 | 0.02 | 50 | 1.0843 | 0.28049 | 23 | 1.0682
12749 | 0.02 | 50 | 1.0417 | 0.29268 | 24 | 1.0683
11928 | 0.03 | 50 | 1.67 | 0.30488 | 25 | 1.0692
12261 | 0.02 | 50 | 1.0831 | 0.31707 | 26 | 1.0694
12618 | 0.02 | 50 | 1.0525 | 0.32927 | 27 | 1.07
11867 | 0.02 | 50 | 1.1191 | 0.34146 | 28 | 1.0707
12783 | 0.02 | 50 | 1.0389 | 0.35366 | 29 | 1.0743
12308 | 0.02 | 50 | 1.079 | 0.36585 | 30 | 1.078
12752 | 0.05 | 50 | 2.6035 | 0.37805 | 31 | 1.0784
12500 | 0.02 | 50 | 1.0624 | 0.39024 | 32 | 1.079
12142 | 0.02 | 50 | 1.0937 | 0.40244 | 33 | 1.0831
12116 | 0.02 | 50 | 1.0961 | 0.41463 | 34 | 1.0843
12124 | 0.03 | 50 | 1.643 | 0.42683 | 35 | 1.0843
12614 | 0.03 | 50 | 1.5792 | 0.43902 | 36 | 1.0853
12081 | 0.02 | 50 | 1.0992 | 0.45122 | 37 | 1.0874
12650 | 0.02 | 50 | 1.0498 | 0.46341 | 38 | 1.0877
12687 | 0.04 | 50 | 2.0935 | 0.47561 | 39 | 1.0885
12580 | 0.08 | 50 | 4.2226 | 0.4878 | 40 | 1.0905
12589 | 0.03 | 81 | 1.5823 | 0.5 | 41 | 1.0914
11976 | 0.02 | 50 | 1.1089 | 0.5122 | 42 | 1.0937
12123 | 0.04 | 50 | 2.1909 | 0.52439 | 43 | 1.0942
12582 | 0.02 | 50 | 1.0555 | 0.53659 | 44 | 1.0961
12387 | 0.04 | 50 | 2.1442 | 0.54878 | 45 | 1.0978
12097 | 0.02 | 50 | 1.0978 | 0.56098 | 46 | 1.0986
12590 | 0.04 | 50 | 2.1096 | 0.57317 | 47 | 1.0992
12033 | 0.02 | 50 | 1.1036 | 0.58537 | 48 | 1.101
12168 | 0.02 | 50 | 1.0914 | 0.59756 | 49 | 1.1011
12697 | 0.02 | 50 | 1.0459 | 0.60976 | 50 | 1.1019
12062 | 0.02 | 50 | 1.101 | 0.62195 | 51 | 1.1036
12517 | 0.02 | 50 | 1.061 | 0.63415 | 52 | 1.1056
12433 | 0.02 | 50 | 1.0681 | 0.64634 | 53 | 1.1084
12247 | 0.02 | 50 | 1.0843 | 0.65854 | 54 | 1.1089
12591 | 0.05 | 50 | 2.6368 | 0.67073 | 55 | 1.1089
12638 | 0.02 | 50 | 1.0508 | 0.68293 | 56 | 1.1191
12178 | 0.02 | 50 | 1.0905 | 0.69512 | 57 | 1.555
12493 | 0.02 | 50 | 1.063 | 0.70732 | 58 | 1.5704
12827 | 0.02 | 50 | 1.0353 | 0.71951 | 59 | 1.5736
12209 | 0.02 | 50 | 1.0877 | 0.73171 | 60 | 1.5769
12549 | 0.02 | 50 | 1.0583 | 0.7439 | 61 | 1.5792
12804 | 0.02 | 50 | 1.0372 | 0.7561 | 62 | 1.5823
11976 | 0.02 | 50 | 1.1089 | 0.76829 | 63 | 1.6088
12314 | 0.02 | 50 | 1.0784 | 0.78049 | 64 | 1.613
12200 | 0.02 | 50 | 1.0885 | 0.79268 | 65 | 1.6271
12088 | 0.02 | 50 | 1.0986 | 0.80488 | 66 | 1.6375
12403 | 0.02 | 50 | 1.0707 | 0.81707 | 67 | 1.6383
12243 | 0.03 | 50 | 1.6271 | 0.82927 | 68 | 1.643
12421 | 0.02 | 50 | 1.0692 | 0.84146 | 69 | 1.6432
12362 | 0.02 | 50 | 1.0743 | 0.85366 | 70 | 1.6436
12159 | 0.03 | 50 | 1.6383 | 0.86585 | 71 | 1.67
12481 | 0.02 | 50 | 1.064 | 0.87805 | 72 | 1.6714
12061 | 0.02 | 50 | 1.1011 | 0.89024 | 73 | 2.0752
12411 | 0.02 | 50 | 1.07 | 0.90244 | 74 | 2.0935
12012 | 0.02 | 50 | 1.1056 | 0.91463 | 75 | 2.1096
12479 | 0.02 | 50 | 1.0642 | 0.92683 | 76 | 2.1442
12052 | 0.02 | 50 | 1.1019 | 0.93902 | 77 | 2.1601
12639 | 0.02 | 50 | 1.0507 | 0.95122 | 78 | 2.1909
12296 | 0.04 | 50 | 2.1601 | 0.96341 | 79 | 2.6035
12213 | 0.02 | 50 | 1.0874 | 0.97561 | 80 | 2.6368
12686 | 0.02 | 50 | 1.0468 | 0.9878 | 81 | 3.3445
11981 | 0.02 | 50 | 1.1084 | 1 | 82 | 4.2226

## Cholla
Cholla 3
ALPHA | BETA
0 | 0.358
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
9802 | 0.04 | 100 | 1.4609 | 0.012658 | 1 | 0.89299 | 5.5664 | 77 | 0.97468
10017 | 0.05 | 100 | 1.787 | 0.025316 | 2 | 0.9207 | 6.2308 | 78 | 0.98734
9856 | 0.04 | 100 | 1.4529 | 0.037975 | 3 | 0.92498 | 97.5th Percentile | 5.583
10219 | 0.03 | 100 | 1.051 | 0.050633 | 4 | 0.93051
9744 | 0.06 | 100 | 2.2044 | 0.063291 | 5 | 0.94751 | Graph Title | Cholla 3: 97.5th Percentile = 5.5830 lb Hg/TBtu
9643 | 0.04 | 100 | 1.485 | 0.075949 | 6 | 1.051
9807 | 0.04 | 100 | 1.4602 | 0.088608 | 7 | 1.1828
9420 | 0.06 | 100 | 2.2803 | 0.10127 | 8 | 1.2017
9707 | 0.09 | 100 | 3.3193 | 0.11392 | 9 | 1.2136
10077 | 0.13 | 100 | 4.6184 | 0.12658 | 10 | 1.2219
10100 | 0.08 | 100 | 2.8356 | 0.13924 | 11 | 1.2235
9665 | 0.07 | 100 | 2.5929 | 0.1519 | 12 | 1.2314
9541 | 0.06 | 100 | 2.2513 | 0.16456 | 13 | 1.2317
10075 | 0.05 | 100 | 1.7767 | 0.17722 | 14 | 1.2377
9240 | 0.04 | 100 | 1.5498 | 0.18987 | 15 | 1.2381
9586 | 0.04 | 100 | 1.4938 | 0.20253 | 16 | 1.2406
9667 | 0.05 | 100 | 1.8517 | 0.21519 | 17 | 1.2431
9644 | 0.13 | 100 | 4.8258 | 0.22785 | 18 | 1.2454
11542 | 0.03 | 100 | 0.93051 | 0.24051 | 19 | 1.2531
11520 | 0.04 | 100 | 1.2431 | 0.25316 | 20 | 1.2536
9193 | 0.16 | 100 | 6.2308 | 0.26582 | 21 | 1.2551
10956 | 0.06 | 100 | 1.9606 | 0.27848 | 22 | 1.2567
11425 | 0.06 | 100 | 1.8801 | 0.29114 | 23 | 1.2674
9214 | 0.17 | 100 | 6.6052 | 0.3038 | 24 | 1.2692
9031 | 0.06 | 100 | 2.3785 | 0.31646 | 25 | 1.2695
11498 | 0.04 | 100 | 1.2454 | 0.32911 | 26 | 1.2774
9058 | 0.06 | 100 | 2.3714 | 0.34177 | 27 | 1.2789
9004 | 0.12 | 100 | 4.7712 | 0.35443 | 28 | 1.2977
11283 | 0.04 | 100 | 1.2692 | 0.36709 | 29 | 1.3135
12027 | 0.03 | 100 | 0.89299 | 0.37975 | 30 | 1.3907
12239 | 0.05 | 100 | 1.4625 | 0.39241 | 31 | 1.4529
11299 | 0.04 | 100 | 1.2674 | 0.40506 | 32 | 1.4602
11665 | 0.03 | 100 | 0.9207 | 0.41772 | 33 | 1.4609
11410 | 0.05 | 100 | 1.5688 | 0.43038 | 34 | 1.4625
11035 | 0.04 | 100 | 1.2977 | 0.44304 | 35 | 1.485
10297 | 0.04 | 100 | 1.3907 | 0.4557 | 36 | 1.4938
11210 | 0.04 | 100 | 1.2774 | 0.46835 | 37 | 1.5097
11106 | 0.06 | 100 | 1.9341 | 0.48101 | 38 | 1.5361
11423 | 0.04 | 100 | 1.2536 | 0.49367 | 39 | 1.5424
11629 | 0.04 | 100 | 1.2314 | 0.50633 | 40 | 1.5435
9193 | 0.14 | 100 | 5.452 | 0.51899 | 41 | 1.5443
9644 | 0.05 | 100 | 1.8561 | 0.53165 | 42 | 1.5498
11591 | 0.05 | 100 | 1.5443 | 0.5443 | 43 | 1.5542
11192 | 0.12 | 100 | 3.8385 | 0.55696 | 44 | 1.5568
9031 | 0.04 | 100 | 1.5856 | 0.56962 | 45 | 1.5613
9004 | 0.14 | 100 | 5.5664 | 0.58228 | 46 | 1.5688
9058 | 0.08 | 100 | 3.1618 | 0.59494 | 47 | 1.5856
9214 | 0.04 | 100 | 1.5542 | 0.60759 | 48 | 1.6537
11075 | 0.11 | 100 | 3.5558 | 0.62025 | 49 | 1.7144
10441 | 0.05 | 100 | 1.7144 | 0.63291 | 50 | 1.7767
10721 | 0.08 | 100 | 2.6714 | 0.64557 | 51 | 1.787
11626 | 0.04 | 100 | 1.2317 | 0.65823 | 52 | 1.8517
11498 | 0.05 | 100 | 1.5568 | 0.67089 | 53 | 1.8561
11605 | 0.05 | 100 | 1.5424 | 0.68354 | 54 | 1.8801
11857 | 0.05 | 100 | 1.5097 | 0.6962 | 55 | 1.8879
12107 | 0.04 | 100 | 1.1828 | 0.70886 | 56 | 1.9341
11800 | 0.04 | 100 | 1.2136 | 0.72152 | 57 | 1.9606
11409 | 0.04 | 100 | 1.2551 | 0.73418 | 58 | 2.1411
11378 | 0.06 | 100 | 1.8879 | 0.74684 | 59 | 2.2044
11704 | 0.04 | 100 | 1.2235 | 0.75949 | 60 | 2.2513
11704 | 0.07 | 100 | 2.1411 | 0.77215 | 61 | 2.2803
11566 | 0.04 | 100 | 1.2381 | 0.78481 | 62 | 2.3714
11610 | 0.08 | 100 | 2.4668 | 0.79747 | 63 | 2.3785
11597 | 0.05 | 100 | 1.5435 | 0.81013 | 64 | 2.4379
11653 | 0.05 | 100 | 1.5361 | 0.82278 | 65 | 2.4668
11543 | 0.04 | 100 | 1.2406 | 0.83544 | 66 | 2.5929
10824 | 0.05 | 100 | 1.6537 | 0.8481 | 67 | 2.6714
11748 | 0.08 | 100 | 2.4379 | 0.86076 | 68 | 2.8356
10902 | 0.04 | 100 | 1.3135 | 0.87342 | 69 | 3.1618
11428 | 0.04 | 100 | 1.2531 | 0.88608 | 70 | 3.3193
11280 | 0.04 | 100 | 1.2695 | 0.89873 | 71 | 3.5558
11395 | 0.04 | 100 | 1.2567 | 0.91139 | 72 | 3.8385
11197 | 0.04 | 100 | 1.2789 | 0.92405 | 73 | 4.6184
11465 | 0.05 | 100 | 1.5613 | 0.93671 | 74 | 4.7712
11335 | 0.03 | 100 | 0.94751 | 0.94937 | 75 | 4.8258
11611 | 0.03 | 100 | 0.92498 | 0.96203 | 76 | 5.452
11570 | 0.04 | 100 | 1.2377 | 0.97468 | 77 | 5.5664
11719 | 0.04 | 100 | 1.2219 | 0.98734 | 78 | 6.2308
11916 | 0.04 | 100 | 1.2017 | 1 | 79 | 6.6052

## Heskett
Heskett B2
ALPHA | BETA
0 | 0.5964
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
11115 | 0.095 | 200 | 5.0974 | 0.027778 | 1 | 1.6176 | 7.6903 | 35 | 0.97222
11218 | 0.165 | 200 | 8.7722 | 0.055556 | 2 | 2.2886 | 8.7722 | 36 | 1
10941 | 0.087 | 200 | 4.7424 | 0.083333 | 3 | 2.8081 | 97.5th Percentile | 7.7985
10882 | 0.088 | 200 | 4.8229 | 0.11111 | 4 | 2.8107
11041 | 0.137 | 200 | 7.4003 | 0.13889 | 5 | 2.8513 | Graph Title | Heskett B2: 97.5th Percentile = 7.7985 lb Hg/TBtu
11105 | 0.072 | 200 | 3.8668 | 0.16667 | 6 | 3.1023
11044 | 0.052 | 200 | 2.8081 | 0.19444 | 7 | 3.2506
11150 | 0.058 | 200 | 3.1023 | 0.22222 | 8 | 3.4086
11090 | 0.143 | 200 | 7.6903 | 0.25 | 9 | 3.4289
11135 | 0.08 | 200 | 4.2849 | 0.27778 | 10 | 3.767
11040 | 0.107 | 200 | 5.7803 | 0.30556 | 11 | 3.8276
11059 | 0.125 | 200 | 6.7411 | 0.33333 | 12 | 3.8668
11035 | 0.09 | 200 | 4.8642 | 0.36111 | 13 | 4.1097
11026 | 0.093 | 200 | 5.0304 | 0.38889 | 14 | 4.2849
11943 | 0.13 | 200 | 6.4918 | 0.41667 | 15 | 4.519
10996 | 0.103 | 200 | 5.5865 | 0.44444 | 16 | 4.5464
11087 | 0.088 | 200 | 4.7338 | 0.47222 | 17 | 4.7338
11008 | 0.111 | 200 | 6.0138 | 0.5 | 18 | 4.7424
10935 | 0.089 | 200 | 4.8541 | 0.52778 | 19 | 4.8229
10854 | 0.101 | 200 | 5.5497 | 0.55556 | 20 | 4.8541
10888 | 0.083 | 200 | 4.5464 | 0.58333 | 21 | 4.8642
11086 | 0.084 | 200 | 4.519 | 0.61111 | 22 | 5.0304
10945 | 0.042 | 200 | 2.2886 | 0.63889 | 23 | 5.0974
11246 | 0.053 | 200 | 2.8107 | 0.66667 | 24 | 5.2423
11063 | 0.071 | 200 | 3.8276 | 0.69444 | 25 | 5.309
11061 | 0.03 | 200 | 1.6176 | 0.72222 | 26 | 5.3924
11263 | 0.099 | 200 | 5.2423 | 0.75 | 27 | 5.5497
10825 | 0.059 | 200 | 3.2506 | 0.77778 | 28 | 5.5865
10766 | 0.068 | 200 | 3.767 | 0.80556 | 29 | 5.7803
11060 | 0.1 | 200 | 5.3924 | 0.83333 | 30 | 6.0138
11029 | 0.076 | 200 | 4.1097 | 0.86111 | 31 | 6.4022
11009 | 0.098 | 200 | 5.309 | 0.88889 | 32 | 6.4918
11086 | 0.053 | 200 | 2.8513 | 0.91667 | 33 | 6.7411
11198 | 0.064 | 200 | 3.4086 | 0.94444 | 34 | 7.4003
10784 | 0.062 | 200 | 3.4289 | 0.97222 | 35 | 7.6903
10806 | 0.116 | 200 | 6.4022 | 1 | 36 | 8.7722

## Antelope
Antelope B1
ALPHA | BETA
0.002164 | 0.81882
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
10550 | 0.064 | 106 | 3.9491 | 0.011494 | 1 | 1.333 | 6.9178 | 84 | 0.96552
10340 | 0.056 | 100 | 3.5717 | 0.022989 | 2 | 1.4638 | 7.1229 | 85 | 0.97701
10470 | 0.088 | 96 | 5.5911 | 0.034483 | 3 | 1.5326 | 97.5th Percentile | 7.087
10490 | 0.068 | 86 | 4.4065 | 0.045977 | 4 | 1.5469
10710 | 0.056 | 131 | 3.2245 | 0.057471 | 5 | 1.5755 | Graph Title | Antelope B1: 97.5th Percentile = 7.0870 lb Hg/TBtu
10650 | 0.06 | 98 | 3.7315 | 0.068966 | 6 | 1.5987
10510 | 0.025 | 98 | 1.5755 | 0.08046 | 7 | 1.6107
10390 | 0.062 | 117 | 3.7932 | 0.091954 | 8 | 1.6221
10590 | 0.057 | 121 | 3.3919 | 0.10345 | 9 | 1.6294
10480 | 0.025 | 74 | 1.6642 | 0.11494 | 10 | 1.6642
10580 | 0.051 | 92 | 3.2345 | 0.12644 | 11 | 3.0339
10510 | 0.025 | 132 | 1.4638 | 0.13793 | 12 | 3.0695
10290 | 0.06 | 90 | 3.9295 | 0.14943 | 13 | 3.0744
10610 | 0.05 | 105 | 3.0744 | 0.16092 | 14 | 3.0854
10550 | 0.025 | 109 | 1.5326 | 0.17241 | 15 | 3.1038
11050 | 0.079 | 152 | 4.2131 | 0.18391 | 16 | 3.1272
10470 | 0.025 | 177 | 1.333 | 0.1954 | 17 | 3.1281
10540 | 0.058 | 175 | 3.0854 | 0.2069 | 18 | 3.2245
10920 | 0.071 | 122 | 4.0885 | 0.21839 | 19 | 3.2345
10590 | 0.093 | 136 | 5.3574 | 0.22989 | 20 | 3.3479
10300 | 0.066 | 89 | 4.3276 | 0.24138 | 21 | 3.3869
10740 | 0.103 | 111 | 6.1759 | 0.25287 | 22 | 3.3919
10510 | 0.069 | 143 | 3.9449 | 0.26437 | 23 | 3.417
10790 | 0.066 | 94 | 4.0866 | 0.27586 | 24 | 3.428
10570 | 0.06 | 95 | 3.7842 | 0.28736 | 25 | 3.4365
10410 | 0.065 | 113 | 4.0036 | 0.29885 | 26 | 3.4411
10400 | 0.058 | 96 | 3.7099 | 0.31034 | 27 | 3.4831
10600 | 0.057 | 106 | 3.5005 | 0.32184 | 28 | 3.5005
10270 | 0.062 | 145 | 3.6119 | 0.33333 | 29 | 3.5717
10320 | 0.062 | 115 | 3.8355 | 0.34483 | 30 | 3.5992
10400 | 0.058 | 134 | 3.417 | 0.35632 | 31 | 3.6066
10477 | 0.025 | 86 | 1.6221 | 0.36782 | 32 | 3.6119
10650 | 0.067 | 88 | 4.258 | 0.37931 | 33 | 3.6166
10430 | 0.079 | 129 | 4.6913 | 0.3908 | 34 | 3.6539
10570 | 0.052 | 131 | 3.0339 | 0.4023 | 35 | 3.6925
10340 | 0.092 | 120 | 5.6192 | 0.41379 | 36 | 3.7099
10490 | 0.069 | 124 | 4.1183 | 0.42529 | 37 | 3.7315
10670 | 0.062 | 122 | 3.6539 | 0.43678 | 38 | 3.734
10970 | 0.066 | 113 | 3.8577 | 0.44828 | 39 | 3.7756
10240 | 0.05 | 117 | 3.1038 | 0.45977 | 40 | 3.7842
10390 | 0.06 | 104 | 3.7756 | 0.47126 | 41 | 3.7932
10560 | 0.052 | 75 | 3.428 | 0.48276 | 42 | 3.7938
10490 | 0.059 | 142 | 3.3869 | 0.49425 | 43 | 3.8242
10380 | 0.066 | 119 | 4.0243 | 0.50575 | 44 | 3.8355
9946 | 0.083 | 109 | 5.3973 | 0.51724 | 45 | 3.8577
10390 | 0.05 | 57 | 3.4831 | 0.52874 | 46 | 3.9295
10260 | 0.054 | 104 | 3.4411 | 0.54023 | 47 | 3.9449
10180 | 0.063 | 108 | 4.0112 | 0.55172 | 48 | 3.9491
10340 | 0.025 | 90 | 1.6294 | 0.56322 | 49 | 4.0036
10230 | 0.053 | 75 | 3.6066 | 0.57471 | 50 | 4.0106
10320 | 0.102 | 59 | 7.1229 | 0.58621 | 51 | 4.0112
10510 | 0.05 | 70 | 3.3479 | 0.5977 | 52 | 4.0243
10410 | 0.079 | 106 | 4.9402 | 0.6092 | 53 | 4.0621
10400 | 0.058 | 93 | 3.734 | 0.62069 | 54 | 4.0866
10200 | 0.107 | 131 | 6.4692 | 0.63218 | 55 | 4.0885
10540 | 0.071 | 111 | 4.3379 | 0.64368 | 56 | 4.1183
10290 | 0.105 | 113 | 6.5428 | 0.65517 | 57 | 4.1325
10400 | 0.082 | 121 | 4.9688 | 0.66667 | 58 | 4.1987
10300 | 0.076 | 84 | 5.0375 | 0.67816 | 59 | 4.2131
10240 | 0.06 | 121 | 3.6925 | 0.68966 | 60 | 4.258
10610 | 0.05 | 97 | 3.1281 | 0.70115 | 61 | 4.32
10530 | 0.073 | 119 | 4.3878 | 0.71264 | 62 | 4.3276
10390 | 0.056 | 92 | 3.6166 | 0.72414 | 63 | 4.3379
10350 | 0.056 | 96 | 3.5992 | 0.73563 | 64 | 4.3878
10480 | 0.123 | 106 | 7.6403 | 0.74713 | 65 | 4.4065
10490 | 0.05 | 111 | 3.0695 | 0.75862 | 66 | 4.5247
10380 | 0.061 | 63 | 4.1987 | 0.77011 | 67 | 4.576
10090 | 0.09 | 129 | 5.5246 | 0.78161 | 68 | 4.6913
10590 | 0.05 | 98 | 3.1272 | 0.7931 | 69 | 4.7031
10680 | 0.061 | 93 | 3.8242 | 0.8046 | 70 | 4.9402
10370 | 0.058 | 87 | 3.7938 | 0.81609 | 71 | 4.9688
10430 | 0.025 | 110 | 1.5469 | 0.82759 | 72 | 4.9903
10470 | 0.109 | 114 | 6.6608 | 0.83908 | 73 | 5.0375
10460 | 0.025 | 90 | 1.6107 | 0.85057 | 74 | 5.3574
10680 | 0.059 | 127 | 3.4365 | 0.86207 | 75 | 5.3973
10470 | 0.025 | 93 | 1.5987 | 0.87356 | 76 | 5.5246
10430 | 0.073 | 104 | 4.576 | 0.88506 | 77 | 5.5911
10480 | 0.073 | 107 | 4.5247 | 0.89655 | 78 | 5.6192
10240 | 0.071 | 87 | 4.7031 | 0.90805 | 79 | 5.7764
10630 | 0.1 | 133 | 5.7764 | 0.91954 | 80 | 6.1759
10410 | 0.103 | 73 | 6.9178 | 0.93103 | 81 | 6.4692
10420 | 0.078 | 95 | 4.9903 | 0.94253 | 82 | 6.5428
10480 | 0.071 | 144 | 4.0621 | 0.95402 | 83 | 6.6608
10080 | 0.25 | 97 | 16.4628 | 0.96552 | 84 | 6.9178
10280 | 0.064 | 97 | 4.1325 | 0.97701 | 85 | 7.1229
10420 | 0.069 | 105 | 4.32 | 0.98851 | 86 | 7.6403
10330 | 0.059 | 71 | 4.0106 | 1 | 87 | 16.4628

## Leland
Leland 2
ALPHA | BETA
0 | 0.9513
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
10830 | 0.073 | 103 | 6.4123 | 0.0097087 | 1 | 2.196 | 9.2788 | 100 | 0.97087
10920 | 0.086 | 93 | 7.4919 | 0.019417 | 2 | 2.2082 | 9.8754 | 101 | 0.98058
10890 | 0.069 | 136 | 6.0275 | 0.029126 | 3 | 2.2628 | 97.5th Percentile | 9.5323
10950 | 0.079 | 121 | 6.8633 | 0.038835 | 4 | 2.2672
11040 | 0.064 | 131 | 5.5148 | 0.048544 | 5 | 2.2672 | Graph Title | Leland 2: 97.5th Percentile = 9.5323 lb Hg/TBtu
10940 | 0.05 | 119 | 4.3478 | 0.058252 | 6 | 4.3478
10930 | 0.078 | 85 | 6.7888 | 0.067961 | 7 | 4.4329
10950 | 0.07 | 86 | 6.0814 | 0.07767 | 8 | 4.5
10800 | 0.072 | 133 | 6.342 | 0.087379 | 9 | 4.5648
10630 | 0.097 | 78 | 8.6807 | 0.097087 | 10 | 4.7389
10690 | 0.058 | 127 | 5.1614 | 0.1068 | 11 | 4.8054
10550 | 0.089 | 120 | 8.0252 | 0.1165 | 12 | 4.8145
10790 | 0.078 | 119 | 6.8769 | 0.12621 | 13 | 4.819
10660 | 0.065 | 161 | 5.8006 | 0.13592 | 14 | 4.8554
10790 | 0.1 | 97 | 8.8165 | 0.14563 | 15 | 4.899
10500 | 0.129 | 107 | 11.6874 | 0.15534 | 16 | 4.911
10500 | 0.109 | 112 | 9.8754 | 0.16505 | 17 | 4.9205
10700 | 0.089 | 168 | 7.9127 | 0.17476 | 18 | 4.95
10700 | 0.113 | 113 | 10.0464 | 0.18447 | 19 | 5.0161
10860 | 0.095 | 117 | 8.3217 | 0.19417 | 20 | 5.0161
10690 | 0.084 | 121 | 7.4751 | 0.20388 | 21 | 5.0164
10710 | 0.081 | 140 | 7.1947 | 0.21359 | 22 | 5.0798
10820 | 0.078 | 125 | 6.8578 | 0.2233 | 23 | 5.1136
10740 | 0.091 | 177 | 8.0604 | 0.23301 | 24 | 5.1614
10680 | 0.073 | 147 | 6.5023 | 0.24272 | 25 | 5.2221
10700 | 0.095 | 111 | 8.4461 | 0.25243 | 26 | 5.2365
10770 | 0.077 | 73 | 6.8013 | 0.26214 | 27 | 5.2648
10720 | 0.097 | 90 | 8.6078 | 0.27184 | 28 | 5.3046
10890 | 0.087 | 125 | 7.5999 | 0.28155 | 29 | 5.4132
10800 | 0.08 | 116 | 7.0467 | 0.29126 | 30 | 5.4568
10840 | 0.054 | 87 | 4.7389 | 0.30097 | 31 | 5.4612
10727 | 0.063 | 98 | 5.587 | 0.31068 | 32 | 5.4858
10410 | 0.072 | 70 | 6.5796 | 0.32039 | 33 | 5.5148
10632 | 0.067 | 166 | 5.9948 | 0.3301 | 34 | 5.587
10654 | 0.055 | 164 | 4.911 | 0.33981 | 35 | 5.6169
10750 | 0.073 | 126 | 6.46 | 0.34951 | 36 | 5.638
10608 | 0.076 | 95 | 6.8155 | 0.35922 | 37 | 5.699
10925 | 0.063 | 120 | 5.4858 | 0.36893 | 38 | 5.7234
10480 | 0.071 | 123 | 6.4449 | 0.37864 | 39 | 5.7461
10801 | 0.067 | 133 | 5.901 | 0.38835 | 40 | 5.7814
10490 | 0.089 | 97 | 8.0711 | 0.39806 | 41 | 5.8006
10430 | 0.055 | 174 | 5.0164 | 0.40777 | 42 | 5.901
10580 | 0.054 | 127 | 4.8554 | 0.41748 | 43 | 5.9401
10690 | 0.054 | 160 | 4.8054 | 0.42718 | 44 | 5.9948
10420 | 0.05 | 103 | 4.5648 | 0.43689 | 45 | 6.0064
10430 | 0.063 | 103 | 5.7461 | 0.4466 | 46 | 6.0275
10630 | 0.063 | 75 | 5.638 | 0.45631 | 47 | 6.0429
10720 | 0.061 | 83 | 5.4132 | 0.46602 | 48 | 6.0814
10440 | 0.054 | 147 | 4.9205 | 0.47573 | 49 | 6.1174
10570 | 0.055 | 97 | 4.95 | 0.48544 | 50 | 6.1314
10490 | 0.025 | 97 | 2.2672 | 0.49515 | 51 | 6.1316
10560 | 0.082 | 88 | 7.387 | 0.50485 | 52 | 6.3303
10520 | 0.077 | 121 | 6.9629 | 0.51456 | 53 | 6.342
10760 | 0.06 | 134 | 5.3046 | 0.52427 | 54 | 6.4123
10770 | 0.025 | 89 | 2.2082 | 0.53398 | 55 | 6.4449
10830 | 0.025 | 119 | 2.196 | 0.54369 | 56 | 6.46
10670 | 0.054 | 138 | 4.8145 | 0.5534 | 57 | 6.4841
10810 | 0.057 | 142 | 5.0161 | 0.56311 | 58 | 6.5023
10660 | 0.054 | 97 | 4.819 | 0.57282 | 59 | 6.5452
10550 | 0.068 | 91 | 6.1316 | 0.58252 | 60 | 6.5796
10770 | 0.068 | 106 | 6.0064 | 0.59223 | 61 | 6.7888
10390 | 0.066 | 137 | 6.0429 | 0.60194 | 62 | 6.8013
10670 | 0.063 | 115 | 5.6169 | 0.61165 | 63 | 6.8155
10240 | 0.066 | 116 | 6.1314 | 0.62136 | 64 | 6.8206
10510 | 0.025 | 83 | 2.2628 | 0.63107 | 65 | 6.8578
10460 | 0.06 | 124 | 5.4568 | 0.64078 | 66 | 6.8633
10490 | 0.025 | 95 | 2.2672 | 0.65049 | 67 | 6.8769
10790 | 0.058 | 137 | 5.1136 | 0.66019 | 68 | 6.9629
10970 | 0.066 | 120 | 5.7234 | 0.6699 | 69 | 7.0467
10600 | 0.087 | 122 | 7.8078 | 0.67961 | 70 | 7.0832
10850 | 0.065 | 71 | 5.699 | 0.68932 | 71 | 7.1947
10640 | 0.097 | 118 | 8.6726 | 0.69903 | 72 | 7.3177
10930 | 0.06 | 117 | 5.2221 | 0.70874 | 73 | 7.3861
10900 | 0.06 | 120 | 5.2365 | 0.71845 | 74 | 7.387
10790 | 0.091 | 112 | 8.023 | 0.72816 | 75 | 7.4751
10300 | 0.055 | 117 | 5.0798 | 0.73786 | 76 | 7.4919
10570 | 0.05 | 122 | 4.5 | 0.74757 | 77 | 7.5999
10560 | 0.103 | 103 | 9.2788 | 0.75728 | 78 | 7.6468
10580 | 0.09 | 134 | 8.0923 | 0.76699 | 79 | 7.6675
10820 | 0.072 | 151 | 6.3303 | 0.7767 | 80 | 7.8005
10680 | 0.055 | 115 | 4.899 | 0.78641 | 81 | 7.8078
10600 | 0.076 | 122 | 6.8206 | 0.79612 | 82 | 7.9127
10730 | 0.05 | 87 | 4.4329 | 0.80583 | 83 | 8.023
10480 | 0.058 | 94 | 5.2648 | 0.81553 | 84 | 8.0252
10670 | 0.093 | 96 | 8.2916 | 0.82524 | 85 | 8.0604
10860 | 0.066 | 83 | 5.7814 | 0.83495 | 86 | 8.0634
10610 | 0.079 | 106 | 7.0832 | 0.84466 | 87 | 8.0711
10660 | 0.092 | 114 | 8.2101 | 0.85437 | 88 | 8.0923
10730 | 0.069 | 85 | 6.1174 | 0.86408 | 89 | 8.2101
10730 | 0.067 | 132 | 5.9401 | 0.87379 | 90 | 8.2916
10270 | 0.091 | 64 | 8.4292 | 0.8835 | 91 | 8.3115
10610 | 0.073 | 145 | 6.5452 | 0.8932 | 92 | 8.3217
10810 | 0.057 | 136 | 5.0161 | 0.90291 | 93 | 8.4292
10800 | 0.062 | 140 | 5.4612 | 0.91262 | 94 | 8.4461
10710 | 0.073 | 103 | 6.4841 | 0.92233 | 95 | 8.6078
10610 | 0.087 | 84 | 7.8005 | 0.93204 | 96 | 8.6726
10670 | 0.086 | 86 | 7.6675 | 0.94175 | 97 | 8.6807
10530 | 0.092 | 91 | 8.3115 | 0.95146 | 98 | 8.8165
10450 | 0.084 | 103 | 7.6468 | 0.96117 | 99 | 9.0296
10790 | 0.083 | 116 | 7.3177 | 0.97087 | 100 | 9.2788
10690 | 0.083 | 107 | 7.3861 | 0.98058 | 101 | 9.8754
10500 | 0.089 | 130 | 8.0634 | 0.99029 | 102 | 10.0464
10430 | 0.099 | 75 | 9.0296 | 1 | 103 | 11.6874

## Stanton10
Stanton 10
ALPHA | BETA
0.002164 | 0.81882
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
10850 | 0.069 | 74 | 4.4367 | 0.025 | 1 | 2.7856 | 8.0289 | 39 | 0.975
11000 | 0.082 | 79 | 5.1447 | 0.05 | 2 | 2.9511 | 8.3157 | 40 | 1
10870 | 0.064 | 83 | 4.0284 | 0.075 | 3 | 3.1 | 97.5th Percentile | 8.0289
10960 | 0.076 | 99 | 4.583 | 0.1 | 4 | 3.1254
10690 | 0.077 | 108 | 4.6687 | 0.125 | 5 | 3.228 | Graph Title | Stanton 10: 97.5th Percentile = 8.0289 lb Hg/TBtu
10920 | 0.081 | 141 | 4.4765 | 0.15 | 6 | 3.315
10570 | 0.074 | 106 | 4.5575 | 0.175 | 7 | 3.8753
10730 | 0.073 | 134 | 4.1684 | 0.2 | 8 | 4.0266
10870 | 0.085 | 123 | 4.9066 | 0.225 | 9 | 4.0284
10570 | 0.065 | 121 | 3.8753 | 0.25 | 10 | 4.095
10900 | 0.079 | 125 | 4.528 | 0.275 | 11 | 4.1298
10600 | 0.067 | 116 | 4.0266 | 0.3 | 12 | 4.1684
10680 | 0.072 | 138 | 4.095 | 0.325 | 13 | 4.4367
10870 | 0.084 | 92 | 5.1853 | 0.35 | 14 | 4.4765
10620 | 0.055 | 141 | 3.1254 | 0.375 | 15 | 4.528
10650 | 0.051 | 158 | 2.7856 | 0.4 | 16 | 4.5575
10680 | 0.054 | 115 | 3.228 | 0.425 | 17 | 4.583
10630 | 0.067 | 103 | 4.1298 | 0.45 | 18 | 4.6687
10660 | 0.05 | 99 | 3.1 | 0.475 | 19 | 4.9066
10750 | 0.051 | 127 | 2.9511 | 0.5 | 20 | 5.1447
10480 | 0.052 | 94 | 3.315 | 0.525 | 21 | 5.1853
10500 | 0.104 | 88 | 6.7039 | 0.55 | 22 | 5.5174
10510 | 0.104 | 87 | 6.712 | 0.575 | 23 | 5.5467
10500 | 0.104 | 88 | 6.7039 | 0.6 | 24 | 6.0958
10610 | 0.116 | 107 | 7.1018 | 0.625 | 25 | 6.5282
10850 | 0.116 | 82 | 7.3308 | 0.65 | 26 | 6.7039
10300 | 0.116 | 64 | 8.0289 | 0.675 | 27 | 6.7039
10620 | 0.115 | 108 | 7.0187 | 0.7 | 28 | 6.712
10770 | 0.115 | 135 | 6.5282 | 0.725 | 29 | 7.0187
10390 | 0.115 | 87 | 7.5077 | 0.75 | 30 | 7.0952
10490 | 0.115 | 97 | 7.2769 | 0.775 | 31 | 7.1018
10520 | 0.115 | 84 | 7.4632 | 0.8 | 32 | 7.1382
10370 | 0.115 | 114 | 7.0952 | 0.825 | 33 | 7.2769
10680 | 0.091 | 106 | 5.5467 | 0.85 | 34 | 7.3308
10760 | 0.091 | 105 | 5.5174 | 0.875 | 35 | 7.4632
10460 | 0.091 | 72 | 6.0958 | 0.9 | 36 | 7.5077
10650 | 0.12 | 72 | 7.895 | 0.925 | 37 | 7.8226
10310 | 0.12 | 63 | 8.3157 | 0.95 | 38 | 7.895
10640 | 0.12 | 119 | 7.1382 | 0.975 | 39 | 8.0289
10590 | 0.119 | 75 | 7.8226 | 1 | 40 | 8.3157

## Stanton1
Stanton 1
ALPHA | BETA
0 | 0.5591
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
10850 | 0.069 | 74 | 3.5556 | 0.025 | 1 | 2.6224 | 6.3056 | 39 | 0.975
11000 | 0.082 | 79 | 4.1678 | 0.05 | 2 | 2.6525 | 6.5075 | 40 | 1
10870 | 0.064 | 83 | 3.2918 | 0.075 | 3 | 2.6774 | 97.5th Percentile | 6.3056
10960 | 0.076 | 99 | 3.877 | 0.1 | 4 | 2.7742
10690 | 0.077 | 108 | 4.0272 | 0.125 | 5 | 2.8269 | Graph Title | Stanton 1: 97.5th Percentile = 6.3056 lb Hg/TBtu
10920 | 0.081 | 141 | 4.1472 | 0.15 | 6 | 2.8955
10570 | 0.074 | 106 | 3.9142 | 0.175 | 7 | 3.2918
10730 | 0.073 | 134 | 3.8038 | 0.2 | 8 | 3.4382
10870 | 0.085 | 123 | 4.372 | 0.225 | 9 | 3.524
10570 | 0.065 | 121 | 3.4382 | 0.25 | 10 | 3.5339
10900 | 0.079 | 125 | 4.0522 | 0.275 | 11 | 3.5556
10600 | 0.067 | 116 | 3.5339 | 0.3 | 12 | 3.7692
10680 | 0.072 | 138 | 3.7692 | 0.325 | 13 | 3.8038
10870 | 0.084 | 92 | 4.3206 | 0.35 | 14 | 3.877
10620 | 0.055 | 141 | 2.8955 | 0.375 | 15 | 3.9142
10650 | 0.051 | 158 | 2.6774 | 0.4 | 16 | 4.0272
10680 | 0.054 | 115 | 2.8269 | 0.425 | 17 | 4.0522
10630 | 0.067 | 103 | 3.524 | 0.45 | 18 | 4.1472
10660 | 0.05 | 99 | 2.6224 | 0.475 | 19 | 4.1678
10750 | 0.051 | 127 | 2.6525 | 0.5 | 20 | 4.3206
10480 | 0.052 | 94 | 2.7742 | 0.525 | 21 | 4.372
10500 | 0.104 | 88 | 5.5378 | 0.55 | 22 | 4.7284
10510 | 0.104 | 87 | 5.5325 | 0.575 | 23 | 4.7639
10500 | 0.104 | 88 | 5.5378 | 0.6 | 24 | 4.8641
10610 | 0.116 | 107 | 6.1127 | 0.625 | 25 | 5.5325
10850 | 0.116 | 82 | 5.9775 | 0.65 | 26 | 5.5378
10300 | 0.116 | 64 | 6.2967 | 0.675 | 27 | 5.5378
10620 | 0.115 | 108 | 6.0543 | 0.7 | 28 | 5.97
10770 | 0.115 | 135 | 5.97 | 0.725 | 29 | 5.9775
10390 | 0.115 | 87 | 6.1883 | 0.75 | 30 | 6.0543
10490 | 0.115 | 97 | 6.1293 | 0.775 | 31 | 6.1118
10520 | 0.115 | 84 | 6.1118 | 0.8 | 32 | 6.1127
10370 | 0.115 | 114 | 6.2002 | 0.825 | 33 | 6.1293
10680 | 0.091 | 106 | 4.7639 | 0.85 | 34 | 6.1883
10760 | 0.091 | 105 | 4.7284 | 0.875 | 35 | 6.2002
10460 | 0.091 | 72 | 4.8641 | 0.9 | 36 | 6.2826
10650 | 0.12 | 72 | 6.2997 | 0.925 | 37 | 6.2967
10310 | 0.12 | 63 | 6.5075 | 0.95 | 38 | 6.2997
10640 | 0.12 | 119 | 6.3056 | 0.975 | 39 | 6.3056
10590 | 0.119 | 75 | 6.2826 | 1 | 40 | 6.5075

## Kline
Kline 1
ALPHA | BETA
0 | 0.0025
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
5238 | 0.16 | 100 | 0.076365 | 0.018182 | 1 | 0.024704 | 0.11698 | 53 | 0.96364
5296 | 0.21 | 100 | 0.099131 | 0.036364 | 2 | 0.053161 | 0.11898 | 54 | 0.98182
5092 | 0.18 | 100 | 0.088374 | 0.054545 | 3 | 0.05895 | 97.5th Percentile | 0.11823
5230 | 0.17 | 100 | 0.081262 | 0.072727 | 4 | 0.05916
5246 | 0.16 | 100 | 0.076249 | 0.090909 | 5 | 0.065235 | Graph Title | Kline 1: 97.5th Percentile = 0.1182 lb Hg/TBtu
5347 | 0.14 | 100 | 0.065457 | 0.10909 | 6 | 0.065457
5397 | 0.17 | 100 | 0.078747 | 0.12727 | 7 | 0.067088
5362 | 0.19 | 100 | 0.088586 | 0.14545 | 8 | 0.068776
5364 | 0.16 | 100 | 0.074571 | 0.16364 | 9 | 0.069444
5173 | 0.11 | 100 | 0.053161 | 0.18182 | 10 | 0.074571
5089 | 0.14 | 100 | 0.068776 | 0.2 | 11 | 0.075729
5082 | 0.17 | 100 | 0.083628 | 0.21818 | 12 | 0.076249
5060 | 0.05 | 100 | 0.024704 | 0.23636 | 13 | 0.076365
5400 | 0.15 | 100 | 0.069444 | 0.25455 | 14 | 0.076871
5288 | 0.19 | 100 | 0.089826 | 0.27273 | 15 | 0.078747
4675 | 0.17 | 200 | 0.090909 | 0.29091 | 16 | 0.078989
5217 | 0.14 | 100 | 0.067088 | 0.30909 | 17 | 0.079707
5071 | 0.12 | 100 | 0.05916 | 0.32727 | 18 | 0.080922
5239 | 0.17 | 100 | 0.081122 | 0.34545 | 19 | 0.081122
5313 | 0.19 | 100 | 0.089403 | 0.36364 | 20 | 0.081262
5316 | 0.22 | 100 | 0.10346 | 0.38182 | 21 | 0.081778
5277 | 0.19 | 100 | 0.090013 | 0.4 | 22 | 0.082109
5166 | 0.17 | 100 | 0.082269 | 0.41818 | 23 | 0.082269
5091 | 0.17 | 100 | 0.083481 | 0.43636 | 24 | 0.082572
4769 | 0.16 | 100 | 0.083875 | 0.45455 | 25 | 0.083481
5170 | 0.19 | 100 | 0.091876 | 0.47273 | 26 | 0.083503
4710 | 0.19 | 100 | 0.10085 | 0.49091 | 27 | 0.083628
5129 | 0.24 | 100 | 0.11698 | 0.50909 | 28 | 0.083875
5389 | 0.18 | 100 | 0.083503 | 0.52727 | 29 | 0.083928
5252 | 0.17 | 100 | 0.080922 | 0.54545 | 30 | 0.083987
5146 | 0.23 | 200 | 0.11174 | 0.56364 | 31 | 0.085911
4622 | 0.22 | 100 | 0.119 | 0.58182 | 32 | 0.087767
4665 | 0.11 | 100 | 0.05895 | 0.6 | 33 | 0.088374
3703 | 0.13 | 100 | 0.087767 | 0.61818 | 34 | 0.088586
5178 | 0.2 | 100 | 0.096562 | 0.63636 | 35 | 0.089403
5197 | 0.17 | 100 | 0.081778 | 0.65455 | 36 | 0.089445
4472 | 0.16 | 100 | 0.089445 | 0.67273 | 37 | 0.089826
4406 | 0.19 | 100 | 0.10781 | 0.69091 | 38 | 0.090013
5147 | 0.17 | 100 | 0.082572 | 0.70909 | 39 | 0.09003
4982 | 0.13 | 100 | 0.065235 | 0.72727 | 40 | 0.090909
4766 | 0.16 | 100 | 0.083928 | 0.74545 | 41 | 0.091876
4934 | 0.19 | 100 | 0.096271 | 0.76364 | 42 | 0.093615
5074 | 0.19 | 100 | 0.093615 | 0.78182 | 43 | 0.096271
5064 | 0.16 | 100 | 0.078989 | 0.8 | 44 | 0.096562
5145 | 0.2 | 100 | 0.097182 | 0.81818 | 45 | 0.097182
5358 | 0.18 | 100 | 0.083987 | 0.83636 | 46 | 0.098309
5086 | 0.2 | 100 | 0.098309 | 0.85455 | 47 | 0.099131
5854 | 0.18 | 100 | 0.076871 | 0.87273 | 48 | 0.099413
5238 | 0.18 | 100 | 0.085911 | 0.89091 | 49 | 0.10085
5332 | 0.17 | 100 | 0.079707 | 0.90909 | 50 | 0.10346
5282 | 0.16 | 100 | 0.075729 | 0.92727 | 51 | 0.10781
5785 | 0.19 | 100 | 0.082109 | 0.94545 | 52 | 0.11174
5043 | 0.24 | 100 | 0.11898 | 0.96364 | 53 | 0.11698
5281 | 0.21 | 200 | 0.099413 | 0.98182 | 54 | 0.11898
5276 | 0.19 | 100 | 0.09003 | 1 | 55 | 0.119

## Scrubgrass
Scrubgrass 1
ALPHA | BETA
0 | 0.0011
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
7621 | 0.67 | 900 | 0.096706 | 0.019608 | 1 | 0.044132 | 0.1547 | 49 | 0.96078
7646 | 0.57 | 900 | 0.082004 | 0.039216 | 2 | 0.056424 | 0.15808 | 50 | 0.98039
8045 | 0.83 | 1200 | 0.11349 | 0.058824 | 3 | 0.066727 | 97.5th Percentile | 0.15715
7636 | 0.56 | 897 | 0.080671 | 0.078431 | 4 | 0.070204
7968 | 0.77 | 997 | 0.1063 | 0.098039 | 5 | 0.070827 | Graph Title | Scrubgrass 1: 97.5th Percentile = 0.1572 lb Hg/TBtu
7047 | 0.71 | 997 | 0.11083 | 0.11765 | 6 | 0.073683
7267 | 1.01 | 1295 | 0.15288 | 0.13725 | 7 | 0.073796
7879 | 0.67 | 1047 | 0.09354 | 0.15686 | 8 | 0.073974
7515 | 1.08 | 1146 | 0.15808 | 0.17647 | 9 | 0.074977
7261 | 0.57 | 997 | 0.086352 | 0.19608 | 10 | 0.079303
7704 | 0.59 | 1278 | 0.084242 | 0.21569 | 11 | 0.080381
6645 | 0.5 | 1621 | 0.082769 | 0.23529 | 12 | 0.080481
7977 | 0.87 | 1247 | 0.11997 | 0.2549 | 13 | 0.080581
7846 | 1 | 1387 | 0.1402 | 0.27451 | 14 | 0.080671
7893 | 0.9 | 1535 | 0.12543 | 0.29412 | 15 | 0.080957
7629 | 0.55 | 1319 | 0.079303 | 0.31373 | 16 | 0.081138
7510 | 0.76 | 1597 | 0.11132 | 0.33333 | 17 | 0.082004
8370 | 0.71 | 1696 | 0.093309 | 0.35294 | 18 | 0.082769
7807 | 0.63 | 1455 | 0.088766 | 0.37255 | 19 | 0.082823
7781 | 0.57 | 1410 | 0.080581 | 0.39216 | 20 | 0.084242
7499 | 1.08 | 1590 | 0.15842 | 0.41176 | 21 | 0.086352
7735 | 0.72 | 1828 | 0.10239 | 0.43137 | 22 | 0.086761
7604 | 0.95 | 1418 | 0.13743 | 0.45098 | 23 | 0.088766
7476 | 0.85 | 1350 | 0.12507 | 0.47059 | 24 | 0.089888
7629 | 0.52 | 1022 | 0.074977 | 0.4902 | 25 | 0.093309
8076 | 0.52 | 1083 | 0.070827 | 0.5098 | 26 | 0.09354
7991 | 0.51 | 1209 | 0.070204 | 0.52941 | 27 | 0.096706
8163 | 0.8 | 1306 | 0.1078 | 0.54902 | 28 | 0.10239
8241 | 0.65 | 1201 | 0.086761 | 0.56863 | 29 | 0.10388
7922 | 0.84 | 2120 | 0.11664 | 0.58824 | 30 | 0.1063
7730 | 0.73 | 1709 | 0.10388 | 0.60784 | 31 | 0.10709
7592 | 0.56 | 4277 | 0.081138 | 0.62745 | 32 | 0.1078
7836 | 0.59 | 1923 | 0.082823 | 0.64706 | 33 | 0.11083
7609 | 0.56 | 1531 | 0.080957 | 0.66667 | 34 | 0.11132
7763 | 0.52 | 1398 | 0.073683 | 0.68627 | 35 | 0.11349
8476 | 0.57 | 2774 | 0.073974 | 0.70588 | 36 | 0.11441
7993 | 0.41 | 1712 | 0.056424 | 0.72549 | 37 | 0.11664
7453 | 0.5 | 1789 | 0.073796 | 0.7451 | 38 | 0.11907
7748 | 0.47 | 1820 | 0.066727 | 0.76471 | 39 | 0.11997
7976 | 0.32 | 1650 | 0.044132 | 0.78431 | 40 | 0.12158
7654 | 0.56 | 1266 | 0.080481 | 0.80392 | 41 | 0.12507
8052 | 0.89 | 1058 | 0.12158 | 0.82353 | 42 | 0.12543
7794 | 0.89 | 1607 | 0.12561 | 0.84314 | 43 | 0.12561
7253 | 0.53 | 2003 | 0.080381 | 0.86275 | 44 | 0.13743
7048 | 0.89 | 1008 | 0.1389 | 0.88235 | 45 | 0.1389
7097 | 0.97 | 1172 | 0.15035 | 0.90196 | 46 | 0.1402
7668 | 0.83 | 1309 | 0.11907 | 0.92157 | 47 | 0.15035
7704 | 0.75 | 1390 | 0.10709 | 0.94118 | 48 | 0.15288
7307 | 0.76 | 2123 | 0.11441 | 0.96078 | 49 | 0.1547
6755 | 0.95 | 1055 | 0.1547 | 0.98039 | 50 | 0.15808
7832 | 0.64 | 1607 | 0.089888 | 1 | 51 | 0.15842

## Polk
Polk 1
ALPHA | BETA
0 | 0.6601
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
12931 | 0.12 | 1000 | 6.1257 | 0.041667 | 1 | 1.9674 | 6.1257 | 23 | 0.95833
12987 | 0.18 | 1100 | 9.149 | 0.083333 | 2 | 2.4414 | 9.149 | 24 | 1
12996 | 0.11 | 1100 | 5.5872 | 0.125 | 3 | 2.445 | 97.5th Percentile | 7.335
12997 | 0.09 | 800 | 4.571 | 0.16667 | 4 | 2.4468
12998 | 0.11 | 900 | 5.5863 | 0.20833 | 5 | 2.449 | Graph Title | Polk 1: 97.5th Percentile = 7.3350 lb Hg/TBtu
13009 | 0.09 | 600 | 4.5668 | 0.25 | 6 | 2.9381
13022 | 0.11 | 1000 | 5.576 | 0.29167 | 7 | 2.9429
13029 | 0.11 | 800 | 5.573 | 0.33333 | 8 | 2.9508
13036 | 0.09 | 1000 | 4.5573 | 0.375 | 9 | 2.9625
13053 | 0.11 | 1100 | 5.5628 | 0.41667 | 10 | 3.5291
13074 | 0.09 | 1000 | 4.5441 | 0.45833 | 11 | 4.5392
13088 | 0.09 | 1100 | 4.5392 | 0.5 | 12 | 4.5441
13093 | 0.07 | 1100 | 3.5291 | 0.54167 | 13 | 4.5573
13106 | 0.11 | 900 | 5.5403 | 0.58333 | 14 | 4.5668
13114 | 0.1 | 1000 | 5.0336 | 0.625 | 15 | 4.571
13369 | 0.06 | 1000 | 2.9625 | 0.66667 | 16 | 5.0336
13421 | 0.04 | 800 | 1.9674 | 0.70833 | 17 | 5.5403
13422 | 0.06 | 1000 | 2.9508 | 0.75 | 18 | 5.5628
13458 | 0.06 | 1000 | 2.9429 | 0.79167 | 19 | 5.573
13477 | 0.05 | 1200 | 2.449 | 0.83333 | 20 | 5.576
13480 | 0.06 | 1000 | 2.9381 | 0.875 | 21 | 5.5863
13489 | 0.05 | 1200 | 2.4468 | 0.91667 | 22 | 5.5872
13499 | 0.05 | 1100 | 2.445 | 0.95833 | 23 | 6.1257
13519 | 0.05 | 1300 | 2.4414 | 1 | 24 | 9.149

## Wabash
Wabash 1+1a
ALPHA | BETA
0 | 0.6747
H (lb/Btu) | Hg(ppm) | Cl(ppm) | lb Hg/TBtu | Cummulative Frequency | Index | Sorted lb Hg/TBtu
11539 | 0.084 | 317 | 4.9116 | 0.012658 | 1 | 1.255 | 8.2919 | 77 | 0.97468
11539 | 0.084 | 317 | 4.9116 | 0.025316 | 2 | 1.2923 | 9.779 | 78 | 0.98734
11594 | 0.094 | 358 | 5.4702 | 0.037975 | 3 | 1.3173 | 97.5th Percentile | 5.392
11594 | 0.094 | 358 | 5.4702 | 0.050633 | 4 | 2.2003
12276 | 0.111 | 666.7 | 6.1007 | 0.063291 | 5 | 2.4376 | Graph Title | Wabash 1+1a: 97.5th Percentile = 5.3920 lb Hg/TBtu
12276 | 0.127 | 658.1 | 6.98 | 0.075949 | 6 | 2.4754
12276 | 0.098 | 531.2 | 5.3862 | 0.088608 | 7 | 2.5402
12276 | 0.097 | 623.7 | 5.3312 | 0.10127 | 8 | 2.5537
12276 | 0.116 | 697.8 | 6.3755 | 0.11392 | 9 | 2.5646
12374 | 0.076 | 520.5 | 4.1439 | 0.12658 | 10 | 2.5992
12442 | 0.071 | 492.2 | 3.8502 | 0.13924 | 11 | 2.6224
12451 | 0.065 | 343.7 | 3.5222 | 0.1519 | 12 | 2.7882
12505 | 0.071 | 490.1 | 3.8308 | 0.16456 | 13 | 2.7882
12530 | 0.024 | 442.2 | 1.2923 | 0.17722 | 14 | 2.8126
12550 | 0.058 | 514.7 | 3.1181 | 0.18987 | 15 | 2.8413
12573 | 0.059 | 476.8 | 3.1661 | 0.20253 | 16 | 2.9258
12578 | 0.084 | 498.3 | 4.5059 | 0.21519 | 17 | 2.9808
12580 | 0.079 | 548.5 | 4.237 | 0.22785 | 18 | 2.9961
12598 | 0.078 | 491.9 | 4.1774 | 0.24051 | 19 | 3.0279
12660 | 0.078 | 532.5 | 4.1569 | 0.25316 | 20 | 3.0439
12662 | 0.08 | 480.4 | 4.2628 | 0.26582 | 21 | 3.0675
12663 | 0.06 | 282 | 3.1969 | 0.27848 | 22 | 3.1051
12666 | 0.091 | 345.3 | 4.8474 | 0.29114 | 23 | 3.1178
12718 | 0.084 | 492 | 4.4563 | 0.3038 | 24 | 3.1181
12749 | 0.048 | 472 | 2.5402 | 0.31646 | 25 | 3.1577
12782 | 0.084 | 522.9 | 4.434 | 0.32911 | 26 | 3.1661
12785 | 0.067 | 389 | 3.5358 | 0.34177 | 27 | 3.1969
12791 | 0.062 | 825 | 3.2704 | 0.35443 | 28 | 3.243
12796 | 0.132 | 426.5 | 6.96 | 0.36709 | 29 | 3.2488
12796 | 0.257 | 338 | 13.5509 | 0.37975 | 30 | 3.2704
12798 | 0.067 | 462 | 3.5322 | 0.39241 | 31 | 3.292
12800 | 0.067 | 450 | 3.5316 | 0.40506 | 32 | 3.3183
12805 | 0.025 | 318.9 | 1.3173 | 0.41772 | 33 | 3.3688
12816 | 0.087 | 478.6 | 4.5801 | 0.43038 | 34 | 3.5222
12818 | 0.064 | 406 | 3.3688 | 0.44304 | 35 | 3.5234
12820 | 0.06 | 692 | 3.1577 | 0.4557 | 36 | 3.5316
12820 | 0.059 | 462 | 3.1051 | 0.46835 | 37 | 3.5322
12823 | 0.054 | 366 | 2.8413 | 0.48101 | 38 | 3.5358
12825 | 0.053 | 591 | 2.7882 | 0.49367 | 39 | 3.5653
12825 | 0.053 | 252 | 2.7882 | 0.50633 | 40 | 3.6768
12830 | 0.067 | 745 | 3.5234 | 0.51899 | 41 | 3.7808
12833 | 0.186 | 322 | 9.779 | 0.53165 | 42 | 3.8308
12836 | 0.057 | 380 | 2.9961 | 0.5443 | 43 | 3.832
12845 | 0.07 | 464 | 3.6768 | 0.55696 | 44 | 3.8502
12853 | 0.073 | 400.9 | 3.832 | 0.56962 | 45 | 3.8689
12856 | 0.058 | 352 | 3.0439 | 0.58228 | 46 | 4.1439
12864 | 0.05 | 384 | 2.6224 | 0.59494 | 47 | 4.1569
12876 | 0.062 | 229 | 3.2488 | 0.60759 | 48 | 4.1774
12879 | 0.042 | 832 | 2.2003 | 0.62025 | 49 | 4.237
12899 | 0.062 | 313 | 3.243 | 0.63291 | 50 | 4.2628
12902 | 0.057 | 467 | 2.9808 | 0.64557 | 51 | 4.434
12903 | 0.024 | 499 | 1.255 | 0.65823 | 52 | 4.4563
12905 | 0.074 | 474 | 3.8689 | 0.67089 | 53 | 4.4839
12910 | 0.103 | 461.7 | 5.383 | 0.68354 | 54 | 4.5059
12912 | 0.063 | 434 | 3.292 | 0.6962 | 55 | 4.5801
12914 | 0.056 | 362 | 2.9258 | 0.70886 | 56 | 4.7898
12924 | 0.058 | 507 | 3.0279 | 0.72152 | 57 | 4.8082
12946 | 0.049 | 526 | 2.5537 | 0.73418 | 58 | 4.8474
12954 | 0.054 | 272 | 2.8126 | 0.74684 | 59 | 4.8746
12977 | 0.059 | 712 | 3.0675 | 0.75949 | 60 | 4.9116
12979 | 0.05 | 399 | 2.5992 | 0.77215 | 61 | 4.9116
12984 | 0.06 | 406 | 3.1178 | 0.78481 | 62 | 5.0676
13001 | 0.106 | 418.1 | 5.501 | 0.79747 | 63 | 5.2802
13009 | 0.047 | 743 | 2.4376 | 0.81013 | 64 | 5.2944
13013 | 0.064 | 532.6 | 3.3183 | 0.82278 | 65 | 5.3312
13019 | 0.16 | 260 | 8.2919 | 0.83544 | 66 | 5.383
13027 | 0.073 | 232 | 3.7808 | 0.8481 | 67 | 5.3862
13083 | 0.048 | 578 | 2.4754 | 0.86076 | 68 | 5.4702
13100 | 0.152 | 313 | 7.8286 | 0.87342 | 69 | 5.4702
13126 | 0.103 | 188 | 5.2944 | 0.88608 | 70 | 5.501
13154 | 0.05 | 555 | 2.5646 | 0.89873 | 71 | 5.9794
13202 | 0.117 | 347.2 | 5.9794 | 0.91139 | 72 | 6.1007
13241 | 0.094 | 281.7 | 4.7898 | 0.92405 | 73 | 6.3755
13247 | 0.07 | 755 | 3.5653 | 0.93671 | 74 | 6.96
13289 | 0.104 | 758 | 5.2802 | 0.94937 | 75 | 6.98
13314 | 0.1 | 351 | 5.0676 | 0.96203 | 76 | 7.8286
13392 | 0.089 | 291 | 4.4839 | 0.97468 | 77 | 8.2919
13426 | 0.097 | 306 | 4.8746 | 0.98734 | 78 | 9.779
13471 | 0.096 | 253 | 4.8082 | 1 | 79 | 13.5509

## SDAFF
Fabric Filter (Baghouse) with Spray Dryer Absorber
Plant | Unit | Tested Coal | Cl (ppm) "Xi" | Fremoved (Control) | -LN(1-Fremoved) "Yi" | Xi2 | XiYi | Calculated Fremoved from 2 Parameter Fit | (FrCal.-FrMea.)2
Stanton Station | 10 | Lignite | 28.3333 | 0.0147 | 0.014809 | 802.7778 | 0.41959 | 0.22988 | 0.046303 | A="ALPHA" | 0.002164 | Removal/Cl Curve
Coyote | 1 | Lignite | 100 | 0.3824 | 0.48191 | 10000 | 48.1914 | 0.34052 | 0.0017543 | B | 0.1999 | Cl (ppm) | Fremove
Sherburne County Generating Plant | #3 | Subbituminous | 102 | 0.0446 | 0.045625 | 10404 | 4.6538 | 0.34336 | 0.08926 | Minimum Removal | 0.18118 | 0 | 0.18118
Antelope Valley Station | B1 | Lignite | 107 | 0.3333 | 0.40542 | 11449 | 43.3794 | 0.35043 | 0.00029345 | EXP(-B)="BETA" | 0.81882 | 5 | 0.19
Craig | C3 | Subbituminous | 116.6667 | 0.336 | 0.40947 | 13611.1111 | 47.7719 | 0.36388 | 0.00077716 | Residual Variance | 0.018897 | 10 | 0.19871
Rawhide | 101 | Subbituminous | 126.6667 | 0.3183 | 0.38317 | 16044.4444 | 48.5343 | 0.3775 | 0.0035041 | Total Variance | 0.15714 | 15 | 0.20734
SEI - Birchwood Power Facility | 1 | Bituminous | 917.3333 | 0.9736 | 3.6344 | 841500.4444 | 3333.9483 | 0.88752 | 0.0074091 | Residual/Total | 0.12026 | 20 | 0.21587
Logan Generating Plant | GEN 1 | Bituminous | 1500 | 0.9752 | 3.6969 | 2250000 | 5545.3674 | 0.96812 | 5.0068e-05 | R | 0.9668 | 25 | 0.22431
Dwayne Collier Battle Cogeneration Facility | 2B | Bituminous | 1700 | 0.9366 | 2.7583 | 2890000 | 4689.0954 | 0.97932 | 0.0018252 | R**2 | 0.93469 | 30 | 0.23265
Mecklenburg Cogeneration Facility | GEN 1 | Bituminous | 1892.6667 | 0.9881 | 4.4312 | 3582187.1111 | 8386.8165 | 0.98637 | 2.9855e-06 |  |  | 35 | 0.24091
[12 empty] | 40 | 0.24908
[12 empty] | 45 | 0.25716
Fabric Filter (Baghouse) with Spray Dryer Absorber - Bituminous only
Plant | Unit | Tested Coal | Cl (ppm) "Xi" | Fremoved (Control) | -LN(1-Fremoved) "Yi" | Xi2 | XiYi | Calculated Fremoved from 2 Parameter Fit | (FrCal.-FrMea.)2
SEI - Birchwood Power Facility | 1 | Bituminous | 917.3333 | 0.9736 | 3.6344 | 841500.4444 | 3333.9483 | 0.88752 | 0.0074091 | A="ALPHA" | 0.00025804 | Removal/Cl Curve
Logan Generating Plant | GEN 1 | Bituminous | 1500 | 0.9752 | 3.6969 | 2250000 | 5545.3674 | 0.96812 | 5.0068e-05 | B | 3.2425 | Cl (ppm) | Fremove
Dwayne Collier Battle Cogeneration Facility | 2B | Bituminous | 1700 | 0.9366 | 2.7583 | 2890000 | 4689.0954 | 0.97932 | 0.0018252 | Minimum Removal | 0.96093 | 0 | 0.18118
Mecklenburg Cogeneration Facility | GEN 1 | Bituminous | 1892.6667 | 0.9881 | 4.4312 | 3582187.1111 | 8386.8165 | 0.98637 | 2.9855e-06 | EXP(-B)="BETA" | 0.039066 | 5 | 0.19
[10 empty] | Residual Variance | 0.0046437 | 10 | 0.19871
[10 empty] | Total Variance | 0.00049087 | 15 | 0.20734
[10 empty] | Residual/Total | 9.4602 | 20 | 0.21587
[10 empty] | R | -0.13691 | 25 | 0.22431
[10 empty] | R**2 | 0.018743 | 30 | 0.23265
[12 empty] | 35 | 0.24091
[12 empty] | 40 | 0.24908
Fabric Filter (Baghouse) with Spray Dryer Absorber - Bituminous only - Top 12% only | [11 empty] | 45 | 0.25716
Plant | Unit | Tested Coal | Cl (ppm) "Xi" | Fremoved (Control) | -LN(1-Fremoved) "Yi" | Xi2 | XiYi | Calculated Fremoved from 2 Parameter Fit | (FrCal.-FrMea.)2 |  |  | 50 | 0.26516
SEI - Birchwood Power Facility | 1 | Bituminous | 917.3333 | 0.9736 | 3.6344 | 841500.4444 | 3333.9483 | 0.88752 | 0.0074091 | A="ALPHA" | 0.00025847 | 55 | 0.27306
Dwayne Collier Battle Cogeneration Facility | 2B | Bituminous | 1700 | 0.9366 | 2.7583 | 2890000 | 4689.0954 | 0.97932 | 0.0018252 | B | 3.2194 | 60 | 0.28089
Mecklenburg Cogeneration Facility | GEN 1 | Bituminous | 1892.6667 | 0.9881 | 4.4312 | 3582187.1111 | 8386.8165 | 0.98637 | 2.9855e-06 | Minimum Removal | 0.96002 | 65 | 0.28863
[10 empty] | EXP(-B)="BETA" | 0.039979 | 70 | 0.29628
[10 empty] | Residual Variance | 0.0046187 | 75 | 0.30385
[10 empty] | Total Variance | 0.00070525 | 80 | 0.31135
[10 empty] | Residual/Total | 6.549 | 85 | 0.31876
[10 empty] | R | -0.1821 | 90 | 0.32609
[10 empty] | R**2 | 0.033162 | 95 | 0.33334
[12 empty] | 100 | 0.34052
[12 empty] | 105 | 0.34761
[12 empty] | 110 | 0.35463
[12 empty] | 115 | 0.36158
[12 empty] | 120 | 0.36845
[12 empty] | 125 | 0.37525
[12 empty] | 130 | 0.38197
[12 empty] | 135 | 0.38862
[12 empty] | 140 | 0.3952
[12 empty] | 145 | 0.40171
[12 empty] | 150 | 0.40815
[12 empty] | 155 | 0.41452
[12 empty] | 160 | 0.42082
[12 empty] | 165 | 0.42705
[12 empty] | 170 | 0.43322
[12 empty] | 175 | 0.43932
[12 empty] | 180 | 0.44535
[12 empty] | 185 | 0.45132
[12 empty] | 190 | 0.45722
[12 empty] | 195 | 0.46306
[12 empty] | 200 | 0.46884
[12 empty] | 205 | 0.47456
[12 empty] | 210 | 0.48021
[12 empty] | 215 | 0.48581
[12 empty] | 220 | 0.49134
[12 empty] | 225 | 0.49682
[12 empty] | 230 | 0.50223
[12 empty] | 235 | 0.50759
[12 empty] | 240 | 0.51289
[12 empty] | 245 | 0.51813
[12 empty] | 250 | 0.52331
[12 empty] | 255 | 0.52844
[12 empty] | 260 | 0.53352
[12 empty] | 265 | 0.53854
[12 empty] | 270 | 0.54351
[12 empty] | 275 | 0.54842
[12 empty] | 280 | 0.55328
[12 empty] | 285 | 0.55809
[12 empty] | 290 | 0.56284
[12 empty] | 295 | 0.56755
[12 empty] | 300 | 0.5722
[12 empty] | 305 | 0.5768
[12 empty] | 310 | 0.58136
[12 empty] | 315 | 0.58586
[12 empty] | 320 | 0.59032
[12 empty] | 325 | 0.59473
[12 empty] | 330 | 0.59909
[12 empty] | 335 | 0.6034
[12 empty] | 340 | 0.60767
[12 empty] | 345 | 0.61189
[12 empty] | 350 | 0.61607
[12 empty] | 355 | 0.6202
[12 empty] | 360 | 0.62429
[12 empty] | 365 | 0.62833
[12 empty] | 370 | 0.63233
[12 empty] | 375 | 0.63629
[12 empty] | 380 | 0.6402
[12 empty] | 385 | 0.64408
[12 empty] | 390 | 0.64791
[12 empty] | 395 | 0.6517
[12 empty] | 400 | 0.65544
[12 empty] | 405 | 0.65915
[12 empty] | 410 | 0.66282
[12 empty] | 415 | 0.66645
[12 empty] | 420 | 0.67004
[12 empty] | 425 | 0.67359
[12 empty] | 430 | 0.6771
[12 empty] | 435 | 0.68058
[12 empty] | 440 | 0.68401
[12 empty] | 445 | 0.68742
[12 empty] | 450 | 0.69078
[12 empty] | 455 | 0.69411
[12 empty] | 460 | 0.6974
[12 empty] | 465 | 0.70066
[12 empty] | 470 | 0.70388
[12 empty] | 475 | 0.70706
[12 empty] | 480 | 0.71022
[12 empty] | 485 | 0.71333
[12 empty] | 490 | 0.71642
[12 empty] | 495 | 0.71947
[12 empty] | 500 | 0.72249
[12 empty] | 505 | 0.72548
[12 empty] | 510 | 0.72843
[12 empty] | 515 | 0.73135
[12 empty] | 520 | 0.73424
[12 empty] | 525 | 0.7371
[12 empty] | 530 | 0.73993
[12 empty] | 535 | 0.74273
[12 empty] | 540 | 0.7455
[12 empty] | 545 | 0.74824
[12 empty] | 550 | 0.75095
[12 empty] | 555 | 0.75363
[12 empty] | 560 | 0.75628
[12 empty] | 565 | 0.7589
[12 empty] | 570 | 0.7615
[12 empty] | 575 | 0.76407
[12 empty] | 580 | 0.7666
[12 empty] | 585 | 0.76912
[12 empty] | 590 | 0.7716
[12 empty] | 595 | 0.77406
[12 empty] | 600 | 0.77649
[12 empty] | 605 | 0.7789
[12 empty] | 610 | 0.78128
[12 empty] | 615 | 0.78363
[12 empty] | 620 | 0.78596
[12 empty] | 625 | 0.78826
[12 empty] | 630 | 0.79054
[12 empty] | 635 | 0.79279
[12 empty] | 640 | 0.79502
[12 empty] | 645 | 0.79723
[12 empty] | 650 | 0.79941
[12 empty] | 655 | 0.80157
[12 empty] | 660 | 0.80371
[12 empty] | 665 | 0.80582
[12 empty] | 670 | 0.80791
[12 empty] | 675 | 0.80998
[12 empty] | 680 | 0.81202
[12 empty] | 685 | 0.81404
[12 empty] | 690 | 0.81604
[12 empty] | 695 | 0.81802
[12 empty] | 700 | 0.81998
[12 empty] | 705 | 0.82192
[12 empty] | 710 | 0.82384
[12 empty] | 715 | 0.82573
[12 empty] | 720 | 0.82761
[12 empty] | 725 | 0.82946
[12 empty] | 730 | 0.8313
[12 empty] | 735 | 0.83311
[12 empty] | 740 | 0.83491
[12 empty] | 745 | 0.83669
[12 empty] | 750 | 0.83844
[12 empty] | 755 | 0.84018
[12 empty] | 760 | 0.8419
[12 empty] | 765 | 0.8436
[12 empty] | 770 | 0.84529
[12 empty] | 775 | 0.84695
[12 empty] | 780 | 0.8486
[12 empty] | 785 | 0.85023
[12 empty] | 790 | 0.85184
[12 empty] | 795 | 0.85343
[12 empty] | 800 | 0.85501
[12 empty] | 805 | 0.85657
[12 empty] | 810 | 0.85812
[12 empty] | 815 | 0.85964
[12 empty] | 820 | 0.86115
[12 empty] | 825 | 0.86265
[12 empty] | 830 | 0.86413
[12 empty] | 835 | 0.86559
[12 empty] | 840 | 0.86703
[12 empty] | 845 | 0.86847
[12 empty] | 850 | 0.86988
[12 empty] | 855 | 0.87128
[12 empty] | 860 | 0.87267
[12 empty] | 865 | 0.87404
[12 empty] | 870 | 0.87539
[12 empty] | 875 | 0.87673
[12 empty] | 880 | 0.87806
[12 empty] | 885 | 0.87937
[12 empty] | 890 | 0.88067
[12 empty] | 895 | 0.88195
[12 empty] | 900 | 0.88322
[12 empty] | 905 | 0.88448
[12 empty] | 910 | 0.88572
[12 empty] | 915 | 0.88695
[12 empty] | 920 | 0.88817
[12 empty] | 925 | 0.88937
[12 empty] | 930 | 0.89056
[12 empty] | 935 | 0.89174
[12 empty] | 940 | 0.89291
[12 empty] | 945 | 0.89406
[12 empty] | 950 | 0.8952
[12 empty] | 955 | 0.89633
[12 empty] | 960 | 0.89744
[12 empty] | 965 | 0.89855
[12 empty] | 970 | 0.89964
[12 empty] | 975 | 0.90072
[12 empty] | 980 | 0.90179
[12 empty] | 985 | 0.90284
[12 empty] | 990 | 0.90389
[12 empty] | 995 | 0.90492
[12 empty] | 1000 | 0.90595
[12 empty] | 1005 | 0.90696
[12 empty] | 1010 | 0.90796
[12 empty] | 1015 | 0.90895
[12 empty] | 1020 | 0.90993
[12 empty] | 1025 | 0.9109
[12 empty] | 1030 | 0.91186
[12 empty] | 1035 | 0.91281
[12 empty] | 1040 | 0.91375
[12 empty] | 1045 | 0.91467
[12 empty] | 1050 | 0.91559
[12 empty] | 1055 | 0.9165
[12 empty] | 1060 | 0.9174
[12 empty] | 1065 | 0.91829
[12 empty] | 1070 | 0.91917
[12 empty] | 1075 | 0.92004
[12 empty] | 1080 | 0.9209
[12 empty] | 1085 | 0.92175
[12 empty] | 1090 | 0.92259
[12 empty] | 1095 | 0.92342
[12 empty] | 1100 | 0.92425
[12 empty] | 1105 | 0.92506
[12 empty] | 1110 | 0.92587
[12 empty] | 1115 | 0.92667
[12 empty] | 1120 | 0.92746
[12 empty] | 1125 | 0.92824
[12 empty] | 1130 | 0.92901
[12 empty] | 1135 | 0.92977
[12 empty] | 1140 | 0.93053
[12 empty] | 1145 | 0.93128
[12 empty] | 1150 | 0.93202
[12 empty] | 1155 | 0.93275
[12 empty] | 1160 | 0.93347
[12 empty] | 1165 | 0.93419
[12 empty] | 1170 | 0.9349
[12 empty] | 1175 | 0.9356
[12 empty] | 1180 | 0.93629
[12 empty] | 1185 | 0.93698
[12 empty] | 1190 | 0.93765
[12 empty] | 1195 | 0.93833
[12 empty] | 1200 | 0.93899
[12 empty] | 1205 | 0.93965
[12 empty] | 1210 | 0.9403
[12 empty] | 1215 | 0.94094
[12 empty] | 1220 | 0.94157
[12 empty] | 1225 | 0.9422
[12 empty] | 1230 | 0.94282
[12 empty] | 1235 | 0.94344
[12 empty] | 1240 | 0.94405
[12 empty] | 1245 | 0.94465
[12 empty] | 1250 | 0.94525
[12 empty] | 1255 | 0.94584
[12 empty] | 1260 | 0.94642
[12 empty] | 1265 | 0.94699
[12 empty] | 1270 | 0.94757
[12 empty] | 1275 | 0.94813
[12 empty] | 1280 | 0.94869
[12 empty] | 1285 | 0.94924
[12 empty] | 1290 | 0.94979
[12 empty] | 1295 | 0.95033
[12 empty] | 1300 | 0.95086
[12 empty] | 1305 | 0.95139
[12 empty] | 1310 | 0.95191
[12 empty] | 1315 | 0.95243
[12 empty] | 1320 | 0.95294
[12 empty] | 1325 | 0.95345
[12 empty] | 1330 | 0.95395
[12 empty] | 1335 | 0.95445
[12 empty] | 1340 | 0.95494
[12 empty] | 1345 | 0.95542
[12 empty] | 1350 | 0.9559
[12 empty] | 1355 | 0.95638
[12 empty] | 1360 | 0.95684
[12 empty] | 1365 | 0.95731
[12 empty] | 1370 | 0.95777
[12 empty] | 1375 | 0.95822
[12 empty] | 1380 | 0.95867
[12 empty] | 1385 | 0.95912
[12 empty] | 1390 | 0.95956
[12 empty] | 1395 | 0.95999
[12 empty] | 1400 | 0.96042
[12 empty] | 1405 | 0.96085
[12 empty] | 1410 | 0.96127
[12 empty] | 1415 | 0.96169
[12 empty] | 1420 | 0.9621
[12 empty] | 1425 | 0.96251
[12 empty] | 1430 | 0.96291
[12 empty] | 1435 | 0.96331
[12 empty] | 1440 | 0.9637
[12 empty] | 1445 | 0.9641
[12 empty] | 1450 | 0.96448
[12 empty] | 1455 | 0.96486
[12 empty] | 1460 | 0.96524
[12 empty] | 1465 | 0.96562
[12 empty] | 1470 | 0.96599
[12 empty] | 1475 | 0.96635
[12 empty] | 1480 | 0.96671
[12 empty] | 1485 | 0.96707
[12 empty] | 1490 | 0.96743
[12 empty] | 1495 | 0.96778
[12 empty] | 1500 | 0.96812
[12 empty] | 1505 | 0.96847
[12 empty] | 1510 | 0.96881
[12 empty] | 1515 | 0.96914
[12 empty] | 1520 | 0.96947
[12 empty] | 1525 | 0.9698
[12 empty] | 1530 | 0.97013
[12 empty] | 1535 | 0.97045
[12 empty] | 1540 | 0.97077
[12 empty] | 1545 | 0.97108
[12 empty] | 1550 | 0.97139
[12 empty] | 1555 | 0.9717
[12 empty] | 1560 | 0.97201
[12 empty] | 1565 | 0.97231
[12 empty] | 1570 | 0.9726
[12 empty] | 1575 | 0.9729
[12 empty] | 1580 | 0.97319
[12 empty] | 1585 | 0.97348
[12 empty] | 1590 | 0.97377
[12 empty] | 1595 | 0.97405
[12 empty] | 1600 | 0.97433
[12 empty] | 1605 | 0.9746
[12 empty] | 1610 | 0.97488
[12 empty] | 1615 | 0.97515
[12 empty] | 1620 | 0.97541
[12 empty] | 1625 | 0.97568
[12 empty] | 1630 | 0.97594
[12 empty] | 1635 | 0.9762
[12 empty] | 1640 | 0.97646
[12 empty] | 1645 | 0.97671
[12 empty] | 1650 | 0.97696
[12 empty] | 1655 | 0.97721
[12 empty] | 1660 | 0.97745
[12 empty] | 1665 | 0.9777
[12 empty] | 1670 | 0.97794
[12 empty] | 1675 | 0.97817
[12 empty] | 1680 | 0.97841
[12 empty] | 1685 | 0.97864
[12 empty] | 1690 | 0.97887
[12 empty] | 1695 | 0.9791
[12 empty] | 1700 | 0.97932
[12 empty] | 1705 | 0.97955
[12 empty] | 1710 | 0.97977
[12 empty] | 1715 | 0.97998
[12 empty] | 1720 | 0.9802
[12 empty] | 1725 | 0.98041
[12 empty] | 1730 | 0.98062
[12 empty] | 1735 | 0.98083
[12 empty] | 1740 | 0.98104
[12 empty] | 1745 | 0.98124
[12 empty] | 1750 | 0.98144
[12 empty] | 1755 | 0.98164
[12 empty] | 1760 | 0.98184
[12 empty] | 1765 | 0.98204
[12 empty] | 1770 | 0.98223
[12 empty] | 1775 | 0.98242
[12 empty] | 1780 | 0.98261
[12 empty] | 1785 | 0.9828
[12 empty] | 1790 | 0.98298
[12 empty] | 1795 | 0.98316
[12 empty] | 1800 | 0.98335
[12 empty] | 1805 | 0.98353
[12 empty] | 1810 | 0.9837
[12 empty] | 1815 | 0.98388
[12 empty] | 1820 | 0.98405
[12 empty] | 1825 | 0.98422
[12 empty] | 1830 | 0.98439
[12 empty] | 1835 | 0.98456
[12 empty] | 1840 | 0.98473
[12 empty] | 1845 | 0.98489
[12 empty] | 1850 | 0.98505
[12 empty] | 1855 | 0.98521
[12 empty] | 1860 | 0.98537
[12 empty] | 1865 | 0.98553
[12 empty] | 1870 | 0.98569
[12 empty] | 1875 | 0.98584
[12 empty] | 1880 | 0.98599
[12 empty] | 1885 | 0.98614
[12 empty] | 1890 | 0.98629
[12 empty] | 1895 | 0.98644
[12 empty] | 1900 | 0.98659
[12 empty] | 1905 | 0.98673
[12 empty] | 1910 | 0.98687
[12 empty] | 1915 | 0.98702
[12 empty] | 1920 | 0.98715
[12 empty] | 1925 | 0.98729
[12 empty] | 1930 | 0.98743

## FBC
Fabric Filter (Baghouse) with Fluidized Bed Combustion
Plant name | Unit name | Tested Coal | Cl in test coal (ppm) ="Xi" | Xi2 | Fremove (Control) | -LN(1-Fremove) ="Yi" | XiYi | Calculated Fr from 2 Parameter Fit | (Frmea.-Frcalc.)2
AES Hawaii, Inc. | A | Subbituminous | 45.6667 | 2085.4444 | 0.5252 | 0.74486 | 34.0153 | 0.76712 | 0.058523 | Xbar | 325.8 | Removal/Cl Curve
TNP-One | U2 | Lignite | 133.3333 | 17777.7778 | 0.5698 | 0.84351 | 112.4673 | 0.87238 | 0.091553 | Ybar | 3.3792 | Cl (ppm) | Fremove
Kline Township Cogen Facility | GEN1 | Waste Bituminous | 266.6667 | 71111.1111 | 0.9975 | 5.9915 | 1597.7239 | 0.94887 | 0.0023645 | SUMx2 | 791252.1111 | 0 | 0.68143
Stockton Cogen Company | GEN1 | Bituminous/Petroleum Coke | 583.3333 | 340277.7778 | 0.9182 | 2.5035 | 1460.3622 | 0.99418 | 0.0057726 | SUMxy | 7292.0358 | 10 | 0.70255
Scrubgrass Generating Company L. P. | GEN1 | Waste Bituminous | 600 | 360000 | 0.9989 | 6.8124 | 4087.4671 | 0.99481 | 1.6755e-05 | N | 5 | 20 | 0.72227
[10 empty] | A | 0.0068608 | 30 | 0.74069
[10 empty] | B | 1.1439 | 40 | 0.75788
[10 empty] | "ALPHA" | 0.0068608 | 50 | 0.77394
[10 empty] | "BETA" | 0.31857 | 60 | 0.78893
[10 empty] | Minimum Removal | 0.68143 | 70 | 0.80292
[10 empty] | Total Variance | 0.055257 | 80 | 0.81599
[10 empty] | Residual Variance | 0.052743 | 90 | 0.82819
[10 empty] | Residual/Total | 0.95452 | 100 | 0.83958
[10 empty] | R | 0.90508 | 110 | 0.85022
[10 empty] | R2 | 0.81918 | 120 | 0.86015
[12 empty] | 130 | 0.86943
[12 empty] | 140 | 0.87808
[12 empty] | 150 | 0.88617
[12 empty] | 160 | 0.89372
[12 empty] | 170 | 0.90076
[12 empty] | 180 | 0.90734
[12 empty] | 190 | 0.91349
[12 empty] | 200 | 0.91922
[12 empty] | 210 | 0.92458
[12 empty] | 220 | 0.92958
[12 empty] | 230 | 0.93425
[12 empty] | 240 | 0.93861
[12 empty] | 250 | 0.94268
[12 empty] | 260 | 0.94648
[12 empty] | 270 | 0.95003
[12 empty] | 280 | 0.95334
[12 empty] | 290 | 0.95644
[12 empty] | 300 | 0.95933
[12 empty] | 310 | 0.96202
[12 empty] | 320 | 0.96454
[12 empty] | 330 | 0.96689
[12 empty] | 340 | 0.96909
[12 empty] | 350 | 0.97114
[12 empty] | 360 | 0.97305
[12 empty] | 370 | 0.97484
[12 empty] | 380 | 0.97651
[12 empty] | 390 | 0.97806
[12 empty] | 400 | 0.97952
[12 empty] | 410 | 0.98088
[12 empty] | 420 | 0.98214
[12 empty] | 430 | 0.98333
[12 empty] | 440 | 0.98443
[12 empty] | 450 | 0.98547
[12 empty] | 460 | 0.98643
[12 empty] | 470 | 0.98733
[12 empty] | 480 | 0.98817
[12 empty] | 490 | 0.98895
[12 empty] | 500 | 0.98969
[12 empty] | 510 | 0.99037
[12 empty] | 520 | 0.99101
[12 empty] | 530 | 0.99161
[12 empty] | 540 | 0.99216
[12 empty] | 550 | 0.99268
[12 empty] | 560 | 0.99317
[12 empty] | 570 | 0.99362
[12 empty] | 580 | 0.99404
[12 empty] | 590 | 0.99444
[12 empty] | 600 | 0.99481