July 22, 1994

Contract #TW0592

SPECIAL SPECIFICATION

SECTION 13001

CLEAN ROOM SYSTEMS

Page

PART 1 - GENERAL

1.01  Contents..	2

1.02  Work Included.	2

1.03  Related Sections 	3

1.04  Clean Room Director.	3

1.05  Clean Construction Protocol.	5

1.06  Quality Assurance.	8

1.07  Submittals and Mockups.	9

1.08  Photographs.	13

1.09  Training and Badge Requirements.	14

PART 2 - PRODUCTS

2.01  Packaging.	15

PART 3 - EXECUTION

3.01  Installation.	16

3.02  Erection.	16

Attachment   Table 1 - Clean Room Protocol

SPECIAL SPECIFICATION

SECTION 13001

CLEAN ROOM SYSTEMS

PART 1 - GENERAL

1.01   CONTENTS

A.  		Work included.

B.  	Related work.

C.  	Clean Room Director.

D.  	Clean construction protocol.

E.  	Quality assurance.

F.  	Submittals and mockups.

G.  	Photographs.

H.  	Training and badge requirements.

1.02   WORK INCLUDED

A.  		This section specifies the requirements for the primary Clean Room contractor responsible for direction and coordination of all Clean Room activities.

B.  		The requirements and authority are established for the Clean Room Director to be provided by the Contractor.

C.  		The work of the following sections will be performed by other contractors, but the primary Clean Room Contractor responsible for this section shall be responsible for coordination of all related Clean Room construction activities.

1.  	Section 13007 - Clean Room Cleaning Procedures.

1.03   RELATED SECTIONS

A.  		This section shall be used in conjunction with the following specifications and related Contract Documents to establish the total requirements for the referenced Clean Room work.

1.  	Division 1 sections included in the project specifications.

2.  	Section 10270 - Access Flooring System.

3.  	Section 10615 - Clean Room Metal Wall Systems.

4.  	Section 15055 - Clean Room Testing and Certification.

5.  	Section 15175 - Clean Room Ceiling System.

6.  	Section 15833 - Clean Room Recirculation Air-Handling Units.

B.  		In the event of conflicting requirements for the work between this section and any other section, the provisions of this section shall govern.

1.04   CLEAN ROOM DIRECTOR

A.  	General:

1.  		The Contractor shall provide a Clean Room Director, hereinafter referred to as the "Director" for the duration of all construction and startup activities covered by this Section.

2.  		The Director shall act in SDR's best interests in successful completion of the project.

3.  		The Director shall solicit advice from SDR on matters peculiar to the type of project being built.

4.  		The Director shall attend all construction coordination meetings.

5.  		The Director shall log and document all staged construction events, as well as decisions made in the course of their completion.

6.  		The Director shall plan, organize, and lead the protocol training sessions required by all persons working in the Clean Room.

B.  	Authority:

1.  		The Director shall carry full authority over all construction personnel working within the Clean Room.

2.  		His authority over the construction personnel shall include:

a.  	Ability to remove incompetent or uncooperative workers from the site for breach of Clean Room protocol.

b.  	Require full compliance with project requirements.

c.  	Stop construction on specific tasks of the project not being built in conformance with the construction documents where the ultimate function of the clean room or its support systems could be jeopardized.

C.  	Qualifications:

1.  		The Director shall have a minimum of 10 years' experience constructing, testing, and qualifying clean rooms in the electronics industry.

2.  		The most recent project completion shall have been with the previous 2 years.

3.  		The Director shall have completed at least one project similar in design and style to the type being constructed of a multilevel fabrication area to perform submicron wafer technology under Class 10 or better conditions.

4.  		Previous projects supervised by the proposed Director shall not have been involved in litigation for reason of person integrity, building or utility system performance, or nonperformance or his employer.

5.  		Comparable experience in design, construction, or operation of cleanrooms will be considered by the SDR.

6.  		SDR reserves the right to accept or reject any proposed Clean Room Director candidate.

D.  	References:

1.  		A list shall be made available upon request to SDR of at least three projects completed within the last five years that involved the proposed Director.

2.  		The project name, address, and phone number of responsible people from the previous project for which he served as Clean Room Supervisor, Superintendent, or equivalent position shall be provided to SDR.

1.05   CLEAN CONSTRUCTION PROTOCOL

A.  	Cleaning:

1.  		Refer to Section 13007 for specific cleaning requirements.

2.  		The Contractor shall provide a cleanup crew to perform the following:

a.  	Continuous cleanup of construction site and Clean Room to meet cleanliness levels of each specific construction stage.

b.  	Supervision of people and materials entering the Clean Room.

3.  		Each Contractor working in the Clean Room is responsible for daily cleanup of his area.

4.  		The Contractor is responsible for the overall cleaning of the Clean Room, including any residue from other contractor activities.

a.  	Use a sweeping compound that will be antidusting for Stages of 1 and 2.  Sweep until areas are visibly free of debris and fine dust.  Excessive fine dust shall be wet mopped until removed.

b.  	Areas within the Clean Room during Stage 3 shall require 99.99 percent HEPA filtered vacuuming and wipedowns (course cleaning) as the only acceptable means of cleaning.

c.  	Prior commencement of Stage 3, the Director shall inspect the temporary staging and climate control facilities for compliance with the Contract Documents.

d.  	The Director will make reports of the clean levels with the Clean Room and provide a complete record of log tests on a weekly basis.

B.  		Schedule:  The Contractor shall be responsible for a schedule that will enhance the implementation of the clean protocols and scheduling the work of the cleanup crew.

C.  	Preenclosure Meeting:

1.  		Prior to completing the enclosure of Clean Room areas, the Contractor shall call a meeting to coordinate and explain cleaning procedures and requirements and to review the proposed staging areas.

2.  		Attendees shall include, but not be limited to, representatives from SDR, superintendents for all contractor performing work, and component manufacturers' representatives furnishing equipment and materials in the Clean Room.

3.  		Provide 7 days' prior notice of meeting to attendees.  The meeting shall be scheduled for 30 days prior to scheduled completion of Clean Room enclosure.

D. 	Staging Areas:

1.  		Provide continuous and uninterrupted staging areas and enclosed access routes to Clean Room.

a.  	Changing area to change work garments, shoes, and headgear.

b.  	Equipment and product staging areas for precleaning and assembly of products prior to entry into the Clean Room.

c.  	Isolated storage area for cleaned and tested materials, separate from precleaning and assembly areas.

d.  	Portable filtered shoe cleaner at each entrance from staging into Clean Room.

2.  		Provide shoe scrapers, grates, and cleanup mats at every entrance into the building to permit removal of mud and debris from shoes.

3.  		Create removable semipermanent barricades to restrict all movement of personnel and materials to several controlled entry points into the Clean Room.

4.  		Create a temporary contractors' gowning area in these central entry points to be used by all personnel. Outfit this area with hooks for hanging outdoor protective garments for all anticipated workers, plus an area for storage of outdoor shoes.  Future upgrade of these gowning areas will be required to permit better air cleanliness control and worker protocol.

5.  		Provide benches in these gowning areas, strategically located to create a barrier to unobstructed walk-through traffic.  The bench shall provide a convenient place to change from outdoor shoes to dedicated Clean Room shoes.  Everyone entering the Clean Room will be required to change into comfortable Clean Room shoes of his choice whenever entering, and likewise to remove the shoes when departing.

6.  Remove all flammable and odoriferous materials so that they are applied/stored outside the Clean Room.

7.  		Provide sufficient portable vertical laminar flow clean hoods over the storage racks for all Clean Room work garments.  Units shall be fitted with HEPA absolute filters rated at 99.99 percent on 0.3 micron particles, served with air at nominal 100 fpm downflow laminar flow velocity.

8.  		Install hanger rods or bar rods with hangers to be mounted underneath the vertical laminar flow hoods.  Provide sufficient storage for one dedicated garment for each worker who has been trained and authorized to enter the Clean Room, plus a quantity of 25 extra to be used by inspectors and SDR personnel.

E.  	Temporary Climate Control:

1.  		Maintain positive pressure within the Clean Room of 0.05-inch WC continuously during working and off-hours throughout Stages 2 through 5, or until permanent makeup air system is activated and the building has reached Class 5,000.

2.  		Provide temporary fans with 30 percent prefilters and 99.99 percent HEPA filters operating with 100 percent outside air.

a.  	Provide sufficient fans for six air changes per hour.

b.  	Replace prefilters and HEPA filters every 30 days minimum.

c.  	Operate fewer fans during off-peak hours, providing cleanliness requirements are maintained.

3.  		Provide emergency backup power to maintain climate control in the Clean Room.

F.  	Temporary Flooring, Partitions, and Doors:

1.  		Provide products that are water resistant, sealed against particle gathering or release, airtight, and suitable to maintain class requirements.

2.  		Door Hardware:  Provide automatic closure and self-latching key locks and National Guard Products, Inc. "Wild Hairs" seals at heads, jambs, and sills.

3.  		Door Frames:  22 gauge knockdown, as manufactured by Timely.

G.  	Temporary Signage:

1.  		Post the following sign at the entrance to personnel gowning and equipment staging areas:

a.  	Controlled area.

b.  	Before entering, contact SDR.

2.  	Material:

a. 		Sign:  Painted sheet metal.

b.  	Sign background color:  Safety yellow.

c.  		Lettering:  Two inches high with colors indicated.

3.  	Location:  Temporary mounting to entry doors.

1.06   QUALITY ASSURANCE

A. 	The SDR shall review the procedures and work performed on a continuous basis to verify compliance with these requirements.

1.  		Deviations to the specifications will be reported to SDR.

2. 		Deviations shall be corrected to the satisfaction of SDR prior to further work in the affected area.

3.  		Failure to achieve and maintain cleanliness levels shall require cleaning and retesting until specified Class is attained.

B.  	Training shall be provided for new personnel during construction.

C.  	Weekly reports shall be submitted to SDR that summarize the following activities:

1.  	Cleanup crew operations for the previous week.

2.  		Clean Room particle counts for each day of the previous week.

3.  		Updated list of visitors entering the Clean Room for the previous week.

4.  		Inventory list of tools, equipment, materials, and other items entering the Clean Room for the previous week.

5.  		Updated list of construction workers authorized/cleared for entry into the Clean Room for the upcoming week.

D.  		Factory test logs shall be submitted for all equipment and products used within the Clean Room to fully document the name of the quality control inspector, test date, original performance and test data logs, corrective action required, and final certified performance and test data logs.

E.  		Test data logs shall be included with each shipment for every item that is included therein, enclosed inside waterproof clear plastic jackets suitable for placing in a standard three-ring binder.

F.  		Every product shall include the final certified performance and test data information shown on a permanent nameplate, decal, or sticker located for easy viewing.

G.  		A qualified technical supervisor shall be furnished by all manufacturers whose Clean Room products require field application, assembly, or installation by workers who are not direct employees or the manufacturer.

H.  		Technical supervisor shall observe field conditions, qualify of surface finishes, and other field conditions essential to acceptance and use of the finished product.

I.  		During subsequent work activities by the installing workers, the manufacturer's technical supervisor shall provide periodic, timely inspection and counseling to ensure system complies with factory requirements.

J.  		Technical supervisor shall submit a written report to the SDR listing tasks performed, observations, and finished results.

K.  		Take particle counts within the Clean Room on a random schedule at least twice each week.  Maintain particle count records and submit as part of monthly status reports.

1.07   SUBMITTALS AND MOCKUPS

A.  		Shop Drawings:  Provide shop drawing submittals in accordance with Section 01300, Descriptive Submittals.

B.  	Performance and Method Statements:

1.  		Written performance and method statements shall be prepared and submitted by all specialty firms that will perform supplementary tasks and services for this project, as well as the management firm responsible for supervision of these services.

2.  		Statements shall outline the organization, manpower, procedures, sequence, products, and equipment to be used in performance of the service.

3.  		Performance/method statements shall be prepared for each of the construction cleanliness stages for the following activities and services.

a.  	Development, monitoring, and enforcement of clean construction protocol.

b.  	Construction, monitoring, and security of personnel, equipment, and process tool staging and entry areas.

c.  	Placement, use, and monitoring of temporary wall partitions, tacky mats, particle counters, lighting, and environmental air handlers.

d.  	Contents, format, and instructor for each protocol training class.

e.  	Organization, supervision, and enforcement to comply with special off-gas criteria.

f.  		Location, schedule, and procedures to create mockups of cleanroom systems.

g.  	Procedures for continuous and special cleaning where it differs from the specifications.

h.  	Procedures for Clean Room testing and certification where it differs from the specifications.

i.  		Procedures for air and water system testing and balancing where it differs from the specifications.

C.  	Mockups:

1.  		Factory Mockup of First Constructed Unit:

a.  	The first production unit of each type shall be assembled at the manufacturer's factory to demonstrate that the unit design can be constructed, matches the quality, and performs in accordance with the Contract Documents.  Factory test stand shall duplicate jobsite field conditions as closely as possible.

b.  	This demonstration unit must be complete with all components, accessories, and trim required by the finished installation. Fan/motor assemblies and movable devices must be operable.

c.  	This demonstration unit must be accepted by the SDR's review team prior to fabrication of the remainder of the units, unless waived by the SDR.

d.  	Modifications required by the SDR's review team must be incorporated into the design prior to fabrication of the remainder of the units.

e.  	Products and materials from the accepted mockup may be used in the completed work.

f.  		Factory mockup is required for the following:

1) 	Recirculation Air Handler:  One unit.

2) 	Makeup Air Handler:  One unit.

3) 	Clean Room Wall System:  Three panels.

4) Clean Room Ceiling System:  One module or 32 square feet.

5) 	VLF Tunnel Module:  One module.

6) 	Raised Access Floor:  16 square feet.

7) 	Clean Room Doors:  One unit.

8) 	Duct Discharge Plenum:  One unit.

g.  	SDR reserves the right to substitute procedures for a field mockup in lieu of the factory mockup for any product that is identical to one already constructed and in service in the field.

2.  	Field Mockup of Clean Room Systems:

a.  	A complete, full scale operable mockup of the proposed Clean Room shall be built at the jobsite to demonstrate the finished appearance, coordination, and operation of the assembled room components.

b.  	SDR will provide a dedicated area within the facility, completed with required services, where the mockup will be constructed.  The manufacturer shall be responsible for final hookup to utility services to enable operation.

c.  	Products and materials from the accepted mockup may be used in the completed work.

d.  	The manufacturer shall be responsible for assembling the products used for the mockup.  After inspection and approval, dismantle the mockup.  Either relocate it to the proper place on the jobsite, or remove it from the jobsite as directed.

e.  	Full operable field mockup is required for the following Clean Room Scheme:

1) 		Class 1 clean area incorporating at least 100 square feet, one zone of a recirculating air handler, or one packaged ceiling module, complete with:

a)  Recirculation air handler.

b)  Discharge plenum duct.

c)  Ceiling grid with sealant.

d)  ULPA filter modules with flexible ducts.

e)  Blank and trim panels.

f)  Light fixtures.

g)  Sprinkler heads and escutcheons.

h)  Wall panels.

i)  One window of each type.

j)  One door of each type.

k)  Raised floor panels of each type.

l)  Safety and emergency accessories.

2) 		Class 1,000 clean area incorporating at least 100 square feet complete with:

a)  Ceiling grid with sealant.

b)  HEPA filter modules with flexible ducts.

c)  Blank and trim panels.

d)  Light fixtures.

e)  Sprinkler heads and escutcheons.

f)  Wall panels.

g)  One window of each type.

h)  One door of each type.

i)  Raised floor panels of each type.

j)  Safety and emergency accessories.

f.  		Full room performance will be evaluated, including filter airflow velocity profiles, fan noise levels, light levels, and all construction details and finishes.

1.08   PHOTOGRAPHS

A.  	Fixed-Position Still Photography:

1.  		The Contractor shall place one camera on a fixed-position wall mounting bracket for the purpose of taking one still picture each work day.  Area to be photographed will be selected by the SDR.  Final pictures shall be 35-mm color prints.

2.  		The camera can either be rigged with an automatic timing device to take a picture at the same time each day, or the picture can be taken manually during regular routines of the photographer designated by the Director.

3.  		Pictures will commence at the beginning of Cleanliness Stage 2 construction and terminate at completion of the ceiling ULPA filter installation.

B.  		Mobile Video Camera Photography:

1.  		The Contractor shall furnish one complete video camera assembly and cassette film to photograph specific construction activities.

2.  		Pictures will be used for monitoring clean construction protocol, to record specific or special installation procedures, and to create general log of project construction completion.

3.  		Total site and building construction completion shall be documented once every 2 weeks in all areas of work.

4.  		Sections of the film shall be shown at each protocol training class as examples of good and bad construction practices among the workers.

1.09   TRAINING AND BADGE REQUIREMENTS

A.  	Training Sessions:

1.  		Mandatory construction protocol training sessions shall be organized for all workers who will be assigned tasks within the Clean Room.  Workers of all contractors shall undergo this training before they are permitted to work in the Clean Room.  Training sessions will be developed and presented by the Director in the presence of the SDR.

2.  		A system of Clean Room identification badges shall be implemented that permits the Director or any SDR's to know that the workers within the Clean Room have been properly trained in the three protocol training sessions and are permitted to work within the area.

PART 2 - PRODUCTS

2.01   PACKAGING

A.  		All materials and equipment intended for Clean Room duty must be removed from the pallets and containers that have been protected during storage in the manner prescribed.  All materials remaining in the storage container must remain covered as inventory is withdrawn in order to ensure all that remains stays in an enclosed, protected environment.

B.  		Any material specified to be fully enclosed in protective covers may be rejected by the Director prior to installation if cover has been damaged or removed.  If such material is deemed satisfactory to permit field cleanup, it shall be recleaned to match the condition in which it arrived on the jobsite.  If not, it shall be rejected and returned to the manufacturer.

C.  		No Clean Room materials shall be walked on or laid directly on the floor during the course of erection or assembly,  or it shall be rejected by the Director until it has been recleaned to match stored material standards.

PART 3 - EXECUTION

3.01   INSTALLATION

A.  		The nature of the completed facility demands special attention to maintaining an overall cleanliness in the project area.  Methods of construction which minimize the generation of contaminants are essential to avoid major cleanup problems.  The construction of the Clean Room represents a potential for surface contamination unless careful attention is paid to the manner in which the erection and placement is handled.

B.  		All installation methods shall be in accordance with the latest recommendations of the component manufacturer.

C.  		All installation procedures for Clean Room materials shall be done only by personnel who have received the Clean Room protocol training sessions.

D.  		All finished materials directly exposed to Clean Room operating procedures, or to the airstreams serving the Clean Rooms, shall only be unwrapped and installed in the Clean Room during final clean erection phase.

3.02   ERECTION

A.  		Verify dimensions of building shell structure by field measurements so that Clean Room work will be accurately designed, fabricated, and fitted to the structure.

B.  		Coordinate Clean Room work with the work of other sections and provide items to be placed during the installation of other work at the proper time to avoid delays in the work.

END OF SECTION

EXCEPT FOR ATTACHED TABLE