July 22, 1994

Contract #TW0592

SPECIAL SPECIFICATION

SECTION 16425

SWITCHBOARDS

PART 1 - GENERAL                                           						  Page

1.01 Related Documents	2

1.02 Summary 	2

1.03 Submittals	2

1.04 Quality Assurance	3

1.05 Delivery, Storage, and Handling	4

1.06 Extra Materials 	4

PART 2 - PRODUCTS

2.01 Manufacturers	5

2.02 Switchboards, General	5

2.03 Fabrication and Features	5

2.04 Overcurrent Protective Devices (OCPDs)	7

2.05 Instrumentation 	7

2.06 Control Power 	8

2.07 Ratings	8

2.08 Accessory Components and Features	8

2.09 Identification	9

PART 3 - EXECUTION

3.01 Installation 	10

3.02 Identification 	11

3.03 Grounding 	11

3.04 Connections	11

3.05 Field Quality Control	11

3.06 Cleaning 	13

3.07 Protection	14

3.08 Demonstration	14

3.09 Commissioning 	14

SPECIAL SPECIFICATION

SECTION 16425

SWITCHBOARDS

PART 1 - GENERAL

1.01  RELATED DOCUMENTS

A.  	Drawings and general provisions of Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

B.  	Requirements of the following Division 16 Sections apply to this Section:

1.  "Electrical Work."

1.02  SUMMARY

A.  	This Section includes low-voltage power service and distribution switchboards and associated auxiliary equipment rated 600 V or less.

B.  	Related Sections:  The following Division 16 sections contain requirements that relate to this Section:

1.  	"Overcurrent Protective Devices" for circuit breakers, fusible switches, fuses, and other similar devices used in switchboards.

2.  	"Electrical Identification" for identification and warning signs for switchboards and switchboard components.

1.03  SUBMITTALS

A.  	General:  Submit the following in accordance with Conditions of Contract and Division 1 Specification Sections.

B.  	Product data for each product and component specified.

C.  	Shop drawings for each switchboard including dimensioned plans and elevations, component and device lists, and a single-line diagram showing main and branch bus current ratings and short-time and short-circuit ratings of switchboard.

D.  	Shop drawings or other descriptive documentation of optional barriers specified for electrical insulation and isolation.

E.  	Schedule of features, characteristics, ratings, and factory settings of individual protective devices.

F.  	Manufacturer's Schematic Wiring Diagram.

G.  	Point-to-Point Control Wiring Diagram:  Differentiating between manufacturer-installed and field-installed wiring (may be submitted upon delivery of switchboard).

H.  	Qualification data for field-testing organization certificates, signed by the Contractor, certifying that the organization complies with the requirements specified in Quality Assurance below.  Include list of completed projects with project names, addresses, names of Architects and Owners, plus other information specified.

I.  	Report of field tests and observations certified by the testing organization.

J.  	Maintenance data for materials and products.

1.04  QUALITY ASSURANCE

A.  	Listing and Labeling:  Provide switchboard assemblies that are listed and labeled.

1.  	The terms "listed" and "labeled":  As defined in the National Electrical Code, Article 100.

2.  	Listing and Labeling Agency Qualifications:  A "Nationally Recognized Testing Laboratory" (NRTL) as defined in OSHA Regulation 1910.7.

B.  	Field-Testing Organization Qualifications:  To qualify for acceptance, the testing organization must demonstrate, based on evaluation of organization-submitted criteria conforming to ASTM E 699, that it has the experience and capability to conduct satisfactorily the testing indicated.

C.  	Sign Technician Qualifications:  Engage an experienced sign technician who is a professional installer/painter of signs to execute the mimic bus.

D.  	Electrical Component Standard:  Components and installation shall comply with NFPA 70, "National Electrical Code."

E.  	NEMA Standard:  Comply with NEMA Standard PB2, "Deadfront Distribution Switchboards."

F.  	UL Standard:  Comply with UL 891, "Deadfront Switchboards."

G.  Product Selection for Restricted Space:  The Drawings indicate maximum dimensions for switchboard equipment including clearances between switchboard and adjacent surfaces and items.  Switchboards having equal performance characteristics and complying with indicated maximum dimensions may be considered.

1.05  DELIVERY, STORAGE, AND HANDLING

A.  	Deliver in shipping splits of lengths that can be moved past obstructions in delivery path as indicated.

B.  	Store so condensation will not occur on or in switchboards.  Provide temporary heaters as required to assure avoiding condensation.

C.  	Handle switchboards in accordance with NEMA Standard PB2.1, "General Instructions for Proper Handling, Installation, Operation, and Maintenance of Deadfront Distribution Switchboards."  Use factory-installed lifting provisions.

1.06  EXTRA MATERIALS

A.  	Spare Fuses:  Six spares of each type and rating of fuse and fusible devices used.  Include spares for:

1.  	Control power fuses.

B.  	Spare Indicating Lights:  Six of each type installed.

C.  	Touch-Up Paint:  Three half-pint containers.

PART 2 - PRODUCTS

2.01  MANUFACTURERS

A.  	Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated in the Work include, but are not limited to, the following:

B.  	Manufacturers:  Subject to compliance with requirements, provide products by the following:

1.  ABB Power Distribution, Inc.

2.  Challenger Electrical Equipment Corp.

3.  General Electric Co.

4.  Siemens Energy & Automation, Inc.

5.  Square D Co.

6.  Westinghouse Electric Corp.

2.02  SWITCHBOARDS, GENERAL

A.  	Description:  Front-connected, front-accessible, with panel-mounted main device, panel-mounted branches, and sections rear aligned.

B.  	Description:  Front-connected, front-accessible, with fixed, individually mounted main device, panel-mounted branches, and sections rear aligned.

C.  	Description:  Front- and side-accessible section for fixed, individually mounted main device, panel-mounted branches, and sections rear aligned.

D.  	Description:  Front- and rear-accessible sections, front and rear aligned, with features as follows:

1.  Main Device:  Drawout mounted.

2.  Branch Devices:  Panel mounted.

E.  	Barriers:  Between adjacent switchboard sections.

1.  Insulation and isolation for main and vertical buses of feeder sections.

2.  Insulation and isolation for main bus and vertical bus.

2.03  FABRICATION AND FEATURES

A.  	Enclosure Finish for Indoor Units:  Manufacture standard gray finish over a rust inhibiting primer on phosphatizing treated metal surface.  Provide painted surfaces that conform to IEEE C37.20.1, "Standard for Metal-Enclosed Low-Voltage Power Circuit Breaker Switchgear," paragraph 5.2.8.

B.  	Bus Transition and Incoming Line Pull Sections:  Match and align with basic switchboard.

C.  	Removable Hinged Rear Covers:  Secured by captive thumb screws, for access to rear interior of switchboard.

D.  	Hinged Front Panels:  Provide to allow access to breaker, metering, accessory, and blank compartments.

E.  	Pull Box on Top of Switchboard:  Provide where required by installation conditions, and include the following features:

1.  	Adequate ventilation to maintain air temperature in pull box within same limits as switchboard.

2.  	Set back from front to clear circuit-breaker removal mechanism.

3.  	Removable covers forming top, front, and sides.  Top covers at rear easily removable for drilling and cutting.

4.  	Bottom of insulating, fire-resistant material with separate holes for cable drops into switchboards.

5.  	Cable supports arranged to facilitate cabling, and adequate to support cables indicated including those for future installation.

F.  	Buses and Connections:  Three-phase, four-wire except as otherwise indicated.  Features as follows:

1.  	Phase and Neutral Bus Material:  Hard-drawn copper of 98 percent conductivity with feeder circuit-breaker line connections.

2.  	At load terminals of feeder breakers, provide silver-plated copper bus extensions equipped with pressure terminal connectors for outgoing circuit conductors.

3.  	Ground Bus:  1/4-inch by 2-inch minimum size, hard-drawn copper of 98 percent conductivity, and equipped with pressure connector terminations for feeder- and branch-circuit ground conductors.  For busway feeders extend insulated equipment grounding cable to busway ground connection and support cable at intervals in vertical run.

4.  	Supports and Bracing for Buses:  Adequate strength for 30, 000 A short-circuit currents.

5.  	Contact Surfaces of Buses:  Silver plated.

6.  	Main Phase Buses, Neutral Bus, and Equipment Ground Bus:  Uniform capacity the entire length of the switchboard main and distribution sections.  Provide for future extensions from either end by means of bolt holes or other approved method and connecting links.

7.  	Isolation Barrier Access Provisions:  Permit checking bus bolt tightness.

8.  	Neutral Buses:  50 percent of the ampacity of the phase buses except as indicated, equipped with pressure connector terminations for outgoing circuit neutral cables.  Provide braced neutral bus extensions for busway feeders with neutral conductors.

G.  	Bus Bar Insulation:  Factory-applied, flame-retardant, 105 deg C minimum tape wrapping of individual bus bars or flame-retardant, spray-applied insulation of the same temperature rating.

1.  	Sprayed Insulation Thickness:  3 mils, minimum.

2.  	Bolted Bus Joints:  Insulate with joint covers after assembly.  Use secure covers that are easily removed and reinstalled.

3.  	Phase Bar Load Runbacks from OCPDs:  Increase insulation thickness where clearances prior to insulation are less than required for bare bus.

4.  	Substitute insulation methods will be considered upon submission, and where they are shown to provide equivalent electrical and mechanical characteristics to those specified, will be found acceptable.

2.04  OVERCURRENT PROTECTIVE DEVICES (OCPDs)

A.  	Comply with requirements of Division 16 Section "Overcurrent Protective Devices" for types of OCPDs indicated.  Provide indicated features, ratings, characteristics, and settings.

B.  	Future Devices:  Where provision for future overcurrent protective devices or space is indicated, equip compartments with mounting brackets, supports, bus connections, and necessary appurtenances, designed for the OCPD types and ampere ratings indicated for future installation of devices.

2.05INSTRUMENTATION

A.  	Instrument Transformers:  NEMA Standard EI 21.1, "Instrument Transformers for Revenue Metering 110 kV BIL and Less," IEEE Standard C57.13, "Requirements for Instrument Transformers," and the following:

1.  	Potential Transformers:  Secondary voltage rating of 120 V and NEMA accuracy class of 0.3 with burdens of W, X, and Y.

2.  	Current Transformers:  Ratios as indicated and accuracy class suitable for connected relays, meters, and instruments.

3.  	Control Power Transformers:  Dry type.  Separate compartments for units larger than 3 kV and their primary and secondary fuses.

4.  	Current Transformers for Neutral and Ground Fault Current Sensing:  Connect secondaries to ground overcurrent relays to provide selective tripping of bus tie and main breaker.  Coordinate with feeder breaker ground fault protection.

B.  	Multifunction Digital Metering Monitor:  Provide Power Lodic meters as described and in the quantity listed on the drawings.

2.06  CONTROL POWER

A.  	General:  Where electrically operated devices or ground fault relays requiring external power are required, provide 120-V control circuits supplied through secondary disconnect devices from control power transformer.

B.  	Control Power Fuses:  Include primary and secondary fuses for current-limiting and overload protection of transformer and fuses for protection of control circuits.

C.  	Control Wiring:  Factory-installed, complete with bundling, lacing, and protection.  Provide flexible conductors for No. 8 AWG and smaller, for conductors across hinges, and for conductors for interconnections between shipping units.

2.07  RATINGS

A.  	Provide nominal system voltage and continuous main bus amperage as indicated.

B.  	Nominal System Voltage:  480/277 V, 60 Hz.

C.  	Main Bus Continuous:  1200 amperes.

2.08  ACCESSORY COMPONENTS AND FEATURES

A.  	Accessory Set:  Include tools and miscellaneous items as required for overcurrent protective device test, inspection, maintenance, and operation.

B.  	Portable Test Set:  Arranged to permit testing of all functions of solid-state trip devices without removal from switchboard.  Include relay and meter test plugs suitable for testing switchboard meters and switchboard class relays.

C.  	Circuit-Breaker Removal Apparatus:  Overhead breaker lifting device, mounted at top front of switchboard and complete with hoist and lifting yokes matching each drawout breaker.

D.  	Fungus Proofing:  Permanent fungicidal treatment for switchboard interior including instruments and instrument transformers.

E.  	Kirk Key Interlocks:  Provide kirk key interlock sysyem between tie-breakers and adjacent main circuit breakers.  See drawing 104618E3.

2.09  IDENTIFICATION

A.  	General:  Refer to Division 16 Section "Electrical Identification."  Identify units, devices, controls, and wiring with factory-applied labels and signs.

B.  	Compartment Nameplates:  Engraved laminated plastic or metal nameplate for each compartment, mounted with corrosion-resistant screws.

PART 3 - EXECUTION

3.01  INSTALLATION

A.  	General:  Install switchboards and accessory items in accordance with manufacturers' written installation instructions and the following specifications:

B.  	Anchor each switchboard assembly to two 4-inch-minimum channel-iron sills arranged in accordance with manufacturer's recommendations.  Attach by tack welding or bolting.  Level and grout sills flush with switchboard mounting surface.

C.  	Strength, Spacing, and Placement of Equipment Housekeeping Pads:  Provide a concrete membrane-waterproofed floor or pressure slab housekeeping pad under the switchboard, and where otherwise indicated. Provide 4-inch channel sills specified above in the pad.  Fabricate pads as follows:

1.  	Coordinate size of equipment bases with actual unit sizes provided.  Fabricate base 4 inches larger in both directions than the overall dimensions of the supported unit.

2.  	Form concrete pads with ASTM A36 steel channels; size and location as indicated.  Miter and weld corners and provide cross bracing.  Anchor or key to floor slab.

3.  	Form concrete pads with framing lumber with form release compounds.  Chamfer top edge and corners of pad.

4.  	Install reinforcing bars, tied to frame, and place anchor bolts and sleeves to facilitate securing units.

5.  	Place concrete and allow to cure before installation of units.  Use Portland cement that conforms to ASTM C 150, 4000-psi compressive strength, and normal weight aggregate.

6.  	Clean exposed steel form in accordance with SSPC Surface Preparation Specifications SP 2 or SP 3, and apply 2 coats of rust-preventive metal primer.

7.  	Footings:  For outdoor switchboard pads, provide footings as indicated.

D.  	Temporary Lifting Provisions:  Remove temporary lifting eyes, channels, and brackets and temporary blocking of moving parts from switchboard units and components.

E.  	Operating Instructions:  Frame and mount printed, basic operating instructions for switchboards, including control and key interlocking sequences, and emergency procedures.  Fabricate frame of finished wood or metal and cover instructions with clear acrylic plastic.  Mount on the front of the switchboards.

3.02  IDENTIFICATION

A.  	Identify field-installed wiring and components and provide warning signs as specified in Division 16 Section "Electrical Identification."

3.03  GROUNDING

A.  	Connections:  As indicated.  Tighten connections to comply with tightening torques specified in UL 486A and 486B.

B.  	Ground equipment to main electrical ground bus indicated.  Provide minimum 5-ohm ground resistance at switchboard location.

3.04  CONNECTIONS

A.  	Tighten switchboard bus joint bolts and electrical connector and terminal bolts in accordance with manufacturer's published torque-tightening values.  Where manufacturer's torque values are not stated, use those specified in UL 486A and UL 486B.

3.05  FIELD QUALITY CONTROL

A.  	General:  Comply with applicable standards of the InterNational Electrical Testing Association (INETA) including Standard ATS, "Acceptance Testing Specifications for Electrical Power Distribution Equipment and Systems."

B.  	Manufacturer's Field Services:  Arrange and pay for the services of a factory-authorized service representative to supervise the pretesting and adjustment of switchboard components for a total or 5 working days.

C.  	Independent Testing Organization:  Arrange and pay for the services of an independent electrical testing organization to perform quality control electrical testing and calibration, visual and mechanical inspections, and tests of overcurrent protective devices switchboards.

D.  	Pretesting:  Upon completing installation of the system, perform the following preparations for tests:

1.  	Make insulation resistance tests of switchboard buses, components, and connecting supply, feeder, and control circuits.

2. 	Make continuity tests of circuits.

3.  	Provide set of Contract Documents to test organization.  Include full updating on final system configuration and parameters where they supplement or differ from those indicated in original Contract Documents.

4.  	Provide manufacturer's instructions for installation and testing of switchboard to test organization.

E.  	Quality Control Testing Program:  Conform to the following:

1.  	Program Objectives:  To assure switchboard installation meets specified requirements, is operational within specified tolerances, provides appropriate protection for systems and equipment, and is suitable for energizing.

2.  	Procedures:  Make field tests and inspections and prepare switchboard for satisfactory operation in accordance with manufacturer's recommendations and these specifications.

3.  	Schedule tests and notify Architect at least one week in advance of test commencement.

4.  	Reports:  Prepare written reports of test results and observations.  Report defective materials and workmanship.  Include complete records of adjustments and remedial efforts.

5.  	Labeling:  Upon satisfactory completion of tests and related effort.  Apply a label to tested components indicating test results, person responsible, and date.

6.  	Protective Device Ratings and Settings:  Verify indicated ratings and settings and make the final system adjustments of OCPDs in accordance with Division 16 Section "Overcurrent Protection Devices."

F.  	Visual and Mechanical Inspections:  Include the following inspections and related work:

1.  	Inspect for defects and physical damage, testing laboratory, labels, and nameplate compliance with up-to-date circuit connections.

2.  	Verify that potential transformers, including their overcurrent protection and current transformers, meet specified requirements.

3.  	Perform operational test and exercise of mechanical components and other operable devices in accordance with manufacturer's instruction manual.

4.  	Check switchboard anchorage, area clearances, and alignment and fit of components.

5.  	Check tightness of bolted electrical connections with calibrated torque wrench.  Refer to manufacturer's instructions for proper torque values.

6.  	Clean switchboard interior and exterior using manufacturer's approved methods and materials.

7.  	Perform visual and mechanical inspection and related work for OCPDs as specified in Section "Overcurrent Protective Devices."

G.  	Electrical Tests:  Include the following items performed in accordance with manufacturer's instruction:

1.  	Insulation resistance test of buses and portions of control wiring that disconnect from solid state devices through normal disconnecting features.  Insulation resistance less than 100 megohms is not acceptable.

2.  	Ratio and polarity tests on current and voltage transformers.

3.  	Ground resistance test on system and equipment ground connections.

4.  	Calibrate ammeters and voltmeters at midscale.  Use check instruments with documented up-to-date calibration traceable to NIST standards.

5.  	Verify appropriate capacity, overcurrent protection, and operating voltage of control power elements including control power transformer and control power wiring.

6.  	Calibrate watthour and demand meters to 0.5 percent, and verify meter multipliers.  Use check instruments with documented up-to-date calibration traceable to NIST standards.

7.  	Check phasing of alternate supply sources to the same bus.

8.  	Test overcurrent protective devices as specified in Section "Overcurrent Protective Devices."

H.  	Retesting:  Correct deficiencies identified by tests and observations and retest switchboards.  Verify by the retests that switchboards meet specified requirements.

3.06  CLEANING

A.  	Upon completion of installation, inspect interior and exterior of switchboards.  Remove paint splatters and other spots, dirt, and debris.  Touch up scratches and mars of finish to match original finish.

3.07  PROTECTION

A.  	Temporary Heating:  Apply temporary heat in accordance with manufacturer's recommendation within each section of switchboards throughout periods during which the switchboard is not in a space that is continuously under normal control of temperature and humidity.

3.08  DEMONSTRATION

A.  Training:  Arrange and pay for the services of factory-authorized service representatives to demonstrate switchboards and train Owner's maintenance personnel.

B.  	Training:  Conduct a minimum of one-half day of training in operation and maintenance as specified under "Instructions to Owner Employees" in the Division 1 Section "Project Closeout."  Include both classroom training and hands-on equipment operation and maintenance procedures.

C.  	Schedule training with at least seven days' advance notification.

3.09  COMMISSIONING

A.  	Infrared Scanning:  After Substantial Completion, but not more than 2 months after Final Acceptance, perform an infrared scan of switchboard bus joints and connections.  Open or remove metal doors, covers, inspection plates, and barriers to make joints and connections accessible to a portable scanner.

B.  	Follow-up Infrared Scanning:  Perform 2 additional follow-up infrared scans of the same joints and connections, one 4 months after Substantial Completion and one 11 months after Substantial Completion.

C.  	Instrument:  Use an infrared scanning device designed to measure temperature or detect significant deviations from normal values.  Provide documentation of device calibration.

D.  	Record of Infrared Scanning:  Prepare a certified report identifying all connections checked and describing results of scanning.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

END OF SECTION 16425