## Lighting Calcs
| Celilo Lighting Upgrade Recommendations 3/7/2005 | [12 empty] | Electric Rate = |  | 4.6 | cents/kwh
| Existing Condition |  |  |  |  | Proposed Condition |  |  |  |  | kWh Savings |  |  | Financial Summary
[12 empty] | Inter- |  |  |  | Contractor |  |  | Savings to
Description | Fixture | Watts | # of | Hours | kWh | Proposed | Watts | # of | Hours | kWh | Gross kWh | Action | Actual kWh | Potential | Dollars | or | Total | Simple | Investment
of Space | Type | Fixture | Fixtures | Year | Usage | Retrofit | Fixture | Fixtures | Year | Usage | Savings | Factor | Savings | Savings | Fixture | In-House | Investment | Payback | Ratio
SECOND FLOOR
Visitor's center
Stairway | 4x2 T-12 | 96 | 1 | 8760 | 840.96 | 2x4 T-8 | 48 | 1 | 8760 | 420.48 | 420.48 | 1 | 420.48
Hallway | 4x4 T-12 | 192 | 4 | 8760 | 6727.68 | 4x4 T-8 o.s. 30 min delay | 95 | 4 | 3000 | 1140 | 5587.68 | 1 | 5587.68
Mezanine | Flood | 20 | 75 | 8760 | 13140 | no retrofit | 20 | 75 | 8760 | 13140 | 0 | 1 | 0
Mezanine | Halogen | 100 | 10 | 100 | 100 | no retrofit | 100 | 10 | 100 | 100 | 0 | 1 | 0
Mezanine | Five Incan Chandeliers 5X9fix | 75 | 45 | 8760 | 29565 | (15) CFL Chandelier 15X9 fix | 23 | 135 | 8760 | 27199.8 | 2365.2 | 1 | 2365.2
Conference room hallway | 4x4 T-12 | 192 | 11 | 8760 | 18501.12 | 4x4 T-8 o.s. 30 min delay | 95 | 11 | 500 | 522.5 | 17978.62 | 1 | 17978.62
0
Conference room | 2x4 T-12 | 96 | 24 | 8760 | 20183.04 | 2x4 T-8 o.s. | 48 | 24 | 300 | 345.6 | 19837.44 | 1 | 19837.44
Kitchen area | 4x4 T-12 | 192 | 2 | 8760 | 3363.84 | 4x4 T-8 o.s.30 min delay | 95 | 2 | 350 | 66.5 | 3297.34 | 1 | 3297.34
Storage | 4x4 T-12 | 192 | 2 | 8760 | 3363.84 | 4x4 T-8 o.s. | 95 | 2 | 200 | 38 | 3325.84 | 1 | 3325.84
Men's restroom | 4x4 T-12 | 192 | 1 | 8760 | 1681.92 | 4x4 T-8 o.s. 30 min delay | 95 | 1 | 200 | 19 | 1662.92 | 1 | 1662.92
Men's restroom | 4x2 T-12 | 96 | 2 | 8760 | 1681.92 | 4x2 T-8 o.s. 30 min delay | 48 | 2 | 200 | 19.2 | 1662.72 | 1 | 1662.72
Women's restroom | 4x4 T-12 | 192 | 1 | 8760 | 1681.92 | 4x4 T-8 o.s. 30min delay | 95 | 1 | 200 | 19 | 1662.92 | 1 | 1662.92
Women's restroom | 4x2 T-12 | 96 | 1 | 8760 | 840.96 | 4x2 T-8 o.s. 30 min delay | 48 | 1 | 200 | 9.6 | 831.36 | 1 | 831.36
Room 207 (storage room) | 2x4 T-12 | 96 | 7 | 100 | 67.2 | 2x4 T-8 o.s. | 48 | 7 | 100 | 33.6 | 33.6 | 1 | 33.6
Conference room | 4x4 T-12 | 192 | 6 | 700 | 806.4 | 4x4 T-8 o.s. | 95 | 6 | 700 | 399 | 407.4 | 1 | 407.4
Office hallway | 4x4 T-12 | 192 | 8 | 8760 | 13455.36 | 4x4 T-8 o.s. 30 min dealy | 95 | 8 | 3000 | 2280 | 11175.36 | 1 | 11175.36
Office hallway | 4x2 T-12 | 96 | 1 | 8760 | 840.96 | 4x4 T-8 o.s. 30 min delay | 48 | 1 | 3000 | 144 | 696.96 | 1 | 696.96
Clerk's Office | 4x4 T-12 | 192 | 4 | 8760 | 6727.68 | 4x4 T-8 o.s. | 95 | 4 | 2300 | 874 | 5853.68 | 1 | 5853.68
FRED'S Office | 2-U tube T12 | 192 | 2 | 800 | 307.2 | 2xU T-8 o.s. | 95 | 2 | 800 | 152 | 155.2 | 1 | 155.2
FRED'S Office | 4x2 T-12 | 96 | 2 | 800 | 153.6 | 4x2 T-8 o.s. | 48 | 2 | 800 | 76.8 | 76.8 | 1 | 76.8
FRED'S Office | 4x4 T-12 | 192 | 2 | 800 | 307.2 | 4x4 T-8 o.s. | 95 | 2 | 800 | 152 | 155.2 | 1 | 155.2
Communication room | 4x4 T-12 | 192 | 15 | 650 | 1872 | 4x4 T-8 o.s. | 95 | 15 | 650 | 926.25 | 945.75 | 1 | 945.75
SPC AREA | [10 empty] | 0 | 1 | 0
Hallway | 2x4 T-12 | 96 | 9 | 8760 | 7568.64 | 2x4 T-8 o.s. 30 min delay | 48 | 9 | 3000 | 1296 | 6272.64 | 1 | 6272.64
Utility room | 2x4 T-12 | 96 | 2 | 1250 | 240 | 2x4 T-8 o.s. | 48 | 2 | 1250 | 120 | 120 | 1 | 120
Wayne's office | 4x4 T-12 | 192 | 4 | 2500 | 1920 | 4x4 T-8 o.s. | 95 | 4 | 2500 | 950 | 970 | 1 | 970
Kate's office | 4x4 T-12 | 192 | 6 | 400 | 460.8 | 4x4 T-8 o.s. | 95 | 6 | 400 | 228 | 232.8 | 1 | 232.8
SPC Lunch room | 3x4 T-12 | 144 | 15 | 8760 | 18921.6 | 3x4 T-8 o.s. 30 min delay | 73 | 15 | 2000 | 2190 | 16731.6 | 1 | 16731.6
SPC Office area | 4x4 T-12 | 192 | 17 | 8760 | 28592.64 | 4x4 T-8 o.s. | 95 | 17 | 2500 | 4037.5 | 24555.14 | 1 | 24555.14
IT Hallway | 4x4 T-12 | 192 | 3 | 8760 | 5045.76 | 4x4 T-8 o.s. 30 min delay | 95 | 3 | 3000 | 855 | 4190.76 | 1 | 4190.76
IT Office | 4x4 T-12 | 192 | 4 | 1500 | 1152 | 4x4 T-8 o.s. 30 min delay | 95 | 4 | 1500 | 570 | 582 | 1 | 582
Loren's office | 4x4 T-12 | 192 | 3 | 8760 | 5045.76 | 4x4 T-8 o.s. 30 min dealay | 95 | 3 | 2080 | 592.8 | 4452.96 | 1 | 4452.96
PING-PONG ROOM | 2x4 T-12 | 96 | 17 | 8760 | 14296.32 | 2x4 T-8 o.s. 30 min delay | 59 | 17 | 1300 | 1303.9 | 12992.42 | 1 | 12992.42
CONVERTER I | [10 empty] | 0 | 1 | 0
Stairway | 2x4 T-12 | 96 | 12 | 8760 | 10091.52 | 2x4 T-8 | 48 | 12 | 8760 | 5045.76 | 5045.76 | 1 | 5045.76
Converter attic | 2x4 T-12 | 96 | 16 | 8760 | 13455.36 | 2x4 T-8 | 48 | 16 | 8760 | 6727.68 | 6727.68 | 1 | 6727.68
(3) Vbe closets | 2x4 T-12 | 96 | 6 | 100 | 57.6 | No retrofit o.s. | 96 | 6 | 100 | 57.6 | 0 | 1 | 0
Valve Hall | HPS | 400 | 3 | 8760 | 10512 | No retrofit | 400 | 3 | 8760 | 10512 | 0 | 1 | 0
| HPS | 400 | 6 | 8760 | 21024 | No retrofit | 400 | 6 | 8760 | 21024 | 0 | 1 | 0
Battery Room | Incandescent | 100 | 3 | 150 | 45 | CFL o.s. | 25 | 3 | 150 | 11.25 | 33.75 | 1 | 33.75
CONVERTER II | [10 empty] | 0 | 1 | 0
Stairway | 2x4 T-12 | 96 | 12 | 8760 | 10091.52 | 2x4 T-8 | 48 | 12 | 8760 | 5045.76 | 5045.76 | 1 | 5045.76
Converter attic | 2x4 T-12 | 96 | 16 | 8760 | 13455.36 | 2x4 T-8 | 48 | 16 | 8760 | 6727.68 | 6727.68 | 1 | 6727.68
(3) Vbe closets | 2x4 T-12 | 96 | 6 | 100 | 57.6 | No retrofit o.s. | 96 | 6 | 100 | 57.6 | 0 | 1 | 0
Battery Room | Incandescent | 100 | 3 | 150 | 45 | CFL o.s. | 25 | 3 | 150 | 11.25 | 33.75 | 1 | 33.75
(2) Pits | 2x4 T-12 | 96 | 2 | 500 | 96 | 2x4 T-8 o.s. 30 min delay | 48 | 2 | 500 | 48 | 48 | 1 | 48
CRANE ROOM | 2x4 T-12 | 96 | 1 | 500 | 48 | 2x4 T-8 o.s. 30 min delay | 48 | 1 | 500 | 24 | 24 | 1 | 24
Equipment Area | Incandescent | 75 | 2 | 500 | 75 | CFL o.s. | 25 | 2 | 500 | 25 | 50 | 1 | 50
Control room (Air Handling) | 2x8 T-12 | 192 | 3 | 8760 | 5045.76 | 2x8 T-8 o.s. | 95 | 3 | 500 | 142.5 | 4903.26 | 1 | 4903.26
Control room (Air Handling) | 2x4 T-12 | 96 | 24 | 8760 | 20183.04 | 2x4 T-8 o.s. | 48 | 24 | 500 | 576 | 19607.04 | 1 | 19607.04
Control room (Air Handling) | 2x4 T-12 | 96 | 4 | 8760 | 3363.84 | 2x4 T-8 o.s. | 48 | 20 | 500 | 480 | 2883.84 | 1 | 2883.84
Belt room | 2x4 T-12 | 96 | 2 | 100 | 19.2 | 2x4 T-8 o.s. | 48 | 2 | 100 | 9.6 | 9.6 | 1 | 9.6
Group 1/2 Air Handler | 2x4 T-12 | 96 | 3 | 8760 | 2522.88 | 2x4 T-8 | 48 | 3 | 8760 | 1261.44 | 1261.44 | 1 | 1261.44
Group 1/2 Air Handler | 2x4 T-8 | 59 | 2 | 8760 | 1033.68 | No retrofit | 59 | 2 | 8760 | 1033.68 | 0 | 1 | 0
Group 3/4 Air Handler | 2x4 T-8 | 59 | 2 | 8760 | 1033.68 | No retrofit | 59 | 2 | 8760 | 1033.68 | 0 | 1 | 0
Group 5/6 Air Handler | 2x4 T-8 | 59 | 2 | 8760 | 1033.68 | No retrofit | 59 | 2 | 8760 | 1033.68 | 0 | 1 | 0
Stairway | 2x4 T-12 | 96 | 5 | 8760 | 4204.8 | 2x4 T-8 | 48 | 5 | 8760 | 2102.4 | 2102.4 | 1 | 2102.4
Exit 17 | Incandescent | 40 | 50 | 8760 | 17520 | LEDs | 1.5 | 50 | 8760 | 657 | 16863 | 1 | 16863
Converter 3/4 stairway | 2x4 T-12 | 96 | 9 | 8760 | 7568.64 | 2x4 T-8 | 48 | 9 | 8760 | 3784.32 | 3784.32 | 1 | 3784.32
FIRST FLOOR | [9 empty] | 0 | 0 | 1 | 0
Main Hallway | 2x8 T-12 | 192 | 72 | 1000 | 13824 | 2x8 T-8 30 min delay | 95 | 72 | 1000 | 6840 | 6984 | 1 | 6984
THYRISTOR room 1 | MH | 400 | 12 | 1000 | 4800 | no retrofit | 400 | 12 | 1000 | 4800 | 0 | 1 | 0
THYRISTOR room 2 | MH | 400 | 12 | 1000 | 4800 | no retrofit | 400 | 12 | 1000 | 4800 | 0 | 1 | 0
THYRISTOR room 3 | MH | 400 | 12 | 1000 | 4800 | no retrofit | 400 | 12 | 1000 | 4800 | 0 | 1 | 0
THYRISTOR room 4 | MH | 400 | 12 | 1000 | 4800 | no retrofit | 400 | 12 | 1000 | 4800 | 0 | 1 | 0
THYRISTOR room 5 | MH | 400 | 12 | 1000 | 4800 | no retrofit | 400 | 12 | 1000 | 4800 | 0 | 1 | 0
THYRISTOR room 6 | MH | 400 | 12 | 1000 | 4800 | no retrofit | 400 | 12 | 1000 | 4800 | 0 | 1 | 0
Marv's shop | 4x4 T-12 | 192 | 18 | 8760 | 30274.56 | 4x4 T-8 o.s. | 95 | 18 | 2200 | 3762 | 26512.56 | 1 | 26512.56
Marv's shop | 2-U tube T12 | 192 | 4 | 8760 | 6727.68 | 2xU T-8 o.s. | 95 | 4 | 2200 | 836 | 5891.68 | 1 | 5891.68
Assembly room | 6x2 T-12 | 144 | 24 | 2400 | 8294.4 | 6x2 T-8 o.s. 30 min delay | 73 | 24 | 2400 | 4204.8 | 4089.6 | 1 | 4089.6
Assembly office | 3x4 T-12 | 144 | 4 | 2400 | 1382.4 | 3x4 T-8 o.s. 30 min delay | 73 | 4 | 2400 | 700.8 | 681.6 | 1 | 681.6
Men's room | 2x4 T-12 | 96 | 4 | 8760 | 3363.84 | 2x4 T-8 o.s. 30 min delay | 48 | 4 | 200 | 38.4 | 3325.44 | 1 | 3325.44
Chris Office | 2x4 T-12 | 96 | 4 | 2400 | 921.6 | 2x4 T-8 o.s. | 48 | 4 | 2400 | 460.8 | 460.8 | 1 | 460.8
Assembly Room | 6x4 T-12 | 288 | 12 | 8760 | 30274.56 | 6x4 T-8 o.s. 30 min delay | 144 | 12 | 3000 | 5184 | 25090.56 | 1 | 25090.56
Degassing room | 6x4 T-12 | 288 | 28 | 2400 | 19353.6 | 6x4 T-8 o.s. | 144 | 28 | 2400 | 9676.8 | 9676.8 | 1 | 9676.8
Loading Area | 2x4 T-12 | 96 | 4 | 8760 | 3363.84 | 2x4 T-8 | 48 | 4 | 8760 | 1681.92 | 1681.92 | 1 | 1681.92
Hallway entry | 2x4 T-12 | 96 | 1 | 8760 | 840.96 | 2x4 T-8 | 48 | 1 | 8760 | 420.48 | 420.48 | 1 | 420.48
Convertor 1/2 storage | 2x4 T-12 | 96 | 25 | 8760 | 21024 | 2x4 T-8 o.s. | 48 | 25 | 200 | 240 | 20784 | 1 | 20784
Operation's room - main floor | 1x8 T-12 | 96 | 230 | 4380 | 96710.4 | 1x8 T-8 | 48 | 230 | 4380 | 48355.2 | 48355.2 | 1 | 48355.2
Operation's room - main floor | 1x4 T-12 | 48 | 26 | 4380 | 5466.24 | 1x4 T-8 | 30 | 2 | 4380 | 262.8 | 5203.44 | 1 | 5203.44
Storage room | Incandescent | 150 | 3 | 150 | 67.5 | CFL o.s. | 25 | 3 | 150 | 11.25 | 56.25 | 1 | 56.25
Operator Lunch room | 2x4 T-12 | 96 | 8 | 8760 | 6727.68 | 2x4 T-8 30 min delay | 48 | 8 | 8760 | 3363.84 | 3363.84 | 1 | 3363.84
Operator bathroom | 3x4 T-12 | 144 | 1 | 8760 | 1261.44 | 3x4 T-8 o.s. 30 min delay | 73 | 1 | 200 | 14.6 | 1246.84 | 1 | 1246.84
Operator bathroom | 2x4 T-12 | 96 | 1 | 8760 | 840.96 | 2x4 T-8 o.s. 30 min delay | 48 | 1 | 200 | 9.6 | 831.36 | 1 | 831.36
MSC (Master Control Center) | 4x4 T-12 | 192 | 8 | 8760 | 13455.36 | 4x4 T-8 | 95 | 8 | 8760 | 6657.6 | 6797.76 | 1 | 6797.76
Hallway | 2x4 T-12 | 96 | 10 | 8760 | 8409.6 | 2x4 T-8 o.s. 30 min delay | 48 | 10 | 2500 | 1200 | 7209.6 | 1 | 7209.6
Restroom | 4x4 T-12 | 192 | 1 | 8760 | 1681.92 | 4x4 T-8 o.s. 30 min delay | 95 | 1 | 200 | 19 | 1662.92 | 1 | 1662.92
Chief Operator's office | 4x4 T-12 | 192 | 8 | 2000 | 3072 | 4x4 T-8 o.s. | 95 | 8 | 2000 | 1520 | 1552 | 1 | 1552
Operator's office | 4x4 T-12 | 192 | 4 | 2000 | 1536 | 4x4 T-8 o.s. | 95 | 4 | 2000 | 760 | 776 | 1 | 776
Security ofice | 2x4 T-12 | 96 | 3 | 8760 | 2522.88 | 2x4 T-8 | 48 | 3 | 8760 | 1261.44 | 1261.44 | 1 | 1261.44
Foyer Front Desk | Incandescent | 75 | 4 | 8760 | 2628 | CFL | 25 | 4 | 8760 | 876 | 1752 | 1 | 1752
Main Floor | 4x4 T-12 | 192 | 38 | 8760 | 63912.96 | 4x4 T-8 | 95 | 38 | 8760 | 31623.6 | 32289.36 | 1 | 32289.36
Main Floor | 2x4 T-12 | 96 | 2 | 8760 | 1681.92 | 2x4 T-8 | 48 | 2 | 8760 | 840.96 | 840.96 | 1 | 840.96
Hallway | 4x4 T-12 | 192 | 1 | 8760 | 1681.92 | 4x4 T-8 o.s. 30 min delay | 95 | 1 | 2500 | 237.5 | 1444.42 | 1 | 1444.42
Women's Restroom | 3x4 T-12 | 144 | 2 | 8760 | 2522.88 | 3x4 T-8 o.s. 30 min delay | 73 | 2 | 200 | 29.2 | 2493.68 | 1 | 2493.68
Women's Restroom | 2x4 T-12 | 96 | 1 | 8760 | 840.96 | 2x4 T-8 o.s. 30 min delay | 48 | 1 | 200 | 9.6 | 831.36 | 1 | 831.36
Men's restroom | 3x4 T-12 | 144 | 2 | 8760 | 2522.88 | 3x4 T-8 o.s. 30 min delay | 73 | 2 | 200 | 29.2 | 2493.68 | 1 | 2493.68
Men's restroom | 2x4 T-12 | 96 | 1 | 8760 | 840.96 | 2x4 T-8 o.s. 30 min delay | 48 | 1 | 200 | 9.6 | 831.36 | 1 | 831.36
Janitor's | 1x4 T-12 | 48 | 1 | 2000 | 96 | 1x4 T-8 o.s. | 30 | 1 | 2000 | 60 | 36 | 1 | 36
C1/2 basement pump room | 2x4 T12 | 96 | 32 | 8760 | 26910.72 | 2x4 T-8 o.s. 30 min delay | 48 | 32 | 2500 | 3840 | 23070.72 | 1 | 23070.72
Main Basement hallway | 2x4 T12 | 96 | 48 | 8760 | 40366.08 | 2x4 T-8 o.s. on half of the fixtures | 48 | 48 | 5630 | 12971.52 | 27394.56 | 1 | 27394.56
Main Basement hallway | 2x4 T8 | 59 | 2 | 8760 | 1033.68 | No retrofit | 59 | 2 | 8760 | 1033.68 | 0 | 1
Main Basement hallway | 2x8 T12 | 192 | 35 | 8760 | 58867.2 | 2x8 T-8 o.s. on half of the fixtures | 95 | 35 | 5630 | 18719.75 | 40147.45 | 1
Motor Generator room | 2x4 T12 | 96 | 48 | 8760 | 40366.08 | 2x4 T-8 o.s. 30 min delay | 48 | 48 | 3500 | 8064 | 32302.08 | 1 | 32302.08
Room 65 station svc switchgear | 2x4 T12 | 96 | 30 | 3000 | 8640 | 2x4 T-8 o.s. | 48 | 30 | 800 | 1152 | 7488 | 1 | 7488
basement elevator landing | 2x4 T12 | 96 | 1 | 8760 | 840.96 | 2x4 T8 | 48 | 1 | 8760 | 420.48 | 420.48 | 1 | 420.48
small basement office by north elevator | 2x4 T12 | 96 | 2 | 200 | 38.4 | No retrofit. o.s. | 96 | 2 | 200 | 38.4 | 0 | 1 | 0
room 71 degassing cooler room | 2x4 T12 | 96 | 4 | 8760 | 3363.84 | 2x4 T-8 o.s. 30 min delay | 48 | 4 | 2500 | 480 | 2883.84 | 1 | 2883.84
room 71 degassing cooler room | 2x8 T12 | 192 | 10 | 8760 | 16819.2 | 2x8 T-8 o.s. 30 min delay | 95 | 10 | 2500 | 2375 | 14444.2 | 1 | 14444.2
tiny room by basement bathroom | 1x4 T-12 | 48 | 1 | 5000 | 240 | No retrofit o.s. | 48 | 1 | 100 | 4.8 | 235.2
Krueger's office | 2x8 T12 | 192 | 3 | 8760 | 5045.76 | 2x8 T-8 o.s. | 95 | 3 | 2500 | 712.5 | 4333.26 | 1 | 4333.26
tunnel - drive thru | incandescent | 75 | 34 | 8760 | 22338 | CFL turn the lights off at night | 23 | 34 | 2500 | 1955 | 20383 | 1 | 20383
South Basement hallway | 2x4 T12 | 96 | 4 | 8760 | 3363.84 | 2x4 T8 o.s 30 min delay | 48 | 4 | 2500 | 480 | 2883.84 | 1 | 2883.84
Elevator Mechanical room | 2x4 T12 | 96 | 2 | 20 | 3.84 | No retrofit o.s. | 96 | 2 | 20 | 3.84 | 0 | 1 | 0
room 61 | incandescent | 100 | 2 | 10 | 2 | CFLs | 23 | 2 | 10 | 0.46 | 1.54 | 1 | 1.54
Gold room (mechnical room) | 2x4 T12 | 96 | 9 | 8760 | 7568.64 | 2x8 T-8 o.s.30 min delay | 48 | 9 | 2000 | 864 | 6704.64 | 1 | 6704.64
north hallway bathroom | 2x4 T12 | 96 | 3 | 8760 | 2522.88 | 2x4 T-8 o.s. 30 min dealy | 48 | 3 | 1000 | 144 | 2378.88 | 1 | 2378.88
north hallway bathroom | 1x4 T12 | 48 | 1 | 8760 | 420.48 | 1x4 T-8 o.s. 30 min delay | 30 | 1 | 1000 | 30 | 390.48 | 1 | 390.48
North elevator mechanical room | 2x8 T12 | 192 | 3 | 8760 | 5045.76 | No retrofit Sign/turn the light off at night | 192 | 2 | 10 | 3.84 | 5041.92 | 1 | 5041.92
north hallway | 2x4 T12 | 96 | 6 | 8760 | 5045.76 | 2x4 T8 | 48 | 6 | 8760 | 2522.88 | 2522.88 | 1 | 2522.88
cable spreading room | 2x4 T12 | 96 | 34 | 8760 | 28592.64 | 2x4 T8 o.s 30 min delay | 48 | 34 | 2200 | 3590.4 | 25002.24 | 1 | 25002.24
cable spreading room | 3x4 T8 | 89 | 11 | 8760 | 8576.04 | 3x4 T8 o.s. 30 min delay | 73 | 11 | 2200 | 1766.6 | 6809.44 | 1 | 6809.44
cable spreading room | 3x4 T12 | 144 | 11 | 8760 | 13875.84 | 3x4 T8 o.s. 30 min delay | 73 | 11 | 2200 | 1766.6 | 12109.24 | 1 | 12109.24
cable spreading room | 2x8 T12 | 192 | 13 | 8760 | 21864.96 | 2x8 T8 o.s. 30 min dealy | 95 | 13 | 2200 | 2717 | 19147.96 | 1 | 19147.96
water package Hallway mechanical room | 2x4 T12 | 96 | 1 | 8760 | 840.96 | 2x4 T8 | 48 | 1 | 8760 | 420.48 | 420.48 | 1 | 420.48
water package Hallway mechanical room | 2x4 T12 | 96 | 7 | 10 | 6.72 | No retrofit | 96 | 1 | 10 | 0.96 | 5.76 | 1 | 5.76
water package Hallway mechanical room | 2x8 T12 | 192 | 10 | 10 | 19.2 | No retrofit | 192 | 10 | 10 | 19.2 | 0 | 1 | 0
room 64 sandblast room | 2x4 T12 | 96 | 8 | 10 | 7.68 | No retrofit | 96 | 8 | 10 | 7.68 | 0 | 1 | 0
Tiny room off of sandblast room | 2x4 T12 | 96 | 2 | 1 | 0.192 | No retrofit | 96 | 2 | 1 | 0.192 | 0 | 1 | 0
Battery Room | incandescnt | 150 | 6 | 10 | 9 | CFLs | 40 | 6 | 10 | 2.4 | 6.6 | 1 | 6.6
Cable Tunnel | incandescent | 75 | 54 | 200 | 810 | CFL turn the light on when in use | 23 | 54 | 200 | 248.4 | 561.6 | 1 | 561.6
Room 10 Equipment Storage | 2x4 T12 | 96 | 10 | 4500 | 4320 | 2x4 T8 o.s. | 48 | 10 | 2200 | 1056 | 3264 | 1 | 3264
Room 10 Equipment Storage | 3x4 T12 | 144 | 2 | 4500 | 1296 | 3x4 T8 o.s. | 73 | 2 | 2200 | 321.2 | 974.8 | 1 | 974.8
Room 10 Equipment Storage | 2x8 T12 | 192 | 2 | 4500 | 1728 | 2x8 T8 o.s. | 95 | 2 | 2200 | 418 | 1310 | 1 | 1310
Machine shop | 2x4 T12 | 96 | 6 | 4500 | 2592 | 2x4 T8 o.s. 30 min delay | 48 | 6 | 2200 | 633.6 | 1958.4 | 1 | 1958.4
Machine shop | 3x4 T8 | 89 | 24 | 4500 | 9612 | No retrofit o.s 30 min delay | 89 | 24 | 2200 | 4699.2 | 4912.8 | 1 | 4912.8
Machine shop | MH | 400 | 36 | 8760 | 126144 | No retrofit o.s. 30 min delay | 400 | 36 | 2000 | 28800 | 97344 | 1 | 97344
Machine shop (crane) | MH | 250 | 4 | 8760 | 8760 | No retrofit | 250 | 4 | 8760 | 8760 | 0 | 1 | 0
Maintenance bathroom | 2x4 T12 | 96 | 5 | 8760 | 4204.8 | 2x4 T8 o.s.30 min delay | 48 | 5 | 1000 | 240 | 3964.8 | 1 | 3964.8
Maintenance stairway north | 2x4 T12 | 96 | 3 | 8760 | 2522.88 | 2x4 T8 | 48 | 3 | 8760 | 1261.44 | 1261.44 | 1 | 1261.44
Maintenance stairway South | 2x4 T12 | 96 | 3 | 8760 | 2522.88 | 2x4 T8 | 48 | 3 | 8760 | 1261.44 | 1261.44 | 1 | 1261.44
Maintenance Lunchroom | 4x4 T-12 | 192 | 12 | 4500 | 10368 | 4x4 T-8 o.s. 30 min delay | 95 | 12 | 2200 | 2508 | 7860 | 1 | 7860
Maintenance Warehouse | 3x4 T8 | 96 | 46 | 8760 | 38684.16 | 3x4 T-8 o.s. | 96 | 46 | 2500 | 11040 | 27644.16 | 1 | 27644.16
Maintenance office hallway | 2x4 T12 | 96 | 4 | 8760 | 3363.84 | 2x4 T8 | 48 | 4 | 8760 | 1681.92 | 1681.92 | 1 | 1681.92
Karl's Office | 3x4 T12 | 144 | 6 | 4500 | 3888 | 3x4 T-8 dual o.s. | 73 | 6 | 2200 | 963.6 | 2924.4 | 1 | 2924.4
Room 1015 |  |  |  |  | 0 |  |  |  |  | 0 | 0 | 1 | 0
Upstairs maintenance mens room | 2x4 T12 | 96 | 4 | 8760 | 3363.84 | 2x4 T-8 o.s. 30 min delay | 48 | 4 | 500 | 96 | 3267.84 | 1 | 3267.84
Upstairs maintenance womens room | 2x4 T12 | 96 | 4 | 8760 | 3363.84 | 2x4 T-8 o.s. 30 min delay | 48 | 4 | 100 | 19.2 | 3344.64 | 1 | 3344.64
Room 1013 | 2x4 T12 | 96 | 1 | 20 | 1.92 | no retrofit | 96 | 1 | 20 | 1.92 | 0 | 1 | 0
Room 1008 (foreman room) | 3x4 T12 | 144 | 4 | 4000 | 2304 | 3x4 T-8 o.s. | 73 | 4 | 1000 | 292 | 2012 | 1 | 2012
Room 1009 (foreman room) | 3x4 T12 | 144 | 4 | 4000 | 2304 | 3x4 T-8 o.s. | 73 | 4 | 1000 | 292 | 2012 | 1 | 2012
Downstairs electricians office space | 4x4 T12 | 192 | 6 | 1500 | 1728 | 4x4 T-8 o.s. | 95 | 6 | 1000 | 570 | 1158 | 1 | 1158
C3/4 cooling bldg air inlet bay | 2x4 T12 | 96 | 4 | 8760 | 3363.84 | 2x4 T8 | 48 | 4 | 8760 | 1681.92 | 1681.92 | 1 | 1681.92
C3/4 cooling bldg air inlet bay | 2x4 T12 | 96 | 20 | 200 | 384 | no retrofit | 96 | 20 | 200 | 384 | 0 | 1 | 0
C3/4 cooling bldg control room | 3x4 T8 | 89 | 4 | 8760 | 3118.56 | no retrofit | 89 | 4 | 8760 | 3118.56 | 0 | 1 | 0
C3/4 cooling bldg control room | 3x4 T8 | 89 | 10 | 200 | 178 | no retrofit | 89 | 10 | 200 | 178 | 0 | 1 | 0
C3/4 cooling bldg air outlet bay & control room | MH | 400 | 2 | 8760 | 7008 | no retrofit | 400 | 2 | 8760 | 7008 | 0 | 1 | 0
C3/4 cooling bldg air outlet bay & control room | MH | 400 | 10 | 200 | 800 | no retrofit | 400 | 10 | 200 | 800 | 0 | 1 | 0
gp 7/8 ground floor main room | 2x4 T12 | 96 | 6 | 8760 | 5045.76 | 2x4 T8 | 48 | 6 | 8760 | 2522.88 | 2522.88 | 1 | 2522.88
gp 7/8 ground floor main room | 2x4 T12 | 96 | 24 | 500 | 1152 | 2x4 T8 | 48 | 24 | 500 | 576 | 576 | 1 | 576
gp 7/8 ground floor bathroom | 1x4 T12 | 48 | 2 | 10 | 0.96 | No retrofit o.s. 30 min delay | 48 | 2 | 10 | 0.96 | 0 | 1 | 0
GP 7/8 stairway | 1x4 T12 | 48 | 9 | 8760 | 3784.32 | 1x4 T-8 | 30 | 9 | 8760 | 2365.2 | 1419.12 | 1 | 1419.12
GP 7/8 3rd floor | 2x4 T12 | 96 | 25 | 4380 | 10512 | 2x4 T-8 o.s. | 48 | 25 | 400 | 480 | 10032 | 1 | 10032
Gp 7/8 controls room 2nd floor | 2x4 T12 | 96 | 14 | 4380 | 5886.72 | 2x4 T-8 o.s. | 48 | 14 | 400 | 268.8 | 5617.92 | 1 | 5617.92
GP 7/8 battery room 2nd floor | 2x4 T12 | 96 | 6 | 40 | 23.04 | no retrofit | 96 | 6 | 40 | 23.04 | 0 | 1 | 0
GP 7/8 storage room 2nd floor | 2x4 T12 | 96 | 16 | 50 | 76.8 | no retrofit | 96 | 16 | 50 | 76.8 | 0 | 1 | 0
GP 7/8 Bridge rooms | HPS | 250 | 16 | 8760 | 35040 | CFL/timer | 42 | 16 | 200 | 134.4 | 34905.6 | 1 | 34905.6
C1/2 cooling building Air inlet bay | 2x4 T12 | 96 | 4 | 8760 | 3363.84 | 2x4 T8 | 48 | 4 | 8760 | 1681.92 | 1681.92 | 1 | 1681.92
C1/2 cooling building Air inlet bay | 2x4 T12 | 96 | 24 | 200 | 460.8 | 2x4 T8 | 48 | 4 | 200 | 38.4 | 422.4 | 1 | 422.4
C1/2 cooling building Air outlet bay | MH | 400 | 2 | 8760 | 7008 | no retrofit | 400 | 2 | 8760 | 7008 | 0 | 1 | 0
C1/2 cooling building Air outlet bay | MH | 400 | 16 | 200 | 1280 | no retrofit | 400 | 16 | 200 | 1280 | 0 | 1 | 0
C1/2 cooling bldg control room | 3x4 T8 | 89 | 4 | 8760 | 3118.56 | no retrofit | 89 | 4 | 8760 | 3118.56 | 0 | 1 | 0
North Fence Building in C1/2 yard | 2x4 T12 | 96 | 6 | 10 | 5.76 | no retrofit | 96 | 6 | 10 | 5.76 | 0 | 1 | 0
Station Service #4 Bldg | incandescent | 60 | 6 | 40 | 14.4 | CFL | 15 | 6 | 40 | 3.6 | 10.8 | 1 | 10.8
Station Service #5 Bldg | incandescent | 60 | 6 | 40 | 14.4 | CFL | 15 | 6 | 40 | 3.6 | 10.8 | 1 | 10.8
AC Transformer Walkin | 2x4 T12 | 96 | 6 | 400 | 230.4 | 2x4 T8 | 48 | 6 | 400 | 115.2 | 115.2 | 1 | 115.2
DC Filter Walkin | 2x4 T12 | 96 | 3 | 400 | 115.2 | 2x4 T8 | 48 | 3 | 400 | 57.6 | 57.6 | 1 | 57.6
AC Filter Walkin | 2x4 T12 | 96 | 3 | 400 | 115.2 | 2x4 T8 | 48 | 3 | 400 | 57.6 | 57.6 | 1 | 57.6
C1/2 Yard lighting | HPS | 250 | 26 | 8760 | 56940 | photo cell | 250 | 26 | 4380 | 28470 | 28470 | 1 | 28470
C1/2 building mounted lights | HPS | 70 | 15 | 0 | 0 | No retrofit | 70 | 15 | 0 | 0 | 0 | 1 | 0
C1/2 cooling outside lights | HPS | 70 | 4 | 0 | 0 | No retrofit | 70 | 4 | 0 | 0 | 0 | 1 | 0
Middle driveway/rear entry | HPS | 70 | 6 | 0 | 0 | No retrofit | 70 | 6 | 0 | 0 | 0 | 1 | 0
Middle driveway/rear entry | HPS | 70 | 7 | 0 | 0 | No retrofit | 70 | 7 | 0 | 0 | 0 | 1 | 0
Middle driveway/rear entry | incandescent | 75 | 2 | 0 | 0 | No retrofit | 20 | 2 | 0 | 0 | 0 | 1 | 0
Street Lights | MH | 250 | 4 | 8760 | 8760 | No retrofit. photo cell | 250 | 4 | 4380 | 4380 | 4380 | 1 | 4380
Maintenance equipment garage | 3x4 T8 | 89 | 10 | 5000 | 4450 | No retrofit. o.s | 73 | 10 | 500 | 365 | 4085 | 1 | 4085
C3/4 (plus filters) Yard Lighting | MV | 125 | 253 | 8760 | 277035 | (CFL) RAB/photo cell/ wire half of the fitures with o.s. | 42 | 253 | 2100 | 22314.6 | 254720.4 | 1 | 254720.4
C3/4 (plus filters) Yard Lighting | incandescents | 200 | 13 | 0 | 0 |  |  |  |  | 0 | 0 | 1 | 0
C3/4 (plus filters) Yard Lighting | MV | 250 | 33 | 8760 | 72270 | No retrofit. photo cell | 250 | 33 | 4380 | 36135 | 36135 | 1 | 36135
C7/8 outside building lights | HPS | 125 | 4 | 8760 | 4380 | No retrofit. photo cell | 125 | 4 | 4380 | 2190 | 2190 | 1 | 2190
Parking lot lights | MH | 125 | 17 | 8760 | 18615 | No retrofit. photo cell | 125 | 17 | 4380 | 9307.5 | 9307.5 | 1 | 9307.5
Parking lot lights | MV | 250 | 5 | 8760 | 10950 | MH photo cell | 125 | 5 | 4380 | 2737.5 | 8212.5 | 1 | 8212.5
[7 empty] | TOTAL Fix: | 2439
[7 empty] | Fixtures | 933 | 46650 | dollars
[7 empty] | Fixt w/o.s. | 943 | 113160 | dollars
[11 empty] | GRAND |  | kWh savings | Savings |  | $/kwh | Investment | Payback | Sav/Invest
[11 empty] | TOTALS >> |  | 1242789.42 | 57168.3133
Lighting control
30 min delay
Hallways, Lunchrooms, Bathrooms,
Assembly areas, other Work areas
Factory set delay - 15 min
Individual Offices, Conference rooms,
Storage Rooms, Utility Rooms,
Warehouse Area, Athics,
Crowlspace, Closet, Janitor Rooms,
Mechnical/Electrical Rooms,
out Buildings