## list
source
cond
emiss
feed
process
df c8

## source
Source Description
Phase II ID No. | 767
EPA ID No. | TXD008077190
Facility Name | Goodyear Tire and Rubber Company
Facility Location
City | Beaumont
State | TX
Unit ID Name/No. | Boiler B-103
Other Sister Facilities | Boilers B-101, B-102, B-104, B-105 (all identical units)
Number of Sister Facilities | 4
Combustor Class | Liquid-fired boiler
Combustor Type | Liquid-fired
Combustor Characteristics | Watertube boiler. B&W Model FO-27, installed 1961, refractory-lined carbon steel, 100,000 lb/hr steam @ 50 psig, 100 MMBtu/hr heat input
Capacity (MMBtu/hr) | 100
Soot Blowing | Yes, typically once a week
APCS Detailed Acronym | None
APCS General Class
APCS Characteristics | NA
Hazardous Wastes | Liq
Haz Waste Description | Liq. wastes with hexane, benzene, isoprene, toluene, etc.
Supplemental Fuel | Natural gas
Stack Characteristics
Diameter (ft)
Height (ft)
Gas Velocity (ft/sec) | 37.4
Gas Temperature (°F) | 310.5
Permitting Status | Tier I metals, Tier III chlorine
HWC Burn Status (Date if Terminated)

## cond
Cond Description
767C1
Report Name/Date | Test Report for Recertification of Compliance of BIF Boilers B-101, B-102, B-103, B-104, & B-105, July 1995, Test Report II for ReCoC, Nov. 1995
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | 1995-07-11
Cond Dates | 1995-07-01
Condition Descr | CoC; max waste feedrate and steam prod rate
Content | PM, CO, HCl/Cl2
767C2
Report Name/Date | Test Report for Recertification of Compliance of BIF Boilers B-101, B-102, B-103, B-104, & B-105, July 1995, Test Report II for ReCoC, Nov. 1995
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | July 12-13, 1995
Cond Dates | 1995-07-01
Condition Descr | CoC; less aggressive max waste feed and max prod rate
Content | PM, CO, HCl/Cl2
767C3
Report Name/Date | Test Report for Recertification of Compliance of BIF Boilers B-101, B-102, B-103, B-104, & B-105, July 1995, Test Report II for ReCoC, Nov. 1995
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | 1995-07-27
Cond Dates | 1995-07-01
Condition Descr | CoC; min comb chamber exit temp
Content | CO
767C4
Report Name/Date | Test Report for Recertification of Compliance of BIF Boilers B-101, B-102, B-103, B-104, & B-105, July 1995, Test Report II for ReCoC, Nov. 1995
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | July 13-14, 1995
Cond Dates | 1995-07-01
Condition Descr | CoC; similar to C1 but higher prod rate, lower chamber temp
Content | PM, CO, HCl/Cl2
767C5
Report Name/Date | Test Report for Recertification of Compliance of BIF Boilers B-101, B-102, B-103, B-104, & B-105, July 1995, Test Report II for ReCoC, Nov. 1995
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | 1995-10-17
Cond Dates | 1995-10-01
Condition Descr | CoC; max prod rate, no ash spiking
Content | PM, CO
Report Name/Date | Trial Burn Report for BIF Boilers B101-B105, July 1999
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
767C6
Report Name/Date | Trial Burn Report for BIF Boilers B101-B105, July 1999
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | 1998-01-21
Cond Dates | 1998-01-01
Condition Descr | Trial burn, max waste feed, max steam prod
Content | DRE, CO
767C7
Report Name/Date | Trial Burn Report for BIF Boilers B101-B105, July 1999
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | 1998-01-23
Cond Dates | 1998-01-01
Condition Descr | Trial burn, min comb chamber temp
Content | DRE
767C8
Report Name/Date | Risk Burn Report for BIF Boilers B101-B105, Revision 1, July 1999
Report Prepare | The Goodyear Tire and Rubber Co. and Radian Corp.
Testing Firm | Radian Corp.
Testing Dates | January 26-28, 1998
Cond Dates | 1998-01-01
Condition Descr | Risk burn, worst case cond, max waste feed and max prod
Content | PCDD/PCDF, metals

## emiss
Stack Gas Emissions
|  | Comments | Units | 7% O2
Sootblowing
1 | 767C1 | Coc Testing |  |  | R1 | R2 | R3 | Cond Avg
| PM | E1 | gr/dscf | y | 0.036 | 0.031 | 0.096 | 0.035
| CO (RA) | E1 | ppmv | y | 0 | 3.8 | 8.1 | 3.9667
| CO (MHRA) | E1 | ppmv | y | 0 | 9 | 10 | 6.3333
| HCl |  | lb/hr |  | 1.56 | 1.65 | 1.57
| Cl2 |  | lb/hr |  | 0.022 | 0.028 | 0.058
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 28273 | 27821 | 26126 | 27406.6667
| O2 |  | % |  | 9.5 | 9.2 | 9.1 | 9.2667
| Moisture |  | % |  | 14.5 | 15.1 | 16.2 | 15.2667
| Temperature |  | °F |  | 303 | 315.3 | 310.68 | 309.66
| HCl | E1 | ppmv | y | 11.9935 | 12.5638 | 12.6233 | 12.3936
| Cl2 | E1 | ppmv | y | 0.086976 | 0.10964 | 0.2398 | 0.14547
| Total Chlorine | E1 | ppmv | y | 12.1675 | 12.7831 | 13.1029 | 12.6845
2 | 767C2 | CoC Testing |  |  | R1 | R2 | R3 | Cond Avg
Sootblowing
| PM | E1 | gr/dscf | y | 0.019 | 0.019 | 0.02 | 0.014
| CO (RA) | E1 | ppmv | y | 4.2 | 8.3 | 4.3 | 5.6
| CO (MHRA) | E1 | ppmv | y | 7 | 10 | 11 | 9.3333
| HCl |  | lb/hr |  | 1.49 | 1.54 | 1.38
| Cl2 |  | lb/hr |  | 0.042 | 0.24 | 0.015
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 27000 | 27000 | 27000 | 27000
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
| HCl | E1 | ppmv | y | 11.9955 | 12.0828 | 10.7365 | 11.6049
| Cl2 | E1 | ppmv | y | 0.17387 | 0.9683 | 0.06001 | 0.40073
| Total Chlorine | E1 | ppmv | y | 12.3432 | 14.0194 | 10.8565 | 12.4064
3 | 767C3 | CoC Testing |  |  | R1 | R2 | R3 | Cond Avg
| CO (RA) |  | ppmv | y | 0 | 0 | 0 | 0
| CO (MHRA) |  | ppmv | y | 0 | 0 | 0 | 0
4 | 767C4 | CoC Testing |  |  | R1 | R2 | R3 | Cond Avg
Sootblowing
| PM | E1 | gr/dscf | y | 0.027 | 0.019 | 0.075 | 0.028
| CO (RA) | E1 | ppmv | y | 3.2 | 38.4 | 42.5 | 28.0333
| CO (MHRA) | E1 | ppmv | y | 4 | 47 | 53 | 34.6667
| HCl |  | lb/hr | n | 1.65 | 1.03 | 0.88
| Cl2 |  | lb/hr | n | 0.027 | 0.021 | 0.035
| Sampling Train | PM, HCl/Cl2 | E1
| Stack Gas Flowrate |  | dscfm |  | 28000 | 28000 | 28000 | 28000
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
| HCl | E1 | ppmv | y | 12.8092 | 7.7927 | 6.6019 | 9.0679
| Cl2 | E1 | ppmv | y | 0.10778 | 0.081701 | 0.13502 | 0.10817
| Total Chlorine | E1 | ppmv | y | 13.0247 | 7.9561 | 6.872 | 9.2843
5 | 767C5 | CoC Testing |  |  | R1 | R2 | R3 | Cond Avg
Sootblowing
| PM | E1 | gr/dscf | y | 0.0018 | 0.0021 | 0.0092 | 0.0023
| CO | E1 | ppmv | y | 0 | 0 | 0 | 0
| Sampling Train | PM | E1
| Stack Gas Flowrate |  | dscfm |  | 34482 | 35458 | 34222 | 34720.6667
| O2 |  | %
| Moisture |  | %
| Temperature |  | °F
6 | 767C6 | Trial Burn |  |  | R1 | R2 | R3 | Cond Avg
| CO (MHRA) | E1 | ppmv | y | 30 | 2 | 32 | 21.3333
| POHC DRE | Toluene
| POHC Feedrate |  | lb/min |  | 1.86e-05 | 5.35e-05 | 1.96e-05
Emissions Rate
| DRE | E1 | % |  | 99.9998 | 99.9993 | 99.9965
| Sampling Train | CO, DRE | E1
| Stack Gas Flowrate |  | dscfm |  | 36884.9 | 35976.257 | 37561.732 | 36807.6297
| O2 |  | % |  | 10 | 8.7 | 9.4 | 9.3667
| Moisture |  | % |  | 9.88 | 10.81 | 10 | 10.23
| Temperature |  | °F |  | 306 | 308 | 303 | 305.6667
7 | 767C7 | Trial Burn |  |  | R1 | R2 | R3 | Cond Avg
| CO (MHRA) | E1 | ppmv | y | 0 | 0 | 0 | 0
| POHC DRE | Toluene
| POHC Feedrate |  | lb/min |  | 2.82e-05 | 3.52e-05 | 1.94e-05
Emissions Rate
| DRE | E1 | % |  | 99.9942 | 99.9948 | 99.9962
| Sampling Train | CO, DRE | E1
| Stack Gas Flowrate |  | dscfm |  | 20256.1276 | 21042.6655 | 20656.693 | 20651.8287
| O2 |  | % |  | 11.2 | 11.2 | 11.2 | 11.2
| Moisture |  | % |  | 9.76 | 9.4 | 9.6 | 9.5867
| Temperature |  | °F |  | 225 | 216 | 230 | 223.6667
8 | 767C8 | Risk Burn |  |  | R1 | R2 | R3 | Cond Avg
| Mercury |  | g/s |  | 2.85e-07 | 1.26e-07 | 7.47e-07
| Antimony |  | g/s |  | 6.28e-05 | 4.29e-05 | 3.37e-05
| Arsenic |  | g/s |  | 4.7e-05 | 3.39e-05 | 5e-05
| Barium |  | g/s |  | 3.94e-05 | 3.58e-05 | 3.94e-05
| Beryllium |  | g/s |  | 6.74e-06 | 8.68e-06 | 6.67e-06
| Cadmium |  | g/s |  | 1.72e-05 | 3.27e-05 | 2.24e-05
| Chromium |  | g/s |  | 2.5e-05 | 1.9e-05 | 0.000146
| Cobalt |  | g/s |  | 1.55e-05 | 3.86e-05 | 2.82e-05
| Lead |  | g/s |  | 4.48e-05 | 0.000402 | 0.000214
| Manganese |  | g/s |  | 3.73e-05 | 2.75e-05 | 3.73e-05
| Nickel |  | g/s |  | 8.2e-05 | 3.03e-05 | 4.46e-05
| Selenium |  | g/s |  | 3.42e-05 | 3.97e-05 | 2.4e-05
| Thallium |  | g/s |  | 0 | 0 | 0
| Vanadium |  | g/s |  | 1.97e-05 | 1.53e-05 | 7.2e-06
| Sampling Train | PCDD/PCDF | E1
| Stack Gas Flowrate |  | dscfm |  | 33985 | 34884 | 34327 | 34398.6667
| Moisture |  | % |  | 9.34 | 9.79 | 10.1 | 9.7433
| Temperature |  | °F |  | 299 | 304 | 301 | 301.3333
| Sampling Train | Metals | E2
| Stack Gas Flowrate |  | dscfm |  | 34549 | 32776 | 33898 | 33741
| Moisture |  | % |  | 10.7 | 10.9 | 10.3 | 10.6333
| Temperature |  | °F |  | 304 | 303 | 301 | 302.6667
| Mercury | E2 | µg/dscm | y | 0.021291 | 0.00967 | 0.054966 | 0.028642
| Antimony | E2 | µg/dscm | y | 4.6916 | 3.2924 | 2.4797 | 3.4879
| Arsenic | E2 | µg/dscm | y | 3.5112 | 2.6017 | 3.6791 | 3.264
| Barium | E2 | µg/dscm | y | 2.9434 | 2.7475 | 2.8991 | 2.8634
| Beryllium | E2 | µg/dscm | y | 0.50352 | 0.66615 | 0.49079 | 0.55349
| Cadmium | E2 | µg/dscm | y | 1.285 | 2.5096 | 1.6482 | 1.8143
| Chromium | E2 | µg/dscm | y | 1.8677 | 1.4582 | 10.743 | 4.6896
| Cobalt | E2 | µg/dscm | y | 1.158 | 2.9624 | 2.075 | 2.0651
| Lead | E2 | µg/dscm | y | 3.3469 | 30.8518 | 15.7466 | 16.6484
| Manganese | E2 | µg/dscm | y | 2.7866 | 2.1105 | 2.7446 | 2.5472
| Nickel | E2 | µg/dscm | y | 6.1259 | 2.3254 | 3.2818 | 3.911
| Selenium | E2 | µg/dscm | y | 2.555 | 3.0468 | 1.766 | 2.4559
| Thallium | E2 | µg/dscm | y | 0 | 0 | 0 | 0
| Vanadium | E2 | µg/dscm | y | 1.4717 | 1.1742 | 0.52979 | 1.0586
| SVM | E2 | µg/dscm | y | 4.6318 | 33.3614 | 17.3948 | 18.4627
| LVM | E2 | µg/dscm | y | 5.8824 | 4.726 | 14.9129 | 8.5071

## feed
Feedstreams
* | 767C1 | CoC Testing |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste | Spike | Spike | Spike | Spike | Natural gas | Natural gas | Natural gas | Natural gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 5413 |  | 5402 |  | 5400 |  | 5405 | 67.78 | 63.76 | 62.24 | 64.5933 | 889.3216 | 876.3855 | 768.1167 | 844.6079
| Thermal Feedrate |  | MMBtu/hr |  | 89.57 |  | 97.3375 |  | 66.84 |  | 84.5825 |  |  |  |  | 19.315 | 19.03 | 16.68 | 18.3417 |  | 108.885 |  | 116.3675 |  | 83.52 |  | 102.9242
| Heating Value |  | Btu/lb |  | 16546.8 |  | 18018.8 |  | 12378.2 |  | 15647.9333
| Moisture |  | wt % |  | 0.02 |  | 0.04 |  | 0.02 |  | 0.03
| Ash |  | lb/hr | nd | [7 empty] | 20.33 | 19.13 | 18.67 | 19.38
| Chlorine |  | lb/hr | nd | [7 empty] | 12.34 | 11.6 | 11.33 | 11.76
| Antimony |  | ppmw | nd | 0.75 | nd | 0.75 | nd | 0.75 |  | 0.75
| Arsenic |  | ppmw | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Barium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Beryllium |  | ppmw | nd | 0.05 | nd | 0.05 | nd | 0.05 |  | 0.05
| Cadmium |  | ppmw | nd | 0.25 | nd | 0.25 | nd | 0.25 |  | 0.25
| Chromium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Lead |  | ppmw |  | 0.3 |  | 0.3 | nd | 0.25 |  | 0.3
| Mercury |  | ppmw | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02
| Silver |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Thallium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Gas Flowrate |  |  |  | 28273 |  | 27821 |  | 26126 |  | 27406.6667 | 28273 | 27821 | 26126 | 27406.6667 | [5 empty] | 28273 |  | 27821 |  | 26126 |  | 27406.6667
| Oxygen |  |  |  | 9.5 |  | 9.2 |  | 9.1 |  | 9.2667 | 9.5 | 9.2 | 9.1 | 9.2667 | [5 empty] | 9.5 |  | 9.2 |  | 9.1 |  | 9.2667
| Estimated Firing Rate |  | MMBtu/hr | [23 empty] | 102.0862
Feedrate MTEC Calculations
| Ash |  | mg/dscm | [8 empty] | 234.0528 | 218.1255 | 224.7867 | 225.655 | [5 empty] | 234.0528 |  | 218.1255 |  | 224.7867 |  | 225.655
| Chlorine |  | ug/dscm | [8 empty] | 142066.4829 | 132266.3742 | 136413.1472 | 136915.3347 | [5 empty] | 142066.4829 |  | 132266.3742 |  | 136413.1472 |  | 136915.3347
| Antimony |  | ug/dscm | 100 | 46.7386 | 100 | 46.1963 | 100 | 48.762 | 100 | 47.2323 | [8 empty] | 100 | 46.7386 | 100 | 46.1963 | 100 | 48.762 | 100 | 47.2323
| Arsenic |  | ug/dscm | 100 | 18.6954 | 100 | 18.4785 | 100 | 19.5048 | 100 | 18.8929 | [8 empty] | 100 | 18.6954 | 100 | 18.4785 | 100 | 19.5048 | 100 | 18.8929
| Barium |  | ug/dscm | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882 | [8 empty] | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882
| Beryllium |  | ug/dscm | 100 | 3.1159 | 100 | 3.0798 | 100 | 3.2508 | 100 | 3.1488 | [8 empty] | 100 | 3.1159 | 100 | 3.0798 | 100 | 3.2508 | 100 | 3.1488
| Cadmium |  | ug/dscm | 100 | 15.5795 | 100 | 15.3988 | 100 | 16.254 | 100 | 15.7441 | [8 empty] | 100 | 15.5795 | 100 | 15.3988 | 100 | 16.254 | 100 | 15.7441
| Chromium |  | ug/dscm | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882 | [8 empty] | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882
| Lead |  | ug/dscm |  | 18.6954 |  | 18.4785 | 100 | 16.254 | 30.4223 | 17.8093 | [8 empty] | 0 | 18.6954 | 0 | 18.4785 | 100 | 16.254 | 30.4223 | 17.8093
| Mercury |  | ug/dscm | 100 | 1.2464 | 100 | 1.2319 | 100 | 1.3003 | 100 | 1.2595 | [8 empty] | 100 | 1.2464 | 100 | 1.2319 | 100 | 1.3003 | 100 | 1.2595
| Silver |  | ug/dscm | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882 | [8 empty] | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882
| Thallium |  | ug/dscm | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882 | [8 empty] | 100 | 31.1591 | 100 | 30.7975 | 100 | 32.508 | 100 | 31.4882
| SVM |  | ug/dscm | 45.4545 | 34.275 | 45.4545 | 33.8773 | 100 | 32.508 | 63.0699 | 33.5534 | [8 empty] | 45.4545 | 34.275 | 45.4545 | 33.8773 | 100 | 32.508 | 63.0699 | 33.5534
| LVM |  | ug/dscm | 100 | 52.9704 | 100 | 52.3558 | 100 | 55.2636 | 100 | 53.5299 | [8 empty] | 100 | 52.9704 | 100 | 52.3558 | 100 | 55.2636 | 100 | 53.5299
* | 767C2 | CoC Testing |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste | Spike | Spike | Spike | Spike | Natural gas | Natural gas | Natural gas | Natural gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 4952 |  | 4952 |  | 4953 |  | 5000 | 43.62 | 45.88 | 44.06 | 44
| Heating Value |  | Btu/lb |  | 15209.3 |  | 16179.7 |  | 15854 |  | 15854
| Moisture |  | wt % |  | 0.02 |  | 0.02 |  | 0.03 |  | 0.02
| Ash |  | lb/hr | nd | [6 empty] | 0 | 13.38 | 13.15 | 13.21 | 13.2
| Chlorine |  | lb/hr | nd | 0.2 |  | 0.2 |  | 0.2 |  | 0.001 | 8.1 | 7.93 | 8.04 | 8
| Antimony |  | ppmw | nd | 0.75 | nd | 0.75 | nd | 0.75 |  | 0.75
| Arsenic |  | ppmw | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Barium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Beryllium |  | ppmw | nd | 0.05 | nd | 0.05 | nd | 0.05 |  | 0.05
| Cadmium |  | ppmw | nd | 0.25 | nd | 0.25 | nd | 0.25 |  | 0.25
| Chromium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Lead |  | ppmw |  | 0.3 |  | 0.3 |  | 0.3 |  | 0.3
| Mercury |  | ppmw | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02
| Silver |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Thallium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Gas Flowrate |  |  |  | 27000 |  | 27000 |  | 27000 |  | 27000 | 27000 | 27000 | 27000 | 27000 | [5 empty] | 27000 |  | 27000 |  | 27000 |  | 27000
| Oxygen |  |  |  | 9.5 |  | 9.2 |  | 9.1 |  | 9.2667 | 9.5 | 9.2 | 9.1 | 9.2667 | [5 empty] | 9.5 |  | 9.2 |  | 9.1 |  | 9.2667
| Thermal Feedrate |  | MMBtu/hr |  | 75.3165 |  | 80.1219 |  | 78.5249 |  | 79.27 | [9 empty] | 75.3165 |  | 80.1219 |  | 78.5249 |  | 79.27
| Estimated Firing Rate |  | MMBtu/hr | [17 empty] | 98.5714 |  | 101.1429 |  | 102 |  | 100.5714
Feedrate MTEC Calculations
| Ash |  | mg/dscm | [7 empty] | 0 | 161.3024 | 154.4992 | 153.8999 | 156.5671 |  |  |  |  | 0 | 161.3024 | 0 | 154.4992 | 0 | 153.8999 | 0 | 156.5671
| Chlorine |  | ug/dscm | [8 empty] | 97649.4085 | 93169.4686 | 93668.0601 | 94828.9791 |  |  |  |  | 0 | 97649.4085 | 0 | 93169.4686 | 0 | 93668.0601 | 0 | 94828.9791
| Antimony |  | ug/dscm | 100 | 44.7741 | 100 | 43.6357 | 100 | 43.2778 | 100 | 43.8959 | [8 empty] | 100 | 22.387 | 100 | 21.8179 | 100 | 21.6389 | 100 | 43.8959
| Arsenic |  | ug/dscm | 100 | 17.9096 | 100 | 17.4543 | 100 | 17.3111 | 100 | 17.5583 | [8 empty] | 100 | 8.9548 | 100 | 8.7271 | 100 | 8.6556 | 100 | 17.5583
| Barium |  | ug/dscm | 100 | 29.8494 | 100 | 29.0905 | 100 | 28.8519 | 100 | 29.2639 | [8 empty] | 100 | 14.9247 | 100 | 14.5452 | 100 | 14.4259 | 100 | 29.2639
| Beryllium |  | ug/dscm | 100 | 2.9849 | 100 | 2.909 | 100 | 2.8852 | 100 | 2.9264 | [8 empty] | 100 | 1.4925 | 100 | 1.4545 | 100 | 1.4426 | 100 | 2.9264
| Cadmium |  | ug/dscm | 100 | 14.9247 | 100 | 14.5452 | 100 | 14.4259 | 100 | 14.632 | [8 empty] | 100 | 7.4623 | 100 | 7.2726 | 100 | 7.213 | 100 | 14.632
| Chromium |  | ug/dscm | 100 | 29.8494 | 100 | 29.0905 | 100 | 28.8519 | 100 | 29.2639 | [8 empty] | 100 | 14.9247 | 100 | 14.5452 | 100 | 14.4259 | 100 | 29.2639
| Lead |  | ug/dscm |  | 17.9096 |  | 17.4543 |  | 17.3111 |  | 17.5583 | [8 empty] | 0 | 17.9096 | 0 | 17.4543 | 0 | 17.3111 | 0 | 17.5583
| Mercury |  | ug/dscm | 100 | 1.194 | 100 | 1.1636 | 100 | 1.1541 | 100 | 1.1706 | [8 empty] | 100 | 0.59699 | 100 | 0.58181 | 100 | 0.57704 | 100 | 1.1706
| Silver |  | ug/dscm | 100 | 29.8494 | 100 | 29.0905 | 100 | 28.8519 | 100 | 29.2639 | [8 empty] | 100 | 14.9247 | 100 | 14.5452 | 100 | 14.4259 | 100 | 29.2639
| Thallium |  | ug/dscm | 100 | 29.8494 | 100 | 29.0905 | 100 | 28.8519 | 100 | 29.2639 | [8 empty] | 100 | 14.9247 | 100 | 14.5452 | 100 | 14.4259 | 100 | 29.2639
| SVM |  | ug/dscm | 45.4545 | 32.8343 | 45.4545 | 31.9995 | 45.4545 | 31.737 | 45.4545 | 32.1903 | [8 empty] | 22.7273 | 32.8343 | 22.7273 | 31.9995 | 22.7273 | 31.737 | 45.4545 | 32.1903
| LVM |  | ug/dscm | 100 | 50.7439 | 100 | 49.4538 | 100 | 49.0482 | 100 | 49.7486 | [8 empty] | 50 | 50.7439 | 50 | 49.4538 | 50 | 49.0482 | 100 | 49.7486
* | 767C3 | CoC Tesing |  |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste
| Feed Rate |  | lb/hr |  | 1126.8 |  | 1115.4 |  | 1120.7 |  | 1120.7
* | 767C4 | CoC Testing |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste | Spike | Spike | Spike | Spike | Natural gas | Natural gas | Natural gas | Natural gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 5350 |  | 5292 |  | 5264 |  | 5302 | 50.36 | 40.88 | 48.09 | 46.4433 | 2031.2731 | 2127.6344 | 2026.9229 | 2061.9435
| Thermal Feedrate |  | MMBtu/hr |  | 92.56 |  | 96.93 |  | 89.36 |  | 92.95 |  |  |  |  | 44.12 | 46.21 | 44.02 | 44.7833 |  | 136.68 |  | 143.14 |  | 133.38 |  | 137.7333
| Heating Value |  | Btu/lb |  | 17301.6 |  | 18316.8 |  | 17018.4 |  | 17116
| Moisture |  | wt % |  | 0.04 |  | 0.03 |  | 0.02 |  | 0.03
| Ash |  | lb/hr | [7 empty] | 0 | 15.11 | 12.26 | 14.43 | 13.9333
| Chlorine |  | lb/hr | [8 empty] | 9.17 | 7.44 | 8.75 | 8.4533
| Antimony |  | ppmw | nd | 0.75 | nd | 0.75 | nd | 0.75 |  | 0.75
| Arsenic |  | ppmw | nd | 0.3 | nd | 0.3 | nd | 0.3 |  | 0.3
| Barium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Beryllium |  | ppmw | nd | 0.05 | nd | 0.05 | nd | 0.05 |  | 0.05
| Cadmium |  | ppmw | nd | 0.25 | nd | 0.25 | nd | 0.25 |  | 0.25
| Chromium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Lead |  | ppmw |  | 0.3 |  | 0.3 |  | 0.3 |  | 0.3
| Mercury |  | ppmw | nd | 0.02 | nd | 0.02 | nd | 0.02 |  | 0.02
| Silver |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Thallium |  | ppmw | nd | 0.5 | nd | 0.5 | nd | 0.5 |  | 0.5
| Gas Flowrate |  |  |  | 28000 |  | 28000 |  | 28000 |  | 28000 | 28000 | 28000 | 28000 | 28000 | [5 empty] | 28000 |  | 28000 |  | 28000 |  | 28000
| Oxygen |  |  |  | 9.5 |  | 9.2 |  | 9.1 |  | 9.2667 | 9.5 | 9.2 | 9.1 | 9.2667 | [5 empty] | 9.5 |  | 9.2 |  | 9.1 |  | 9.2667
| Estimated Firing Rate |  | MMBtu/hr | [23 empty] | 104.2963
Feedrate MTEC Calculations
| Ash |  | mg/dscm | [8 empty] | 175.6527 | 138.8982 | 162.1092 | 158.8867 |  |  |  |  | 0 | 175.6527 | 0 | 138.8982 | 0 | 162.1092 | 0 | 158.8867
| Chlorine |  | ug/dscm | [8 empty] | 106600.6043 | 84290.5911 | 98299.0369 | 96396.7441 |  |  |  |  | 0 | 106600.6043 | 0 | 84290.5911 | 0 | 98299.0369 | 0 | 96396.7441
| Antimony |  | ug/dscm | 100 | 46.645 | 100 | 44.9663 | 100 | 44.3525 | 100 | 45.3213 | [8 empty] | 100 | 46.645 | 100 | 44.9663 | 100 | 44.3525 | 100 | 45.3213
| Arsenic |  | ug/dscm | 100 | 18.658 | 100 | 17.9865 | 100 | 17.741 | 100 | 18.1285 | [8 empty] | 100 | 18.658 | 100 | 17.9865 | 100 | 17.741 | 100 | 18.1285
| Barium |  | ug/dscm | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142 | [8 empty] | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142
| Beryllium |  | ug/dscm | 100 | 3.1097 | 100 | 2.9978 | 100 | 2.9568 | 100 | 3.0214 | [8 empty] | 100 | 3.1097 | 100 | 2.9978 | 100 | 2.9568 | 100 | 3.0214
| Cadmium |  | ug/dscm | 100 | 15.5483 | 100 | 14.9888 | 100 | 14.7842 | 100 | 15.1071 | [8 empty] | 100 | 15.5483 | 100 | 14.9888 | 100 | 14.7842 | 100 | 15.1071
| Chromium |  | ug/dscm | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142 | [8 empty] | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142
| Lead |  | ug/dscm |  | 18.658 |  | 17.9865 |  | 17.741 |  | 18.1285 | [8 empty] | 0 | 18.658 | 0 | 17.9865 | 0 | 17.741 | 0 | 18.1285
| Mercury |  | ug/dscm | 100 | 1.2439 | 100 | 1.1991 | 100 | 1.1827 | 100 | 1.2086 | [8 empty] | 100 | 1.2439 | 100 | 1.1991 | 100 | 1.1827 | 100 | 1.2086
| Silver |  | ug/dscm | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142 | [8 empty] | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142
| Thallium |  | ug/dscm | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142 | [8 empty] | 100 | 31.0967 | 100 | 29.9775 | 100 | 29.5684 | 100 | 30.2142
| SVM |  | ug/dscm | 45.4545 | 34.2064 | 45.4545 | 32.9753 | 45.4545 | 32.5252 | 45.4545 | 33.2356 | [8 empty] | 45.4545 | 34.2064 | 45.4545 | 32.9753 | 45.4545 | 32.5252 | 45.4545 | 33.2356
| LVM |  | ug/dscm | 100 | 52.8644 | 100 | 50.9618 | 100 | 50.2662 | 100 | 51.3641 | [8 empty] | 100 | 52.8644 | 100 | 50.9618 | 100 | 50.2662 | 100 | 51.3641
* | 767C5 | CoC Testing |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste | Spike | Spike | Spike | Spike | Natural gas | Natural gas | Natural gas | Natural gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 4160 |  | 4097 |  | 4074 |  | 4110 |  |  |  |  | 1064.0374 | 1109 | 1128.9802 | 1100.6725
| Stack Gas Flowrate |  | dscfm | [17 empty] | 34721 |  | 34721 |  | 34721 |  | 34721
| Estimated Firing Rate |  | MMBtu/hr | [17 empty] | 121.2479 |  | 121.2479 |  | 121.2479 |  | 121.2479
* | 767C6 | Trial Burn |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste | Toluene Spike | Toluene Spike | Toluene Spike | Toluene Spike | Nat gas | Nat gas | Nat gas | Nat gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 4883 |  | 5144 |  | 4906 |  | 4977 | 28.8 | 27.6 | 28.8 | 28.4
| Specific Gravity |  |  |  | 0.793 |  | 0.793 |  | 0.793 |  | 0.793
| Stack Gas Flowrate |  | dscfm |  | 36884.9 |  | 35976.257 |  | 37561.732 |  | 36807.6297 | [9 empty] | 36884.9 |  | 35976.257 |  | 37561.732 |  | 36807.6297
| Oxygen |  | % |  | 10 |  | 8.7 |  | 9.4 |  | 9.3667 | [9 empty] | 10 |  | 8.7 |  | 9.4 |  | 9.3667
| Estimated Firing Rate |  | MMBtu/hr | [23 empty] | 135.9351
* | 767C7 | Trial Burn |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste | Toluene Spike | Toluene Spike | Toluene Spike | Toluene Spike | Nat gas | Nat gas | Nat gas | Nat gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 1198 |  | 1117 |  | 1104 |  | 1140 | 27 | 27.6 | 28.8 | 27.8
| Specific Gravity |  |  |  | 0.772 |  | 0.772 |  | 0.772 |  | 0.772
| Stack Gas Flowrate |  | dscfm |  | 20256.1276 |  | 21042.6655 |  | 20656.693 |  | 20651.8287 | [9 empty] | 20256.1276 |  | 21042.6655 |  | 20656.693 |  | 20651.8287
| Oxygen |  | % |  | 11.2 |  | 11.2 |  | 11.2 |  | 11.2 | [9 empty] | 11.2 |  | 11.2 |  | 11.2 |  | 11.2
| Estimated Firing Rate |  | MMBtu/hr |  | 19.168 |  | 17.872 |  | 17.664 |  | 18.24 | [9 empty] | 19.168 |  | 17.872 |  | 17.664 |  | 18.24
| Estimated Firing Rate |  | MMBtu/hr | [23 empty] | 64.2501
* | 767C8 | Risk Burn |  |  | R1 |  | R2 |  | R3 |  | Cond Avg | R1 | R2 | R3 | Cond Avg | R1 | R2 | R3 | Cond Avg |  | R1 |  | R2 |  | R3 |  | Cond Avg
| Feedstream Number |  |  |  | F1 |  | F1 |  | F1 |  | F1 | F2 | F2 | F2 | F2 | F3 | F3 | F3 | F3 |  | F4 |  | F4 |  | F4 |  | F4
| Feed Class |  |  |  | Liq HW |  | Liq HW |  | Liq HW |  | Liq HW | Spike | Spike | Spike | Spike | NG | NG | NG | NG |  | Total |  | Total |  | Total |  | Total
| Feed Class 2 |  |  |  | HW |  | HW |  | HW |  | HW | Spike | Spike | Spike | Spike | MF | MF | MF | MF |  | Total |  | Total |  | Total |  | Total
| Feedstream Description |  |  |  | Waste |  | Waste |  | Waste |  | Waste | Toluene Spike | Toluene Spike | Toluene Spike | Toluene Spike | Nat gas | Nat gas | Nat gas | Nat gas |  | Total |  | Total |  | Total |  | Total
| Feed Rate |  | lb/hr |  | 5103 |  | 5056 |  | 5056 |  | 5000
| Stack Gas Flowrate |  | dscfm |  | 34549 |  | 32776 |  | 33898 |  | 33741 | [9 empty] | 34549 |  | 32776 |  | 33898 |  | 33741
| Oxygen |  | % |  | 10.7 |  | 10.9 |  | 10.3 |  | 10.6333 | [9 empty] | 10.7 |  | 10.9 |  | 10.3 |  | 10.6333
| Estimated Firing Rate |  | MMBtu/hr | [23 empty] | 111.0418

## process
Process Information
767C1
Steam Prod | lb/hr | 72800
Comb Cham Exit Temp | oF | 763
767C2
Steam Prod | lb/hr | 82800
Comb Cham Exit Temp | oF | 783
767C3
Steam Prod | lb/hr | 30900
Comb Cham Exit Temp | oF | 587
767C4
Steam Prod | lb/hr | 87400
Comb Cham Exit Temp | oF | 797
767C5
Steam Prod | lb/hr | 103000
Comb Cham Exit Temp | oF | 784
767C6
Steam Prod | lb/hr | 102000
Comb Cham Exit Temp | oF | 803
767C7
Steam Prod | lb/hr | 46400
Comb Cham Exit Temp | oF | 620
767C8
Steam Prod | lb/hr | 102000
Comb Cham Exit Temp | oF | 776

## df c8
PCDD/PCDF
N
Facility Name and ID: |  | Goodyear Tire and Rubber Company, 767
Condition ID: |  | 767C8
Condition/Test Date: |  | Risk burn, maximum waste feed and maximum steam production condition, January 27, 1998
|  | I-TEF |  | Run 1 |  |  |  |  | Run 2 |  |  |  |  | Run 3
|  | Wght Fact |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ |  | Total | TEQ | Total | TEQ
|  |  |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND |  | Full ND | Full ND | 1/2 ND | 1/2 ND
Detected in sample volume (pg)
| 2,3,7,8-TCDD | 1 | nd |  |  |  |  | nd |  |  |  |  | nd
| TCDD Total | 0 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,7,8-PCDD | 0.5 | nd |  |  |  |  | nd |  |  |  |  | nd
| PCDD Total | 0 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,4,7,8-HxCDD | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,6,7,8-HxCDD | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,7,8,9-HxCDD | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| HxCDD Total | 0 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,4,6,7,8-HpCDD | 0.01 | nd |  |  |  |  | nd |  |  |  |  | nd
| HpCDD Total | 0 | nd |  |  |  |  | nd |  |  |  |  | nd
| OCDD | 0.001 |  | 18.3 | 0.0183 | 18.3 | 0.0183 |  | 23.3 | 0.0233 | 23.3 | 0.0233 |  | 21.9 | 0.0219 | 21.9 | 0.0219
| 2,3,7,8-TCDF | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| TCDF Total | 0 |  | 7 | 0 | 7 | 0 |  | 3.2 | 0 | 3.2 | 0 |  | 4.3 | 0 | 4.3 | 0
| 1,2,3,7,8-PCDF | 0.05 | nd |  |  |  |  | nd |  |  |  |  | nd
| 2,3,4,7,8-PCDF | 0.5 | nd |  |  |  |  | nd |  |  |  |  | nd
| PCDF Total | 0 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,4,7,8-HxCDF | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,6,7,8-HxCDF | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| 2,3,4,6,7,8-HxCDF | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,7,8,9-HxCDF | 0.1 | nd |  |  |  |  | nd |  |  |  |  | nd
| HxCDF Total | 0 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,4,6,7,8-HpCDF | 0.01 | nd |  |  |  |  | nd |  |  |  |  | nd
| 1,2,3,4,7,8,9-HpCDF | 0.01 | nd |  |  |  |  | nd |  |  |  |  | nd
| HpCDF Total | 0 | nd |  |  |  |  | nd |  |  |  |  | nd
| OCDF | 0.001 | nd |  |  |  |  | nd |  |  |  |  | nd
| Gas sample volume (dscf) |  |  |  | 95.913 |  | 95.913 |  |  | 97.992 |  | 97.992 |  |  | 102.5179 |  | 102.5179
| O2 (%)* |  |  |  | 11.2 |  | 11.2 |  |  | 11.2 |  | 11.2 |  |  | 11.2 |  | 11.2
| PCDD/PCDF (pg in sample) |  |  |  | 0.0183 |  | 0.0183 |  |  | 0.0233 |  | 0.0233 |  |  | 0.0219 |  | 0.0219
| PCDD/PCDF (ng/dscm @ 7% O2) |  | 0 |  | 9.6314e-06 |  | 9.6314e-06 | 0 |  | 1.2003e-05 |  | 1.2003e-05 | 0 |  | 1.0784e-05 |  | 1.0784e-05
* O2 % is used from condition 767C7
| TEQ Cond Avg | 1.0806e-05