Natural Resources Conservation Service

Conservation Practice CONSTRUCTION Specification

Irrigation Water Conveyance - STEEL Pipeline

Code 430FF

- SCOPE

The work shall consist of furnishing and installing steel pipe complete with lining, coating, fittings, and appurtenances as shown on the drawings.

## SITE PREPARATION

Site preparation (mobilization and demobilization, clearing and grubbing, structure removal, pollution control, and water for construction) shall be in accordance with Construction Specification 587.

## MATERIALS

- Pipe

Steel pipe shall conform to the requirements of the applicable specification listed below for the kind of pipe and the type, weight, grade, and finish specified:

Pipe	ASTM Specification

Steel, black and hot-dipped, zinc-coated welded and seamless	A 53

Steel, electric-fusion (ARC)-welded (sizes NPS 16 and over)	A 134

Electric-resistance-welded steel	A 135

Electric-fusion (ARC)-welded steel (NPS 4 and over)	A 139

Pipe	AWWA Standard

Steel water pipe, 6 inches and larger	C 200

- Coatings and Lining

Coating and lining materials shall conform to the requirements of the following:

•	AWWA C203, Standard for Coal-Tar Protective Coatings and Linings for Steel Water Pipelines - Enamel and Tape - Hot-Applied

•	AWWA C209, Standard for Cold-Applied Tape Coatings for the Exterior of Special Sections, Connections, and Fittings for Steel Water Pipelines

•	AWWA C214, Standard for Tape Coating Systems for the Exterior of Steel Water Pipelines

and as specified below:

•	Shop coating material shall conform to the requirements of AWWA Standard C203 and AWWA Standard C214 and as specified in section 12 of this specification.

•	Shop lining material shall conform to the requirements of AWWA Standard C203.

•	Field coating and coating repair material shall conform to the requirements of AWWA Standard C203, AWWA Standard C209, AWWA Standard C214, and, as specified in Section 12 of this specification.

•	Field lining material shall conform to the requirements of AWWA Standard C203 and as specified in section 12 of this specification.

- Anodes

Zinc anodes shall meet or exceed the requirements of ASTM Specification B 418 (Standard Specification for Cast and Wrought Galvanic Zinc Anodes).  Each anode shall have a solidly attached full length core with a single strand of insulated copper wire.  The wire shall be No. 12 or larger.  If a header wire is used, the gage shall be adequate to catty the design current with no more than a 20 mV I-R drop.  All anodes shall be commercially packaged.

- Welding Electrodes

Steel welding electrodes shall conform to the requirements of American Welding Society Specification AWS A5.1, "Specification for Mild Steel Covered Arc-Welding Electrodes," except that they shall be uniformly and heavily coated (not washed) and shall be of such a nature that the coating does not chip or peel while being used with the maximum amperage specified by the manufacturer.

- Appurtenances

Unless otherwise specified or as may be shown on the drawings, standard fittings, special fittings and appurtenances shall be of the same material as the pipe.  Steel supports and saddles shall be constructed of material that equals or exceeds the requirements specified in ASTM A 36.

## FOUNDATION WORK

Foundation work (diverting surface water, dewatering the construction site, dewatering borrow areas, and foundation preparation) shall be in accordance with Construction Specification 587.

## EARTHWORK

Earthwork (common excavation and earthfill) shall be in accordance with Construction Specification 587.

## JOINTS AND CONNECTIONS

Pipe joints shall conform to the details shown on the drawings and shall be sound and watertight at the pressures specified in this specification or as may be shown on the drawings.

  - Welded Joints

Welding and welded joints shall conform to the welding procedure details and requirements of AWWA Standard C206.  Field welding shall be done in such a way as to avoid burning the protective coating on the pipe except in the immediate vicinity of the weld.

Where welded field joints are used, they shall be single welded butt joints or lap welded slip joints, as shown on the drawings.  Special closure lap joints shall be used as described in AWWA Standard C206.

  - Bell and Spigot Joints

The dimensions of bells and spigots shall be in accordance with the manufacturer's standard design dimensions and tolerances.

The pipe shall be laid with the bell oriented upstream.  The spigot end shall be seated in the bell to a depth as recommended by the manufacturer.  The spigot, when seated, shall compress the gasket radially in its annular recess to provide a positive seal.  Joints with fish-mouthed gaskets will be taken apart and reseated with a new gasket.

Rubber gaskets shall meet the requirements of AWWA Standard C200.

  - Mechanical Couplings

The ends of pipe to be connected with mechanical couplings shall be machined to allow coupling the pipe sections without damaging or displacing the gaskets and to ensure uniform end separation of the pipes.  Machined ends of the pipe that receive the coupling sleeves shall be free from dents, gouges, rust, or scale.  The pipe and couplings shall be assembled with continuous rubber ring gaskets conforming to the dimensions and tolerances recommended by the pipe manufacturer.  Coupling followers shall be drawn up evenly to ensure uniform pressure on the gaskets.

Grooved and shouldered joints shall be furnished and installed in accordance with AWWA Standard C606.

  - Flanged Joints

All steel ring flanges shall be fabricated in accordance with AWWA Standard C207.  Gaskets shall be either a neoprene cloth insert 1/16 or 1/8 inch thick or red rubber 1/16 inch thick.  The gasket shall be full face where used between flat face flange surfaces.  All flanged joints shall be made up tightly and shall not leak.

  - Fitting and Coupling Coatings

Compression couplings, mechanical couplings, and flanged fittings shall be shop coated with the AWWA Standard C203 coal tar enamel coating, as recommended by the coating manufacturer, or a factory-applied vinyl coating at least 12 mils thick and as specified in this specification.  All bolts furnished for flanges, couplings, and other types of bolted connections shall be stainless steel or low alloy steel and shall be field coated with a coal tar enamel or vinyl coating after installation.

## HANDLING

Coated pipe shall be handled in a manner to prevent abrasion of the coating during transportation, placement, and backfilling.  Pipe shall not be dropped from cars or trucks or allowed to roll down skids without restraining ropes.  Each section of pipe shall be delivered in the field as near as practicable to the place where it is to be installed.  When stockpiled , it shall be neatly piled and blocked with strips between tiers.  If the pipe must be moved longitudinally, care shall be taken to ensure that the pipe coating are not damaged.  Pipe shall not be rolled or dragged on the ground.  If the pipe is supported, as for welding, supports shall be of sufficient width and number and be padded, if necessary, to prevent damage to the coating.

## BURIED PIPELINES

Pipe shall be installed at sufficient depth below the ground surface to provide protection from hazards imposed by traffic crossing, farming operations, freezing temperatures, or soil cracking.  The minimum depth of the cover shall be 24 inches, but in soils subject to deep cracking, the cover shall be a minimum of 36 inches.

If necessary to install the pipe at a lesser depth, adequate protection shall be provided by placing extra fill over the pipeline, constructing a fence or other surface barriers, or using extra heavy gage pipe.

If trenches are excavated in soils containing rock or other hard material that might damage the pipe or coating material, the trenches shall be excavated slightly deeper than required and then filled to grade with sand or fine earth.

Buried steel pipelines shall be protected with sacrificial galvanic anodes if they are specified or otherwise show on the drawings to supplement the protection provided by the pipe coating.  Anodes shall be placed as shown on the drawings.  If horizontally placed, anodes shall be at or below the bottom elevation of the pipeline.  Vertically placed anodes shall have a minimum distance to 3 feet between the ground surface and the top of the anode.  Anodes shall not be placed in fill areas, and magnesium anodes must be placed a minimum distance of 10 feet from the pipeline.

Anodes shall be bedded in moist fine clay, clay loam, silt, or silt loam.  In sandy and gravelly areas, fine material must be imported for bedding and for covering the anodes to a depth of 6 inches.  The packaged anodes and the fine textured soil used for bedding and backfill shall be thoroughly wetted.

The lead wire from the anode, or the header wire for multiple anode installations, shall be attached to the pipeline by cadwelding, thermowelding, or other similar processes.  Testing station facilities shall be located and installed as specified for the job or as shown on the drawings, or both,  Wires at testing stations shall be attached to the pipe by one of the processes specified for anode lead wires.

- PIPELINES INSTALLED ABOVE GROUND

Concrete, timber, or other pipe supports, and anchors and thrust blocks shall be constructed at the locations to the dimensions shown on the drawings and/or as staked in the field.  Saddles shall be shaped to firmly support the pipe throughout the full arc of contact.  At least two layers of felt strips shall be placed between the pipe and its support unless otherwise detailed on the drawings.  The felt shall cover the entire area of contact between the pipe and the saddle.  A graphite lubricant shall be placed between the felt strips before the pipe is placed in the saddle.

- PIPELINES INSTALLED ON THE GROUND

Pipe shall be laid to the lines and grades as shown on the drawings and/or as staked in the field.  Pipe shall be protected from the hazards imposed by traffic crossings, farm operations, or other hazards.  The ground shall be shaped so as to provide support needed.  If there are rocks or objects that might damage the pipe coating, sand or soil shall be used as a base for the pipe.  Concrete, timber, or other anchors and thrust blocks shall be constructed at the locations to the dimensions shown on the drawings and/or as staked in the field.

- FIELD LINING, COATING, WRAPPING, AND REPAIR

Lining and coating or wrapping of field joints or connections and repair of damage to the wrap or coating on pipe, couplings, fittings, and appurtenances shall be made in accordance AWWA Standard C203, AWWA Standard C209 with Type I or II tape, or AWWA Standard C214, unless otherwise as may be shown on the drawings.

  - Surface preparation

Bare steel surfaces shall be prepared for coating by removing all grease and oil or other soluble contaminants with solvent commercial cleaners (wiping, dipping, or steam) or vapor degreasing.  After degreasing, surfaces shall be cleaned with hand tools to remove all loose scale rust and other loose detrimental foreign matter.

On previously coated surfaces, all dirt, paper, and other foreign matter and loose coating shall be removed.  Kraft paper, whitewash, or other surface protective layers shall be removed at least 12 inches on either side of the bare steel to be coated.

Welds shall be cleaned of all welding slag, splatter, and scale.  Sharp edges or burrs that could puncture or cut the coating shall be removed by grinding or filing.  All welds shall be allowed to cool before applying primer or coatings.

  - Primer application

After surface preparation is complete, primer shall be thoroughly mixed and applied in strict adherence to manufacturer's instructions.  The primer shall be permitted to dry to the consistency recommended by the manufacturer before applying the coating.  No foreign matter shall come in contact with the primed surface before application of the coating.  Application of primer to surfaces shall be limited to that amount of area that can be wrapped during the same workshift.  Primed areas not wrapped during the same workshift shall be reprimed.  Cold weather applications of primer shall be done in accordance with AWWA Standard C203.

  - Coating application

The specified coating shall be applied in accordance with the manufacturer's recommendations unless otherwise specified.

After assembly, all pipe joints shall be field wrapped in accordance with AWWA C209 or AWWA C214, as appropriate.  Surface preparation and primer application to the ends of the pipe to be wrapped shall be as previously described in this specification.  A tape or filler tape shall be cigarette wrapped over the annular ring of the joint.  The pipe coating shall be primed 2 inches back from the coating cutback and two layers of tape shall be wrapped overlapping 2 inches of pipe coating on one side of the joint, extending across the joint and overlapping 2 inches of coating on the other side of the joint.  Coal tar enamel coating cutback edges shall be tapered back until 1 inch of coal tar is exposed on the taper before priming and wrapping. Wraps shall be terminated on the underside of the pipe.  Tape widths shall be 6 inches for pipe greater than 8 inches in diameter and 4 inches for pipe 2 to 8 inches in diameter.

Welded field joints of lined pipe shall be lined in accordance with AWWA Standard C203, Section 4.3.

  - Repair and patching factory coatings

All loose or disbonded material shall be removed from the area of the "holiday."  All points, burrs, or rough edges shall be smoothed to a feathered edge.  The surface shall be cleaned and prepared as specified for joints, couplings, and fittings.  The area to be cleaned and prepared shall be at least twice the size of the "holiday."  The repair coating shall be worked onto the surface of the steel to leave no voids or wrinkles on the surface.

Coal tar enamel coatings shall be repaired in accordance with AWWA Standard C203, Section 2.15.  Tape coatings shall be repaired in accordance with AWWA Standard C214, Section 3.4, Coating Repair.  The repair shall be made by wrapping tape around the circumference of the pipe.

All damaged vinyl coat areas shall be cleaned and recoated in accordance with the manufacturer's recommendation.

- TESTING

Underground steel pipelines shall be tested before placing the backfill over the field joints.  Aboveground steel pipelines may be tested at any time after they are ready for operation.

The pipeline shall be filled with water, taking care to bleed air and prevent water hammer.  When the line is full, all valves shall be closed, and the line shall be brought up to full design working pressure.  All joints shall then be carefully inspected for leakage and any visible leaks shall be repaired.

It shall be demonstrated by testing that all valves, vents, surge chambers, and other appurtenances function properly when the pipeline is operated at design capacity.  Objectionable surge, water hammer, unsteady delivery of water, damage to the pipeline, and detrimental discharge from control valves are evidence of malfunction.

- MEASUREMENT

The quantity of each size and type of pipe shall be determined to the nearest foot by measurement of the laid length of pipe along the crown centerline of the pipe.

Project Name:

Date:

- ITEMS OF WORK AND CONSTRUCTION DETAILS

Items of work to be prepared in conformance with this specification and the construction details are: