Video Foil Monitor System ICD

David Gassner

February 2003,   BNL

Preface

The Video Foil Monitor (VFM) System is still in the design stage with a

FDR scheduled in FY03. As such, specific hardware configurations have not yet been selected.  It must be understood that this ICD represents the current design concepts.

# Overall Description

Light produced when the injected beam passes through the primary and secondary stripping foils is collected via a radiation hardened video camera. The image is transferred to image acquisition electronics for analysis. A horizontal and vertical transverse profile can be generated, as well as information regarding the condition of the stripping foil, which has a finite lifetime.

The video images will also be available in real time in the SNS control room.

External timing is required to synchronize the data acquisition with the macro-pulse structure and provide time stamping.

# General Capabilities

The FVM System will provide the following capabilities:

- Video image of the primary stripping foil.

- Video image of the primary stripping foil phosphor.

- Video image of the secondary stripping foil.

- Video image of the secondary stripping foil phosphor.

- Remote control of the primary & secondary neutral density filter attenuation assembly.

- Remote control of primary & secondary lamp illumination.

- System testing.

- System calibration

## 1.	Video image of the primary stripping foil.

Synchronized, time stamped, frame grabbed images of the primary stripping foil will be processed by the LabView using the NI-IMAQ driver for the NI-PCI-1409 Image Acquisition board.  Each frame will have characteristics measured (horizontal & vertical profiles, gaussian fits, etc…) and eventually (with experience) compared to a standard to determine the integrity of the foil.  Positions on the primary foil mount bracket assembly (mechanical dimensions will be provided) will be used as fiducials to calibrate dimensions of the image.

A typical digital image produced by video digitization would have a resolution of 512 (horizontal) X 480 (vertical) pixel resolution and would have individual pixels with a 5:6 aspect ratio.  Setting the NI-1409 digitizer to 8 bits (10 is optional) would yield about 512 X 480 = 250K bytes/Frame.

A 1000 pulse FIFO history of the primary VFM beam characteristics will be kept at the console level for use in a “strip chart” or “water fall” like display. This data will be sent up from the IOCs as packets once per second.

A real time video image will also be available via the second output from the video camera.

Each of the 10 stripping foils (used one at a time) will have a unique identifier, and will be confirmed by querying the foil motion control system.

## 2.	Video image of the primary stripping foil phosphor.

Synchronized, time stamped, frame grabbed images of the primary stripping foil phophor will be processed by the LabView using the NI-IMAQ driver for the NI-PCI-1409 Image Acquisition board.  Each frame will have characteristics measured (horizontal & vertical profiles, gaussian fits, etc…).  Fiducial marks on the phosphor screen (mechanical dimensions will be provided) will be used as to calibrate dimensions of the image.

A real time video image will also be available via the second output from the video camera.

The image acquisition software will know when the primary stripping foil is in place by querying the primary foil motion control system.  Also, the correct neutral density filter will be rotated in place depending on the intensity of the incident beam (this to be learned by experience).

## 3.	Video image of the secondary stripping foil

Synchronized, time stamped, frame grabbed images of the secondary stripping foil will be processed by the LabView using the NI-IMAQ driver for the NI-PCI-1409 Image Acquisition board.  Each frame will have characteristics measured (horizontal & vertical profiles, gaussian fits, etc…) and eventually (with experience) compared to a standard to determine the integrity of the foil.  Positions on the secondary foil mount bracket assembly (mechanical dimensions will be provided) will be used as fiducials to calibrate dimensions of the image.

A 1000 pulse FIFO history of the secondary VFM beam characteristics will be kept at the console level for use in a “strip chart” or “water fall” like display. This data will be sent up from the IOCs as packets once per second.

A real time video image will also be available via the second output from the video camera.

## 4.	Video image of the secondary stripping foil flag

Synchronized, time stamped, frame grabbed images of the secondary stripping foil will be processed by the LabView using the NI-IMAQ driver for the NI-PCI-1409 Image Acquisition board.  Each frame will have characteristics measured (horizontal & vertical profiles, gaussian fits, etc…).  Positions on the secondary foil mount bracket assembly (mechanical dimensions will be provided) will be used as fiducials to calibrate dimensions of the image.

A 1000 pulse FIFO history of the primary VFM beam characteristics will be kept at the console level for use in a “strip chart” or “water fall” like display. This data will be sent up from the IOCs as packets once per second.

A real time video image will also be available via the second output from the video camera.

Each of the 3 stripping foils (used one at a time) will have a unique identifier, and will be confirmed by querying the secondary foil motion control system.

## 5.	Remote control neutral density filter attenuation

A six-position Geneva drive style rotating neutral density filter assembly will be installed between the camera and the lens.  One position (home) will be empty yielding no attention.  The remaining 5 positions will each have decreasing transmittance capabilities  (50%, 25%, 1%, 0.5%, 0.1%).  The NI-PCI-1409 Image Acquisition board has digital I/O available for this task.  A timed bit (500ms) will necessary to increment the position of the assembly, this bit will drive a relay which controls the power to the dc rotation motor.  Also, software must keep track which filter is inserted, and calculate how to get to the next desired filter.  A routine to rotate until home (digital input bit reads home switch) is required in case the filter position is unknown (power dip, etc. .. ).  The Geneva gear also has a position switch to indicate if the drive is in the appropriate Geneva position, if not the motor should be rotated until the switch is made.

## 6.	Remote control primary & secondary lamp illumination.

Two halogen lamps will be placed at each foil location to illuminate the foil or flag to enable viewing of the object’s condition, position, and fiducial mark locations.  The lamps will be powered by a DC power supply.  On/Off control will be via a relay from a digital output bit from the NI-PCI-1409 Image Acquisition board.

## 7.	System Testing

Without beam, and the lamp will be turned on, images can be compared to a reference to ensure system integrity. Neural density filters can be inserted and light attenuation measured.

There will be local TV monitors in the ring service building to view live video images from both stripping foil locations.

8.	System Calibration

Periodically the system will check that the dimensions used in image analysis correspond to fiducial mark distances.

# System Configuration

## Distribution of VFM’s

The two systems, each includes a rad-hard video cameras and a neutral density filter assembly (and lens) will be located in separate cubbyhole recesses in the outer radius of the tunnel wall near the injection region.   The illumination lamps (2 each) will be mounted near the viewing port on the beam line vacuum chamber assembly.  The rack-mounted pc will be mounted in the ring service building.

## Image Acquisition & Control

Each PCI base processor card will acquire one RS-170 video image.  Digital I/O we done through the available channels on this PCI card.

## Timing

A machine synchronous timing signal will be connected to the external trigger input of the NI-1409 card, and all the cards must be synchronized together.  This timing signal will likely have to be delayed so the frame capture time is appropriate with beam arrival on the foil/phosphor.  The Dage 70R-VH video cameras also have a video synch input which needs the same trigger.

## Packaging

The IOC will be a rack mounted PC which will house the video image PCI cards in addition to motion control PCI cards for the primary and secondary foil drives.  The ND filter and lamp control relays will be mounted on DIN rail in the back of the rack, this DIN rail will also serve for cable terminations and inter-rack wiring.

Cabling

Video signals (analog).RG-59 Black, 75 Ohms.

Dage cable between camera in ring to Camera Control Unit (CCU) in ring service building. (1.5” diameter, underwater/radiation rated, it has a variety of shielded pairs, and coax, and a variety of control voltages and bias voltages along with video level signals).

Neutral Density Filter:  Multiconductor, 20 pair, 20 AWG "1140" (about 1 inch diameter, control voltages 5 – 24 VDC).

Lamps: 18 AWG Multiconductor.

## Process Variables

The various signals to be interfaced to the Control System are shown in Table I.

TABLE I

| Signal | # Chan | Type | Range | Characteristic | IOC Rate |
| --- | --- | --- | --- | --- | --- |
| Primary Foil Image | 1 | ADC | 8 bits | NI-1409 digitizer 2-40 MHz | 30 frames/s 250K bytes/Frame |
| Secondary Foil Image | 1 | ADC | 8 bits | NI-1409 digitizer 2-40 MHz | 30 frames/s 250K bytes/Frame |
| Primary ND Filter Command | 1 | Dig Output | 1/ch | TTL | 1/sec |
| Primary ND Filter Readback | 1 | Dig Input | 1/ch | TTL | 1/sec |
| Secondary ND Filter Command | 1 | Dig Output | 1/ch | TTL | 1/sec |
| Secondary ND Filter Readback | 1 | Dig input | 1/ch | TTL | 1/sec |
| Primary Foil Lamp | 1 | Dig Output | 1/ch | TTL | 1/sec |
| Secondary Foil Lamp | 1 | Dig Output | 1/ch | TTL | 1/sec |
| Timing Signal | 1 | V124S | - | - | Video Sync |

Data Acquisition

LabView will be used to control all aspects of data acquisition and digital I/O.  Each NI-1409 has 16MB of onboard RAM, enough to store about 75 frames.

Front End Data Processing

- Data scaling.  Each VFM channel will have calibration parameters for the foil or phosphor image based on defined fiducials on the objects.  The results should be stored in a separate array so that data in either engineering or physics units can be presented.

- Detailed Image Characteristics.  Image data will be processed to generated measurements, for example horizontal and vertical FWHM (full width half max), fit to gaussian, maximum and minimum pixel value range, etc. . .  To be defined further by physics requirements.

- Pulse Identification: Date/time stamp sufficient to specify macro-pulse.

- Long Term History for Each VPM. A 1000 pulse FIFO history of the long term, low level losses for each BLM will be kept at the console level for use in a “strip chart” or “water fall” like display. This data will be sent up from the IOCs once per second.

- Real Time Video for Each VPM. This image will be available by request in the SNS Control Room.

- Handshaking with Motion systems. The system will know if a foil, or phosphor, or the blank position is in the beam path by monitoring the status of the primary and secondary motion system.

7.	System Test.   Without beam, and the lamp will be turned on, images can be compared to a reference to ensure system integrity. Neural density filters can be inserted and light attenuation measured.