July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15820

CUSTOM DEHUMIDIFICATION SYSTEM

Page

PART 1 - GENERAL

1.01 Description..	2

1.02Related Work..	2

1.03Quality Assurance.	2

1.04References..	2

1.05Submittals.	3

1.06 Delivery, Storage, and Handling.	6

1.07Published Performance Data..	7

1.08 Extended Warranty..	7

1.09Equipment Support..	8

PART 2 - PRODUCTS

2.01Acceptable Manufacturers.	9

2.02Equipment.	9

PART 3 - EXECUTION

3.01 Inspection.	21

3.02 Installation/Application/Erection..	21

3.03 Field Quality Control.	22

3.04 Adjusting and Cleaning.	22

3.05 Commissioning.	22

3.06 Demonstration.	23

SPECIAL SPECIFICATION

SECTION 15820

CUSTOM DEHUMIDIFICATION SYSTEM

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section describes the physical and performance requirements for a factory-assembled, automatic, non-cycling, sorption type, desiccant, custom dehumidification system.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 15010

C.  	Section 15200

D.  	Section 15995

1.03	QUALITY ASSURANCE

A.  	The manufacturer of the custom dehumidification unit shall have at least 10 years of continuous, uninterrupted custom fabrication immediately prior to bid date.  Units of similar design and application shall be in operation as of bid date and manufacturer shall have demonstrated the capability to factory test units.  Field assembled units from pre-fabricated panels are not considered equal to a factory fabricated machine.

1.04	REFERENCES

A.  	American Refrigeration Institute (ARI).

B.  American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) Standard 52-76.

C.  	American Society for Testing and Materials (ASTM) E84, Standard Test Method for Surface Burning Characteristics of Building Materials.

D.  	ISO 9001

E.  	National Electrical Manufacturers Association (NEMA).

F.  	National Fire Protection Association (NFPA) 70, National Electrical Code (NEC).

G.  	Sheet Metal and Air Conditioning Contractors National Association (SMACNA), Publication 15d, HVAC Air Duct Leakage Test Manual.

H.  	Underwriter's Laboratories (UL).

I.  	UL 508, Industrial Control Panel.

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15010, and Section 01300.

B.  	The manufacturer shall provide the documentation needed to verify that the equipment will perform as the schedule requires, and that it will accomplish the task with utilities provided and in the space allowed.  Towards that end, the manufacturer shall submit the following documents for approval prior to production.

1.  	Technical Data Sheet:  The performance of the equipment at the specified conditions shall be described on a project-specific technical data sheet which includes:

a. 	Unit

1)  	Electrical utility

2)  	Full load amps

3)  	Project name and HVAC system designation defined by these specifications

4)  	End user name and installation location.

b. 	Process Air Side

1)  	Process air flow

2)  	Inlet dry bulb temperature

3)  	Inlet humidity ratio

4)  	Outlet dry bulb temperature

5)  	Outlet humidity ratio

6)  	Pressure drop through the desiccant wheel

7)  	Pressure drop through the entire dehumidifier

8)  	External static pressure available (if applicable)

9)  	Motor horsepower

10) 	Fan rotation and discharge position

c. 	Reactivation Air Side

1)  	Reactivation air flow

2)  	Inlet humidity ratio

3)  	Outlet dry bulb temperature

4)  	Outlet humidity ratio

5)  	Pressure drop through the desiccant wheel

6)  	Pressure drop through the entire dehumidifier

7)  	External static pressure available

8)  	Motor horsepower

9)  	Fan rotation and discharge position

d. 	Reactivation Energy

1)  	Reactivation energy type

2)  	Net reactivation energy consumption rate at the specified conditions

3)  	Method of automatic energy modulation in response to moisture load changes

4)  	Inlet dry bulb temperature

2.  	Manufacturer's Certifications:  With the documents and drawings submitted for approval, the manufacturer shall provide written certifications to document compliance with following requirements.

a. 	ISO 9001 registration number and the certificate which documents the quality assurance programs of manufacturing and field service.

b. 	Description of any proprietary components, along with documentation of the two or more geographically-separated manufacturing plants required for each component.

c. 	Certification that the unit wiring complies with the current NEC.

d. 	Independent report of the flame spread test for the desiccant wheel, performed in accordance with ASTM E84-90 - "Standard Test Method for Surface Burning Characteristics of Building Materials."

e. 	Material supplier certification that the desiccant wheel contains no fibers with a diameter smaller than 5 microns.

3.  	Product Drawings:  The manufacturer shall provide drawings of the proposed equipment which show:

a. 	A minimum of four dimensioned views of the equipment

1)  	Plan view

2)  	Controller side elevation

3)  	Process air inlet side elevation

4)  	Process air outlet side elevation

b. 	Centerline locations and dimensions of all connection points

1)  	Process air inlet

2)  	Process air outlet

3)  	Reactivation air inlet

4)  	Reactivation air outlet

c. 	Clearances and service access areas required for

1)  	Desiccant wheel removal

2)  	Desiccant wheel drive service

3)  	Airflow adjustment

d. 	Casing material and the net unit weight as proposed including all unit-mounted and remote-mounted components required to meet these specifications.

4.  	Operating & Maintenance Manual:  The manufacturer shall provide a copy of the operating and maintenance manual for the proposed equipment.  As a minimum, the manual shall contain:

a. 	Installation guidelines

b. 	Start-up checklist

c. 	Troubleshooting guide

d. 	Sequence of operations

e. 	Internal wiring diagram showing interconnection points for power and controls

f. 	Electrical parts list

g. 	Required maintenance activities, their recommended frequency

h. 	A list of recommended spar parts with the name, address and telephone number of the organization which supplies each part

i. 	24-hour (hr.), 7-day service assistance telephone number

1.06	DELIVERY, STORAGE, AND HANDLING

A.  	Deliver fan units as a factory-assembled unit to the extent allowable by shipping limitations, with protective crating and covering.

B.  	See Section 15010.

C.  	All rigging and equipment required to get unit to installation location shall be provided by the Contractor.

D.  	All units shall be cleaned after final assembly and/or testing in accordance with these specifications.  After the unit is alcohol-cleaned, wrap in a protective double-layer plastic bag and seal all joints so that the unit can be transported, stored and installed without concern for contamination of the cleaned unit.

E.  	Each cleaned and bagged unit shall then be secured to allow shipment and handling, without damage to the cabinet.  Shipping base shall be suitable for handling and moving.  The cleanroom contractor shall review and approve the method of packaging and shipment prior to the first shipment.

F.  	The Contractor shall receive, unload, inspect, store, uncrate and install the units at the job site.

G.  	Any units arriving at the job site that have not been adequately protected, per the approved methods mentioned in Paragraph 1.06D or have endured damage during shipping, shall be rejected by the cleanroom contractor/Sandia National Laboratory (SNL) and must be returned to the manufacturer for rework or replacement.

H.  	The outside of the package or crate shall be adequately marked or tagged to indicate its contents by equipment number and weight.

1.07	PUBLISHED PERFORMANCE DATA

A.  The manufacturer shall provide published performance data for all proposed equipment, so the approval authority can determine whether the unit has been selected within its normal operating range.  Equipment for which there is no full range of published performance data shall not be acceptable.  Equipment selected outside of the range of published performance data shall not be acceptable.

1.08	EXTENDED WARRANTY

A.  	The manufacturer shall be notified in writing of the date when all installation is complete and the equipment is to be started up.  The manufacturer shall then provide a service technician to visit the site, review the installation and test the operation of the unit to verify that it is performing in accordance with the technical data sheet and published performance specifications.  Operation of the unit and its testing shall be documented in writing by the technician and provided to SNL's representative.

B.  	Within nine months of the original start up, the manufacturer shall provide a second visit to the site by a qualified service technician, who will once again verify operation and performance of the unit and document the testing in writing for SNL's representative.

C.  	Given that the first and second visits by qualified technicians have been made and documented, the manufacturer shall warrant the equipment and the start-up service to be free from defects in materials and workmanship for a period of two years from date of start up or 27 months after shipment from the factory, whichever occurs first.

D.  	If any defects appear under this extended warranty, the manufacturer shall be notified by SNL, and the manufacturer shall provide both replacement parts and labor at no cost to SNL.

1.09	EQUIPMENT SUPPORT

A.  	The manufacturer shall provide support for the equipment for a minimum period of 15 years following shipment of the equipment.  This support shall, as a minimum, consist of:

1.  	Spare Parts for Superseded Equipment:  The manufacturer shall provide spare parts required for the proposed equipment for the full term of the 15-year support period, regardless of whether the equipment remains in current production.

2.  	Spare Parts Availability:  The manufacturer shall maintain an inventory sufficient to provide fast shipment of replacement parts.  This will include:

a. 	Product-specific parts shall be shipped within two weeks of the order

b. 	Parts available from sources other than the manufacturer:  Provide name, address and telephone number of an alternate supplier within 24 hours if the part is not available for shipment by the manufacturer within 48 hours.

3.  	Fully-Trained Service Technicians:  The manufacturer shall ensure that qualified service technicians are available to assist SNL 24 hr. a day, 7 days a week for the full support period.  These technicians shall be documented as having successfully completed training in:

a. 	Psychrometrics and phychrometric measurements

b. 	Methods of dehumidification

c. 	Dehumidifier applications

d. 	Desiccant dehumidifier performance calculations

e. 	Sensible heat and moisture load calculations

f. 	Dehumidifier start up and preventive maintenance

g. 	Dehumidifier troubleshooting and system diagnosis

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Cargocaire or approved equal.

2.02	EQUIPMENT

A.  	Dehumidifier unit casing shall be fabricated of strain-hardened aluminum with a minimum thickness of 0.125 inch (in.) for torsional rigidity and corrosion resistance.  The casing shall be formed, welded and sealed as a single unified structure.  Steel construction is not acceptable.  Aluminum structures depending on screws for casing construction are not acceptable.  In addition, the unit casing shall include:

1.  	Insulation:  To avoid either condensation, heat loss or loss of cooling capacity, the unit casing shall be insulated such that the heat transfer rate through casing walls is less than 0.27 British thermal units (Btu) per square foot (ft.2) per degree Fahrenheit (oF) if the wall separates air streams which differ in temperature by more than 25oF.

2.  	Wiring:  All wiring between dehumidifier components shall comply with the current NEC.  Wiring unprotected by flexible conduit shall not be acceptable.

3.  	Process and Reactivation Air Flow Gauges:  To set and verify the specified air flow rates through the unit, the casing shall be equipped with differential pressure gauges which measure and display the pressure drop across the desiccant wheel.  The dial of the gauges shall include a warning zone to indicate when the air flow is above the recommended operating range of the equipment.

4.  	Coating:  The exterior of the unit casing all surfaces of access panels shall be degreased and cleaned, then primed with one coat of industrial wash primer and finished with one coat of catalyzed polyurethane enamel.  All pieces shall be painted individually prior to assembly to assure complete protection.

5.  	Air Inlets:  Inlets shall be equipped with manual flow control dampers with locking hardware.  For air inlets smaller than 15 in. in height or width, single-blade dampers shall be acceptable.  When any inlet dimension exceeds 15 in., the manufacturer shall provide opposed-blade dampers with stainless steel end seals, elastomeric edge seals and oil-impregnated blade shaft bushings.

6.  	Maintenance Access and Inspection Panels:  The unit casing shall include access panels for inspection and for any maintenance required by the operating and maintenance manual.  These panels shall be fastened by captive hardware permanently fixed to either the panel or the unit casing.  The panels shall be airtight to the extent of not leaking more than 1 percent of the rated airflow when the interior of the casting is under 5 in., water gage (w.g.) positive air pressure.  Panels without gaskets shall not be acceptable.  Panels held in place by drill-screws shall not be acceptable.  Equipment which requires disassembly of components rather than access through removable panels for any maintenance required by the operating and maintenance manual shall not be acceptable.

7.  	Filters:

a. 	Pre-filters shall be 2-in. thick, medium efficiency, pleated, disposable type.  Each filter shall consist of a non-woven cotton and synthetic fabric media, media support gird and enclosing frame.  The filter shall be listed by UL as Class 2.

1)  	The filter media shall have an average efficiency of 25-30 percent on ASHRAE standard 52-76.  It shall have an average arrestance of 90-92 percent based in accordance with that standard.  The effective filter media shall be not less than 4.6 square feet of media per 1.0 square foot of filter face area and shall contain no less than 15 pleats per linear foot.  Initial resistance at 500 feet-per-minute (fpm) approach velocity shall not exceed .28 in. w.g.

2)  	Pre-filters shall be located upstream of the pre-cooling coil and on the reactivation air inlet.

3)  	Pre-filter media shall be Farr 30/30 or pre-approved equal.

b. 	Final filters shall be 12-in. thick, high performance, deep pleated, totally rigid and totally disposable type.  Each filter shall consist of high density media, media support grid, contour stabilizers, diagonal support bracing and enclosing frame.  The filter shall be listed by UL as Class 2.

1)  	Filter media shall be of high density microfine glass fibers, laminated to a reinforcing backing to form a lofted filter blanket.  The filter media shall have an average efficiency of 90-95 percent based on ASHRAE Standard 52-76.  It shall have an average arrestance of 97 percent based on that standard.  Initial resistance at 500 fpm approach velocity shall not exceed 1 in. w.g.

2)  	Final filter media is supplied in supply section only.  Pre-filter and final filter media will mount in glidepack aluminums extrusions suitable for side access service.

3)  	Final filter media shall be Farr RF-15 or pre-approved equal.

c. 	Magnehelic Gauges:  Gauges for the filter banks shall be factory mounted on the face of the unit control panel.  Separate gauges shall be supplied for each filter bank.  The pre-filter bank gauge shall have a 0-1 in. w.g. range.  The final filter banks' gauge shall have a 0-3 in. w.g. range.  All tubing penetration of the unit casing shall be factory sealed airtight.

B.  	Electrical Control Cabinet:  The electrical control cabinet shall meet NEMA 1 standards and shall include:

1.  	Wiring to comply with the current NEC with further fuse and wiring sizing to meet or exceed UL 508A "Industrial Control Panel."

2.  	Wires shall be color-coded or numbered at both ends and all terminal block connection points shall be numbered.  These markings shall correspond with the electrical diagram provided in the operating and maintenance manual.

3.  	Components shall be UL or CSA approved where possible.

4.  	Programmable Logic Controller:  The unit sequence of operations shall be controlled by a programmable logic controller which includes separate indication for:

a. 	Power on

b. 	Unit running

c. 	Desiccant wheel rotation fault

d. 	Reactivation air overheat after heaters

e. 	Reactivation air leaving below set point

f. 	Motor overload

5.  	Operating and Maintenance Manual:  The control cabinet shall include a copy of the O & M manual, mounted in a separate compartment or pocket to allow access to critical information by maintenance personnel after installation.

6.  	Run-Hour Meter:  To allow for recording maintenance practices and to assist fault diagnosis, the cabinet shall have a run-hour meter mounted and visible from the exterior of the unit.

7.  	Fan motor shall be factory wired to a NEMA 1, N-F disconnect located in the units factory mounted, control panel for field connection by others.  The factory mounted control panel shall be exterior to the unit.  Convenience controls (120 Volt [V]) will consist of one light and switch in each access section with one receptacle to be pre-wired and tested at the factory.

8.  	All transformers, terminal strips and wiring to be furnished and factory installed.

9.  	All conduit shall be piped to the exterior of the unit for final field connections where the conduit penetrates the unit casing.  The penetration shall be factory sealed airtight.

C.  	Reactivation Circuit:  The reactivation circuit shall conform in all respects to the current NEC.

1.  	Steam Reactivation:

a. 	Automatic energy modulation shall be provided by means of a variable-position reactivation airflow damper and motor assembly, controlled by a proportioning temperature controller mounted in the reactivation air as it leaves the dehumidifier.

b. 	The damper shall be equipped with edge seals and bearings rated for continuous duty at 400oF.  It shall not leak more than 3 cfm/ft.2 at a pressure difference of 1 in. w.g., nor more than 6 cfm/ft.2 at a pressure of 4 in. w.g..

c. 	Steam coils shall be the steam distributing, non-freeze type.  They shall be constructed with 5/8 in. OD copper condensing tubes with a wall thickness of 0.049 in. and mechanically-bonded aluminum fins.  The maximum length of a single coil shall be less than 120 times the outside diameter of its condensing tubes.  Casing and tube support sheets shall be a minimum of 16-ga. galvanized steel.  Tube holes in the casting and support sheets shall be oversized to allow for free thermal expansion of the tubes.  Coils shall be rated for 150 pounds per square-inch gage (psig) and test at 300 psig steam working pressure.

d. 	Steam fittings and piping shall be provided by the installing contractor in accordance with a recommended diagram provided by the manufacturer of the dehumidifier.

e. 	All control valves and control interlocks for the operation and control of the reactivation circuit shall be by the dehumidifier manufacturer.

D.  	Cooling Coils (Pre-cooling and Final Cooling)

1.  	Primary surface shall be round seamless 5/8 in. OD with .020-in. thick wall copper tubes on 1-1/2-in. centers, staggered in the direction of airflow.  All joints shall be brazed.

2.  	Secondary surface shall consist of rippled .0075-in. aluminum plate fins for higher capacity and structural strength.  Fins shall have full drawn collars to provide a continuous surface cover over the entire tube for maximum heat transfer.  Bare copper tube shall not be visible between fins and the fins shall have no openings punched in them to accumulate lint and dirt.  Tubes shall be mechanically expanded into the fins to provide a continuous primary to secondary compression bond over the entire finned length for maximum heat transfer rates.

3.  	Casings shall be constructed of stainless steel with 3/8-in. diameter, bolt holes for mounting on 6-in. centers.  Coil side plates shall be of reinforced flange type.

4.  	Coils shall have the connections located to permit universal mounting of the coil for right- or left-hand airflow have equal pressure drop through all circuits.  Coils shall be circuited for counterflow heat transfer to provide the maximum mean effective temperature difference for maximum heat transfer rates.  Coil fin height shall not exceed 42 in..

a. 	Water Coils:  Headers on water coils shall be seamless copper tubing.  The headers shall have intruded tube holes to provide a large brazing surface for maximum strength and inherent flexibility.

b. 	The complete coil core shall be tested with 315 psig air pressure under ware water and be suitable for operation at 250 psig working pressures.  Individual tube test and core tests before installation of headers is not considered satisfactory.  Hydrostatic tests alone will not be acceptable.  Water cooling coils shall be circuited for drainibility and for service without removing individual plugs from each tube.  Use of internal restrictive devices to obtain turbulent flow shall not be acceptable since they prevent complete draining of the coil.

c. 	Coils shall have headers within the unit and terminate at the exterior of the unit with flanges.  VIFB coil piping shall include flex connections and condensate piping.  All piping penetrations, of the unit casing shall be sealed airtight at the factory.

5.  	One side of this section shall have a gasketed, and bolted, removable access panel.

6.  	Each coil shall have a condensate drain pan extending a minimum of 12 in. downstream of the coil face for upper coils, and 18 in. for the lower most coil.  All condensate drain pans shall be stainless steel.  All intermediate drain pans shall be fitted with downspouts to drain condensate to primary drain pan.  Trapping of primary drain will be furnished and installed by the Contractor external to the unit casing.

7.  	Cooling coils shall be ARI certified for scheduled performance and bear the ARI seal.  Coils shall be manufactured by Heatcraft or approved equal.

E.  	Steam Coil (Preheat and Final Heat)

1.  	Steam coils shall be the steam distributing, non-freeze type.  They shall be constructed with 5/8-in. OD copper condensing tubes with a wall thickness of 0.049 in. and mechanically-bonded aluminum fins.  The maximum length of a single coil shall be less than 120 times the outside diameter of its condensing tubes.  Casing and tube support sheets shall be a minimum of 16-ga. galvanized steel.  Tube holes in the casting and support sheets shall be oversized to allow for free thermal expansion of the tubes.  Coils shall be rated for 150 psig and test at 300 psig steam working pressure.

2.  	Steam fittings and piping shall be provided by the installing contractor in accordance with a recommended diagram provided by the manufacturer of the dehumidifier.

F.  	Desiccant Wheel:  The desiccant wheel media shall be a monolithic, extended-surface contact medium, fabricated entirely of inert, inorganic binders and glass fibers formed into narrow passages in the direction of airflow.  The wheel shall be bacteriostatic and non-toxic.  It shall also meet the following requirements.

1.  	Materials:  The glass fibers which form the support matrix shall be made from uniform continuous strands larger than five microns in diameter which are nonrespiriable and are not considered a possible health risk by the International Agency for Research on Cancer (IARC).

2.  	Flame Spread and Smoke generation:  The wheel shall be tested according to ASTM E84-90 (Standard Test Method for Surface Burning of Building Materials) and shall achieve the following results:

a. 	Flame spread index = 0

b. 	Smoke developed index = 10

3.  	Desiccant Impregnation:  The desiccant shall be evenly impregnated throughout the structure for predictable, consistent performance and for maximum wheel life.  Coatings applied on top of the contact medium shall not be acceptable unless the manufacturer can provide independent life tests demonstrating less than a 5 percent decline in desiccant capacity over a five year period of normal operation.

4.  	Desiccant Type:  The desiccant impregnated into the contact medium shall be:

a. 	Lithium Chloride:  The desiccant shall be capable of absorbing 240 percent of its own weight in water vapor when in equilibrium with air at 40 percent relative humidity.  The absorption capacity of the desiccant shall not be adversely affected by particulate loading of the air stream as long as air can traverse the depth of the wheel.  The desiccant as impregnated into the medium shall be proven by independent test reports to kill bacteria and fungi which come in contact with the surface of the medium.

G.  	Desiccant Wheel Support and Drive Assembly:  The wheel shall be a single piece for fast removal and simple handling.  In the smaller case, the desiccant wheel shall be supported by four rollers at the base of the unit so the wheel can be easily removed for maintenance by lifting it over the rollers using the drive belt.  Center-axle support or any arrangement which requires disassembly of the support structure for wheel removal shall not be acceptable.  In addition, the wheel drive assembly shall provide:

1.  	Rotation Speed:  To avoid excessive heat carryover from reactivation to the process air, the wheel rotation speed shall not exceed 10 revolutions-per-hr. (rph) while achieving the required moisture removal rate at the specified conditions.

2.  	Drive Belt:  The drive belt shall be the flat, toothed type, with aramid fiber reinforcement.

3.  	Drive Motor:  The drive motor shall be fractional horsepower and rated for continuous duty for a period of 20,000 hr. under the load conditions imposed by the drive assembly.  See below for additional information.

4.  	Rotation Detection:  The drive assembly shall be equipped with a rotation detection circuit which shuts down the dehumidifier and signals the operator through an indicating light on the control cabinet if the wheel is not rotating.

H.  	Air Seals and Internal Air Leakage:  The process and reactivation air streams shall be separated by air seals and internal partitions so that the humid reactivation air does not mix with the dry process air.  The proposed equipment shall meet the following minimum requirements:

1.  	Wheel Face Seals:  The dehumidifier shall have full-face seals on both the process air entering and the process air leaving sides of the wheel.  These shall seal the entire perimeter of both air streams as they enter and leave the wheel.  Partial seals shall not be acceptable.  The seals shall be the silicone rubber bulb-type, with a protective strip of low-friction, abrasive-resistant tape to extend seal life and reduce the force needed to turn the desiccant wheel.  Neither wiper-type seals nor brush-type nor any non-contact-type seal shall be acceptable.  The seals shall be documented to have a minimum working life of 25,000 hr. of normal operation.

2.  	Total Casing Air Leakage:  The unit shall not allow leakage to exceed the greater of the following values:

a. 	One percent of the process air flow

b. 	SMACNA Leakage Class 6.

c. 	Determine leakage using the testing methods described by SMACNA Publication 15d, "HVAC Air Duct Leakage Test Manual."

I.  	Process and Reactivation Air Fans:  Process and reactivation air fans shall be the single-inlet, single-width, centrifugal-type.

1.  	Fan Wheel Type:  Shall be backward-inclined, belt-driven centrifugal type.

2.  	Balancing:  Fans shall be balanced after assembly and after coating at the speed the unit is scheduled to operate.  Fans shall be balanced such that the maximum displacement in any plane is less than 1.0 mils, peak to peak.

3.  	Belt-Driven Fans:  The drive shall be selected for 150 percent of rated capacity.  All belt-driven fans shall be equipped with:

a. 	Removable belt guards with openings to allow tachometer readings at both fan and motor shafts.  Guards shall also be constructed to allow visual inspection of the belts without removing the guard.

b. 	Vibration isolators, with a minimum efficiency of 95 percent and seismic snubbers.  See section 15200.

4. 	Fan Motors:  Fan motors shall be the totally enclosed, fan-cooled, high-efficiency type.  See below for additional information.

J.  	Motors

1.  	General

a. 	Apply requirements below to motors covered by this Section except as otherwise indicated.

b. 	Motors 1 Horsepower (hp) and Larger:  Polyphase.

c. 	Motors Smaller than 1 hp:  Single-phase.

d. 	Frequency Rating:  60 Hertz.

e. 	Voltage Rating:  Determined by voltage of circuit to which motor is connected for the following motor voltage ratings (utilization voltages):

1) 	Motors smaller than 1 hp:  120 V circuit, 115 V - motor rating.

2)  	Motors 1 hp and larger:  480 V circuit, 460 V - motor rating.

f. 	Service factor indicated for motors are minimum values and apply at frequency and utilization voltage at which motor is connected.  Provide motors which will not operate in service factor range when supply voltage is within 10 percent of motor voltage rating.

g. 	Provide permanent-split capacitor classification motors for shaft-mounted fans and capacitor start classification for belted fans.

h. 	Capacity:  Minimum size as indicated.  If not indicated, sufficient to start and operate connected loads at designated speeds in indicated environment, and with indicated operating sequence, without exceeding nameplate ratings.  Provide motors rated for continuous duty at 100 percent of rated capacity.

i. 	Temperature Rise:  50 degree (deg.) Celsius (C) maximum temperature rise at 40 deg. C ambient for continuous duty at full load (Class A Insulation).

j. 	Motor Speed:  Single.

k. 	Motor Construction:  NEMA Standard MG 1.

1)  	Bases:  Adjustable.

2)  	Bearings:  The following features are required:

a)  	Ball or roller bearings with inner and outer shaft seals.

b)  	Grease Lubricated.

c)  		Designed to resist thrust loading where belt drives or other drives produce lateral or axial thrust in motor.

3)  		Enclosure Type:  The following features are required unless noted otherwise.

a)  		Open drip-proof motors where satisfactorily housed or remotely located during operation.

b)  		Guarded drip-proof motors where exposed to contact by employees or building occupants.

4)  		Noise rating:  Quiet.

5)  		Nameplate:  Indicate the full identification of manufacturer, ratings, characteristics, construction, and special features.

2.  	Polyphase Motors

a. 		Squirrel-cage, induction-type, general-purpose conforming to the following requirements except at otherwise indicated.

b. 		Nema Design Letter Designation:  "B," unless specifically designed "C" for high starting torque.

c. 		Service Factor:  1.15.

d. 		Energy Efficient  Motors:  Nominal efficiency equal to or greater than that stated in NEMA MG 1, table 12-6C for that type and rating of motor.

e. Internal Thermal Overload Protection For Motors:  Protection automatically opens control circuit arranged for external connection.  Protection operates when winding temperature exceeds safe value calibrated to the temperature rating of the motor insulation.

f. 		Bearings:  Double-shielded, pre-lubricated ball bearings suitable for radial and thrust loading of the application,unless noted otherwise.

3.  	Single-phase Motors

a. 		Conform to the following requirements except as otherwise indicated.

b. 		Energy Efficient Motors:  One of the following types as selected to suit the starting torque and other requirements of the specific motor application.

1)  		Permanent Split Capacitor.

2)  		Split-Phase Start, Capacitor-Run.

3)  		Capacitor-Start, Capacitor-Run.

c. 		Service Factor:  1.35.

d. 		Shaded-Pole Motors:  Use only for motors smaller than 1/20 hp.

e. 		Internal Thermal Overload Protection for Motors:  Protection automatically opens the power supply circuit to the motor, or a control circuit arranged for external connection.  Protection operates when winding temperature exceeds a safe value calibrated to the temperature rating of the motor temperature returns to normal range except as otherwise indicated.

f. 		Bearings, belt connected motor and other motors with high radial forces on motor shaft shall be ball bearing type.  Sealed, pre-lubricated sleeve bearings may be used for other single phase motors.

K.  	Moisture Removal Capacity Control:  The dehumidifier shall operate automatically, in response to the control system supplied by the manufacturer as follows:

1.  	Process Air Face and Bypass Modulation:  The volume of process air passing through the dehumidifier shall be modulated by means of, electric motor-driven dampers which cover the process air inlet and the bypass air inlet to the dehumidifier casing.  The bypass air duct shall be included inside the dehumidifier casing such that no additional external ductwork need be added to the unit to achieve control.  The bypass duct shall be equipped with an orifice plate to balance the pressure drop of the bypass to equal that of the desiccant wheel at full flow.

a. 		Dampers:  Dampers shall be opposed-blade type, with galvanized steel frames, stainless steel end-seals, elastomeric blade edge seals and oil-impregnated blade shaft bushings.

b. 		Damper Frames and Casing:  The damper frames shall be fastened and sealed to eliminate air bypass around the damper assembly.  The operator(s) and connecting linkages shall be mounted in a separate compartments sealed from the supply air stream and from the ambient environment.  The compartment shall be equipped with an access panel for ease of adjustment and servicing without the need to disturb the supply air flow.

c. 		Damper Operators:  Damper operators shall be the proportional type with spring return on power loss.  They shall operate in response to a continuous signal input signal.

d. 		Responsibility for the control system shall be divided as follows:

1)  		Dehumidifier Manufacturer:  Provide the dehumidifier complete with dampers and motors mounted, wired and tested in the factory prior to shipment.  The manufacturer shall provide the sensor/controller suitable for operation and control at the specified location and humidity control range.

2)  		Installing Contractor:  Install the humidity sensor in the location specified, and wire the sensor and controller to the dehumidifier.  Reset the fixed-position bypass flow control damper such that pressure drop through the bypass equals the pressure drop through the desiccant wheel at the specified process air flow rate.

3)  		Controls shown within the unit and designated on Control Drawing 104658 C3 shall be provided by the unit manufacturer.

PART 3 - EXECUTION

3.01	INSPECTION

A.  	Inspect areas and conditions, with Installer present, for compliance with requirements for installation tolerances, housekeeping pads, and other conditions affecting performance of the dehumidifier.

B.  	Inspect rough-in for utilities to verify actual locations of connections prior to installation.

C.  	Do not proceed until unsatisfactory conditions have been corrected.

3.02	INSTALLATION/APPLICATION/ERECTION

A.  	General

1.  	Install dehumidifier level and plumb, in accordance with manufacturer's written instructions.

a. 		Support floor-mounted units on concrete equipment bases.  Secure units to anchor bolts installed in concrete equipment base.

2.  	Arrange installation of units to provide access space around dehumidifier for service and maintenance.

B	Connections

1. 	Piping installation requirements are specified in other Division 15 Sections.  The Drawings indicate the general arrangement of piping, valves, fittings, and specialties.  The following are specific connection requirements:

a. 		Arrange piping installations adjacent to units to allow unit servicing and maintenance.

b. 		Connection piping to dehumidifier with flexible connectors.

2.  	Duct installations and connections are specified in other Division 15 Sections.  Make final duct connections with flexible connections.

3.  	Electrical Connections:  The following requirements apply:

a. 		Electrical power wiring is specified in Division 16.

b. 		Temperature control wiring and interlock wiring is specified in Division 13 Section "HVAC Controls and Energy Management System."

c. 		Grounding:  Connect unit components to ground in accordance with the NEC.

3.03	FIELD QUALITY CONTROL

A.  	Provide a factory-authorized service representative to perform the following:

1.  	Inspect the field assembly of components and installation of dehumidification systems including piping, ductwork, and electrical connections.

2.  	Prepare a written report on findings and recommended corrective actions.

3.04	ADJUSTING AND CLEANING

A.  	Adjust damper linkages for proper damper operation.

B.  	Clean unit cabinet interiors to remove foreign material and construction dirt and dust.  Vacuum clean fan wheel, fan cabinet, reactivator section, and coils entering air face.

3.05	COMMISSIONING

A.  	The service technician shall start up and adjust the unit in accordance with instructions contained in the operating and maintenance manual provided by the manufacturer.  The start up technician must pay particular attention to the following items:

1.  	Air Flow:  The air flow volume of the process and reactivation air streams shall be set so that the reading on the manometers on the unit matches the values outlined on the technical data sheet provided by the manufacturer.

2.  	Utilities:  The power and reactivation energy connections shall be made carefully and checked against the unit specifications outlined on the technical data sheet provided by the manufacturer.

3.  	Documentation:  The start-up technician shall provide written documentation of compliance with procedures outlined by the manufacturer in the operating and maintenance manual.  As a minimum, the technician shall measure and record the values for the electrical power, the air flow manometers and the run-hour meter.  The technicians full name and telephone number and the start-up date shall be printed legibly on the start up documentation and on the copy of the technical data sheet in the operating and maintenance manual which is mounted inside the unit control cabinet.

B.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.  Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.  See Section 15995.

3.06	DEMONSTRATION

A.  	Provide a factory-authorized service representative to start-up equipment, to demonstrate operations, and to train personnel.

B.  	See Section 15995.

END OF SECTION

EXCEPT FOR ATTACHMENT

SK-AHU-3