4.2.13  Target Pile Air Cooling System

The purpose of the air cooling system is (1) to keep the pit floor and walls at approximately 12.8 °C, (2) to remove the following heat loads: beam heating - 158 kW, stripline - 2.4 kW, ambient - 3.4 kW, fan - 50 kW, (3) to dehumidify at a rate of 20 kilograms/hour at the 158 kW beam heating load, and (4) filter particulates from the airflow.  The automatically controlled system is designed to provide 240 kW of cooling, and to circulate and filter 750 Nm3 of air per hour.  The high efficiency particulate filters have a minimum removal efficiency of 99.97% with 0.3-micron size particles.  The dehumidification rate is based on a leak exchange rate between the target hall and the target pile of 2.5% of the design airflow rate.  The filters are installed in bag-in/bag-out housings.

The flow schematic is shown in Figure 4.2-41 a & b.  It is discussed below, starting where the cooling airflow exits the target pile.

Temperature and humidity of the air exiting the target pile are monitored.  Humidity of the target hall is also monitored.

Pressure drop across the particulate and high efficiency filter banks are individually monitored.  High differential pressure across either bank will shutdown the fan.  It is very important to change the filters at the specified pressure drops.  In particular, the prefilter will come apart at high-pressure drops, and unload the particulates trapped in it.  This will unnecessarily load the much more expensive high efficiency filters, most likely requiring that they be changed immediately.

The airflow is cooled after filtering.  An automatically controlled air damper is installed in parallel with the evaporator coils.  It will make moderate adjustments in the amount of air flowing to the evaporators to reduce the reheat duty.  Air damper position can also be positioned manually.  An electrically operated solenoid valve starts or stops the flow of high-pressure liquid refrigerant 22 to each evaporator coil based on the system heat load.  Solenoid valve operation can be either automatic or manual.  The full-open and full-closed state of each solenoid valve is monitored using limit switches.  A self-operated, thermal expansion valve automatically controls flow of refrigerant 22 to each evaporator coil.  Evaporator coil header pressure is used to automatically adjust condenser unit capacity to match the system heat load.  Operating status of the condensing unit is monitored.

The single-speed fan boosts the airflow to operating pressure after cooling.  Fan differential pressure is monitored.  The particle beam will shutdown if fan differential pressure is too low.  Fan inlet and outlet temperatures are monitored.  The fan can be started and stopped in either the target hall or the power supply room.

The reheater heats the airflow to operating temperature when needed.  Reheater operation can be either automatic or manual.  The heating element is equipped with a high temperature switch to protect it from burning out.  Temperature and humidity of the air entering the target pile are monitored.  The particle beam will shutdown if supply air temperature to the target pile is high or low for too long.

Slow start, smart motor contactors energize the fan and refrigeration compressor motors.  Each contactor will protect its motor from being damaged by current and voltage irregularities.  Each motor winding has an internal high temperature switch that is included in the control logic to further protect the motor from damage.

A PLC, programmable logic controller, is used to automatically control the solenoid valves that start and stop high-pressure refrigerant flow to each evaporator coil.  Control logic for the fan is hardwired.  All monitoring instruments are wired to PLC input modules.  The PLC transmits all monitored signals to Acnet via Ethernet.  The signals will be displayed on Actnet parameter pages.  Selected signals are included on alarm pages and on graphic displays.

The instrument list is given in Table 4.2-16.5a and Table 4.2-16.5b .

Table 4.2-16.5a  Air-cooling system instrument list – Part 1

Table 4.2-16.5b  Air-cooling system instrument list – Part 2

Figure 4.2-41a: Air-cooling system flow schematic

Figure 4.2-41b: Legend for Air-cooling system flow schematic