July 22, 1994

Contract # TW0592

SPECIAL SPECIFICATION

SECTION 15832

COMPUTER ROOM AIR-CONDITIONING UNIT

Page

PART 1 - GENERAL

1.01 Description..	2

1.02Related Work..	2

1.03Quality Assurance..	2

1.04References..	2

1.05Submittals.	3

1.06 Delivery, Storage, and Handling..	3

1.07Sequencing..	4

PART 2 - PRODUCTS

2.01Acceptable Manufacturers...	5

2.02 Equipment...	5

PART 3 - EXECUTION

3.01 Inspection.	8

3.02 Preparation...	8

3.03 Installation/Application/Erection..	8

3.04 Field Quality Control....	8

3.05 Adjusting and Cleaning..	9

3.06 Commissioning..	9

3.07 Demonstration..	9

SPECIAL SPECIFICATION

SECTION 15832

COMPUTER ROOM AIR-CONDITIONING UNIT

PART 1 - GENERAL

1.01	DESCRIPTION

A.  	This Section and the Drawings describe the requirements for the computer room air conditioning units.

B.  	Provide a unit which maintains temperature and humidity conditions in the room or rooms it is located.  Provide a self-contained, factory-assembled, computer-room, air conditioning unit with up-flow air delivery and an integral condensate pump capable of pumping at 20 ft. of head.

1.02	RELATED WORK

A.  	Section 01300

B.  	Section 15010

C.  	Section 15200

D.  	Section 15995

1.03	QUALITY ASSURANCE

A.  	Manufacturer's Qualifications:  Firm experienced in manufacturing computer room air-conditioning unit similar to those indicated for this Project and that have a record of successful in-service performance.

1.04	REFERENCES

A.  American Society of Heating, Refrigerating, and Air-Conditioning Engineers (ASHRAE) 52-76.

B.  	Anti-Friction Bearing Manufacturers Association (AFBMA) Standard 9 for ball-bearings.

C.  	National Electrical Manufacturers Association (NEMA) MG 1.

1.05	SUBMITTALS

A.  	Make submittals according to this Section, Section 15101, and Section 01300.

B.  	Product data for each computer room air-conditioning unit including the following:

1.  	Unit refrigerant.

2.  	Unit design requirements.

3.  	Unit features.

4.  	Weights (shipping, installed, and operating).

5. 	Furnished accessories.

6.  	Installation and start-up instructions.

C. 	Shop drawings detailing fabrication and installation of computer room air-conditioning unit including plans, elevations, sections, component details, attachments, and other construction elements.  Include the following:

1.  	Dimensions.

2.  	Weight loadings and distribution.

3.  	Clearances for maintenance and operation.

4.  	Size and location of field connections.

D.  	Wiring diagrams detailing power and control wiring.  Differentiate clearly between manufacturer-installed wiring and field-installed wiring.

E.  	Maintenance data for each computer room air-conditioning unit to be included in the operating and maintenance manual specified in Section 01300.

F.  	Certification of performance from the factory.

G.  	Certification letter from manufacturer stating that the computer room air-conditioning unit has been through start-up procedures and that it is functioning properly.

1.06	DELIVERY, STORAGE, AND HANDLING

A.  	See Section 15010.

1.07	SEQUENCING

A.  	Coordinate unit with the raised floor installation.

PART 2 - PRODUCTS

2.01	ACCEPTABLE MANUFACTURERS

A.  	Liebert

B. 	Compu-Aire

2.02	EQUIPMENT

A.  	Cabinet and Frame Construction:  Provide a heli-arc welded tubular steel frame. Insulate the exterior panels with a minimum 1 in., 1.5 lbs. density fiber insulation. Use captive 1/4 turn fasteners on the main front panel.  Paint the unit off-white with an accent color of off-white.

B.  	Filter Chamber:  Provide within the cabinet a filter chamber which is serviceable from the front.  Provide 30 percent efficient filters per ASHRAE 52-76.

C.  	Fan Section

1.  	Provide a centrifugal, double-width, double-inlet fan which is statically and dynamically balanced as a completed assembly to a maximum vibration level of 2 millimeters (mm) in any plane.

2.  	Provide a steel shaft with self-aligning ball bearings.  Use lubricatable ball-bearings with a minimum life span of 100,000 hours (hr.) per AFBMA Standard 9.

3.  	Provide poly-phase, 1750 revolutions-per-minute, fan motor mounted on an adjustable slide base.  Use motors rated for 480-V, 3-ph., 60-Hz when the motor is over 3/4 horsepower (hp) and larger.  Provide a motor with NEMA Design Letter Designation "B", rated for continuous duty.  Use an energy efficient motor with a nominal efficiency equal to or greater than that stated in NEMA MG 1, table 12-6C for that type and rating of motor.  Provide double-shielded, pre-lubricated ball-bearings suitable for the radial and thrust loading of the application.

4.  	Provide a two-belt, variable-speed, drive package, sized for 200 percent of the fan motor hp.

5.  	Locate the fans to draw air over the A-frame coil to ensure even air distribution and maximum coil performance.

D.  	Infrared Humidifier:  Provide an infrared type humidifier consisting of high intensity quartz lamps mounted above and out of the water supply.  Use an stainless steel evaporator pan arranged to be serviceable without disconnecting high voltage electrical connections.  Pre-pipe the humidifier section for one final tie-in connection.  Use bypass air to prevent over-humidification of the computer room.  Equip the humidifier with an automatic water supply system.  Provide the system with an adjustable water-overfeed to prevent mineral precipitation.

E.  	Hot Water Reheat:  Provide hot water reheat coil with copper tubes and aluminum fins.  Pre-pipe the 2-way modulating control valve and cleanable Y-strainer.

F.  	Standard Control Processor:  Provide a microprocessor based control system.

1.  	Adjustable Functions:  Provide two .43-inch (in.) high, seven segment, light emitting diode (LED), numerical displays to allow observation of room temperature and humidity and each adjustable function:

a. 		Temperature Set-point 65-85 deg. F.

b. 		Temperature Sensitivity 1 to 5 deg. F.

c. 		Humidity Set-point 40-60 percent relative humidity (rh).

d. 		Humidity Sensitivity 1 percent to 10 percent rh.

e. 		Humidifier Flush Rate.

2.  	Normal Operating Modes:  Indicate the modes below by colored LEDs on the unit-mounted display panel.

a. 		Heating

b. 		Cooling

c. 		Humidification

d. 		Dehumidification

3.  	Alarm Conditions:  Activate audible and visual alarm in the event any of the following factory preset alarm conditions are initiated:

a. 		High Temperature

b. 		Low Temperature

c. 		High Humidity

d. 		Low Humidity

e. 		Restricted Air Filters

f. 		Loss of Air.

4.  	Activate a common alarm light when any of the above conditions exist, high head pressure develops, or water accumulates under the floor.

5.  	Provide a compressor sequence feature to change the lead/lag sequence of the compressors.

G.  	Chilled-Water Systems

1.  	Chilled Water Control Valve:  Provide a 3-way modulating, proportional, valve which is positioned by the microprocessor in response to room conditions.  Control cooling capacity by bypassing chilled water around the coil.

2.  	A-Frame Chilled Water Coil:  Construct the coil of copper tubes and aluminum fins.  Limit the maximum face velocity to 500 ft. per minute.   Provide a stainless steel condensate drain pan.  Control the coil with a 3-way modulating control valve.

3.  	Flow Switch:  Provide a flow switch to activate the alarm system should the chilled water supply be interrupted.  Factory mount and wire the switch.

H.  	Accessories

1. 	Disconnect Switch (Non-Locking Type):  Provide a non-automatic molded case circuit breaker mounted in the high voltage section of the electrical panel.  Make the switch accessible with the door closed.

2.  	Firestat:  Provide a firestat to immediately shut down the computer room air-conditioning system when activated.  Mount the firestat in the electrical panel with the sensing element in the return air.

3.  	Liqui-Tect Sensors (Max. of two per unit):  Provide 2 solid state water sensors under the raised floor.

4.  	Smoke Detector:  Provide a smoke detector to immediately shut down the computer room air-conditioning unit and activate the alarm system when activated.  Mount the smoke detector in the electrical panel with the sensing element in the return air compartment.

I.  	Design Requirements

1.  	See Drawings for information.

PART 3 - EXECUTION

3.01	INSPECTION

A.  	Inspect areas to receive the computer room air-conditioning units for compliance with requirements for installation tolerances and other conditions affecting performance.  Do not proceed with installation until unsatisfactory conditions have been corrected.

3.02	PREPARATION

A.  	Coordinate final locations of the computer room air-conditioning units with the raised floor layout.

3.03	INSTALLATION/APPLICATION/ERECTION

A.  	Install computer room air-conditioning units in accordance with manufacturer's installation instructions.  Install units plumb and level, firmly anchored in locations indicated, and maintain manufacturer's recommended clearances.

B.  	Install and connect electrical devices furnished by manufacturer but not specified to be factory mounted.  Furnish copy of manufacturer's electrical connection diagram submittal to electrical contractor.

C.  	Install and connect devices furnished by manufacturer but not specified to be factory mounted.  Furnish copy of manufacturer's piping connection diagram submittal to piping contractor.

D.  	Install vibration isolation and snubbers according to manufacturer's recommendations and Section 15200.

E.  	Install piping connections maintaining clearances for service and maintenance.

F. 	Install flexible pipe and electrical connections for computer room air-conditioning units mounted on vibration isolation.

G.  	Install shutoff valves at the computer room air-conditioning units' inlet and outlet connections.

3.04	FIELD QUALITY CONTROL

A.  	Start up mainframe coolant units in accordance with manufacturer's start up instructions.  Test controls and demonstrate compliance with requirements.

3.05	ADJUSTING AND CLEANING

A.  	Clean computer room air-conditioning units using materials and methods recommended by the manufacturer.

B.  	Clean finishes to remove dust and dirt.

C.  	Touch up scratches on unfinished surfaces to restore corrosion resistance.

D.  	Touch up scratches on finished surfaces to restore finish.

3.06	COMMISSIONING

A.  	Provide labor, material, equipment, etc., required to facilitate the commissioning process.

B.  	Perform form tests and verification procedures required by the commissioning process when requested by the Commissioning Authority and directed by the General Contractor.

C.  	See Section 15995.

3.07	DEMONSTRATION

A.  Provide factory-authorized service representative to start-up equipment, to demonstrate operation and to train personnel.

B.  	See Section 15995.

END OF SECTION